CANADA/PACIFIC NORTHWEST TO NORTHERN CALIFORNIA TRANSMISSION PROJECT – Avista Corporation 500/230 kV Interconnection

WECC Regional Planning and Phase 1 Rating Study

Study Plan

DRAFT

February 29, 2008

Table of Contents

1.	Objective									3

2.	Background									3

3.	Subregional Study Coordination						4

4.	Study Assumptions								5

5.	Study Base Cases								5

6.	Study Scope									6

6.1	Evaluation of HVDC Converter Station Locations			6

6.2	Power Flow Analysis							7

6.3	Dynamic Stability Analysis						7

6.4	Reactive Margin Analysis						7

6.5	Plan of Service Alternatives and Sensitivities			7

7.	Study Schedule								9

Attachment 1 Conceptual Project Plan

Attachment 2 Load & Resource Scenarios

Attachment 3 Contingency List

# Objective

Perform the WECC Regional Planning and  Phase 1 Rating Study for Avista Corporation’s 500/230 kV interconnection to the Pacific Gas and Electric Company Canada/Pacific Northwest to Northern California Transmission Project (Project) as follows:

  - Identify a preliminary plan of service for the 500/230 kV interconnection, including phase shifting requirements and 230 kV connections to the Avista main grid in and around Spokane, Washington.

  - Determine preliminary bi-directional non-simultaneous ratings for the proposed Project.

  - Coordinate with other proposed transmission projects in the Pacific Northwest, Canada and Northern California.

  - Submit a comprehensive progress reports for the Project to the WECC PCC and TSS committees for approval.

# Background

In August 2006, PG&E initiated a WECC Regional Planning Review for an electric transmission project from Canada/Pacific Northwest to Northern California.  The primary objectives of this project were to access renewable resources in British Columbia and the Pacific Northwest, and to provide transmission benefits to all users of the project.  The Regional Planning Review was conducted in an open stakeholder process with over 75 representatives from renewable developers, energy marketers, investor-owned and municipal utilities, energy industry consultants, regional planning entities, independent transmission companies, and regulators from throughout the West.

As a part of the above process, Avista has proposed an interconnection with the project in either the Spokane or Lewiston, Washington areas.  Preliminary studies indicate that the preferred alternative is an interconnection in the Spokane, Washington area.

The project would have a bi-directional rating of 500 MW and is expected to be operational in late 2015.

# Subregional Study Coordination

The system impacts of interconnecting the Project to the Avista transmission system will be addressed by this Phase 1 Rating Study.  Various stakeholders from the Pacific Northwest will be consulted to determine which contingencies and study scenarios need to be considered in order to determine the system impacts of interconnecting the Project at Devil’s Gap and continuing into the Spokane area.  The Regional Planning and Phase 1 Rating Study will also consider any interaction between this project and other proposed regional projects in the 2010-2015 time-frame.

# Study Assumptions

- The expected on-line date of the Project is 4Q 2015.

- The load and resource scenarios will be developed in collaboration with other stakeholders in the Pacific Northwest, Montana, and Idaho in order to achieve the desired transmission path flows over each section of the Project (see Attachment 3).  As a first cut (and not to presuppose which projects will come on line or in what order) we will assume the following projects:  100 MW near Reardan, WA, 200 MW near Benewah, Idaho, 100 MW near Grangeville, Idaho, and 100 MW near Thompson Falls, Montana.

- This study will take into account all WECC transmission reliability projects in the area that have WECC Phase II approval and that are scheduled to be operational by June 2015.

- Major path flows within the study area will be kept near their pre-Project levels in the starting base cases as appropriate.

- A list of series compensation assumptions for the Canada to California project will be provided.

- Voltage criteria will be applied in accordance with the existing policies of the respective interconnected utilities or operating agents.

# Study Base Cases

Three base cases from the WECC Library compiled in 2007 will be used as the starting base cases for the Phase 1 Rating Study:

- 2015 Heavy Summer Base Case (2015HS1SA):

This base case will be used to model summer peak conditions with moderate  east-to-west flows.

- 2017 Heavy Winter Base Case (2017HW1A):

This base case will model winter peak conditions with moderate east-to-west flows.

- 2011 Light Spring Base Case (2011LSP1SA):

This sensitivity base case will model spring off-peak conditions with high hydro generation and high east-to-west flows.

The major path flows in the three starting base cases are tabulated  below:

| Path | 2015 Summer Peak | 2017 Winter Peak | 2011 Light Spring |
| --- | --- | --- | --- |
| Path x Montana - Northwest - |  |  |  |
| Path x West of Hatwai |  |  |  |
| Path x Idaho - Northwest | xx MW (n2s?) | xx MW (n2s?) | xx MW (n2s?) |
| Path x South of Boundary | xx MW (n2s) | xx MW (s2n) | xx MW (n2s) |
| Path xx |  |  | 1800 MW (n2s) |

The Project model will be inserted into the starting base cases and resources, loads, and interchanges adjusted to achieve the desired Project path flow while maintaining existing paths in the study area near their levels in the starting WECC base cases.

# Study Scope

The following studies will be performed in order to determine the proposed plan of service and demonstrate the non-simultaneous rating  of the Project.

## Evaluation of Devils Gap Phase Shifting Requirements

Phase shifting transformers will likely be required to obtain the full 500 MW bi-directional rating for the interconnection.  The amount of phase shift required will be examined and then “set”, if possible, for the remainder of the study evaluation.

## Power flow Study

Power Flow analysis will be performed for system normal as well as for all of the transmission contingencies that are normally studied for Avista’s NERC/WECC Compliance program (see Attachment 3).  These contingencies also include selected BPA contingencies which are known to impact the Avista transmission system.  The interconnection will be modeled at its proposed 500 MW non-simultaneous rating in each of the three study base cases.  Any impacts of the Project will be determined for the following conditions:

- Category “A” - Normal operating conditions.

- Category “B/C” - Select single and multiple facility outages of the existing system and various segments of the proposed Project.

## Dynamic Stability Analysis

Dynamic stability studies will be conducted with the Project modeled at its proposed non-simultaneous rating in each of the three study base cases to ensure that the transmission system remains in operating equilibrium through abnormal operating conditions after the Project is in operation.  Disturbance simulations will be performed for a study period of up to 20 seconds to determine whether the Project would create any system instability during and following the selected contingencies.  Select Category B and C (single and multiple) contingencies of the existing transmission system or of the Project itself will be evaluated.

## Reactive Margin Analysis

A reactive margin analysis of the transmission system with the Project in service will be conducted in order to identify any reactive power deficiency or voltage instability due to the addition of the Project.  Select Category “B” and “C” contingencies of the existing transmission system or of the Project itself will be evaluated for both dynamic and post transient voltage stability.

All power flow, dynamic stability, and reactive margin studies will be performed in accordance with applicable NERC/WECC Planning Standards and Reliability Criteria.  Sensitivity studies will also be performed with other proposed regional transmission projects modeled in the Northwest in addition to the Canada/Pacific Northwest to Northern California Project in the study base cases.

## Plan of Service Alternatives and Sensitivities

The list of primary system configuration alternatives and sensitivity cases to be studied is as follows (this list is similar to the PG&E project cases, and will be modified as we receive additional comments at the beginning of our study process.  It is clear that stakeholders will be interested in flows on the West of Hatwai path, for example and less interested in the configuration of the system south of Boardman):

- Heavy Summer #1:  500 kV DCTL between Selkirk Substation (BC) and Boardman Hub (Oregon) with an intermediate station at Devil’s Gap near Spokane.  3000 MW HVDC converter station at Boardman Hub with +/- 500 kV DC bipole line to northern California.  Split bipole in Vaca Dixon area to 1500 MW HVDC converter stations at Tesla/Tracy and Collinsville.  2500 MW of incremental renewable resources in British Columbia. 500 MW of incremental renewable resources in the Avista system, with 3000 MW scheduled on the  Canada-California Project between Devils Gap and Tesla/Tracy/Collinsville.

- Heavy Summer #2:  Same physical configuration as #1 above but with no incremental resources in British Columbia and minimal power scheduled between Selkirk and Boardman Hub.  500 MW of incremental renewable resources in the Avista system, 2500 MW of incremental renewable resources in south central Washington and north central Oregon with 3000 MW scheduled on the HVDC section of the Project between Boardman Hub and  Tesla/Tracy/Collinsville.

- Heavy Summer #3:  Same physical configuration as #1 above but with 500 MW import into the Avista system, and 2500 MW from Devils Gap into Northern California

- Heavy Summer #4:  Same physical and resource configuration as #1above, but with higher West of Hatwai and other “Avista Area” path flows.

- Light Spring #1:  Same physical and resource configuration as #1 above coincident with high hydro generation in northern California.

- Heavy Winter #1:  Same physical configuration as #1 above with south-to-north flows of 2000 MW on the Project between Tesla/Tracy/Collinsville and Selkirk.

- Other cases may be considered..

# Study Schedule

|  | Activity | Complete By |
| --- | --- | --- |
| 1 | Announce WECC Phase 1 and Form Study Teams | November-December 2007 |
| 2 | Joint Big Tent Meeting (NW Projects) | January 24, 2008 |
| 3 | Prepare and Finalize Study Plan | December 2007-January 2008 |
| 4 | Prepare Base Cases | December 2007-February 2008 |
| 5 | Pre-Project Case | March 2008 |
| 6 | Technical Studies (Monthly Work Group Conference calls/Meetings) | April June 2008 |
| 7 | Joint Big Tent Meeting(NW Projects) | June 2008 |
| 8 | Draft Study Reports | July 2008 |
| 9 | Comprehensive Progress Report (CPR) | July-August 2008 |
| 10 | Joint Big Tent Meeting(NW Projects) | August 2008 |
| 11 | Submit to (CPR) to PCC and TSS | August 2008 |

Attachment 1

Conceptual Schematic for Transmission Options

Attachment 2

Load and Resource Scenarios

To be developed

Attachment 3

Contingencies to be studied by Avista

Note that this is the complete list- it is assumed that the 115 kV outages (which if they show up as a problem at all it is generally a load problem and therefore universal to all cases) will  be run only on the most stressed West of Hatwai case to prove that there is no interaction with the interconnection project.,

| Contingency Name | Actions | Model Criteria | Status |
| --- | --- | --- | --- |
| B_40017ADDY | OPEN Bus ADDY_115.0 (40017) |  | CHECK |
| B_40019ADDY | OPEN Bus ADDY_230.0 (40019) |  | CHECK |
| B_40021ADDY 2&1 | OPEN Bus ADDY 2_230.0 (40021) |  | CHECK |
| B_40021ADDY2 | OPEN Bus ADDY 2_230.0 (40021) |  | CHECK |
| B_40021ADDY2 | OPEN Gen BOUNDG55_ 14.4 (46472) #55 | South of Boundary > 650 | CHECK |
| B_40021ADDY2 | OPEN Gen BOUNDG56_ 14.4 (46474) #56 | South of Boundary > 650 | CHECK |
| B_40023AHSAHKA | OPEN Bus AHSAHKA_115.0 (40023) |  | CHECK |
| B_40029ALBENIF | OPEN Bus ALBENI F_115.0 (40029) |  | CHECK |
| B_40067ATHOL | OPEN Bus ATHOL_115.0 (40067) |  | CHECK |
| B_40086BELLS1 | OPEN Bus BELL S1_230.0 (40086) |  | CHECK |
| B_40086BELLS1 | OPEN Gen BOUNDG55_ 14.4 (46472) #55 | South of Boundary > 650 | CHECK |
| B_40086BELLS1 | OPEN Gen BOUNDG56_ 14.4 (46474) #56 | South of Boundary > 650 | CHECK |
| B_40087BELLBPA | OPEN Bus BELL BPA_115.0 (40087) |  | CHECK |
| B_40088BELLS2 | OPEN Bus BELL S2_230.0 (40088) |  | CHECK |
| B_40088BELLS2 | OPEN Gen BOUNDG55_ 14.4 (46472) #55 | South of Boundary > 650 | CHECK |
| B_40088BELLS2 | OPEN Gen BOUNDG56_ 14.4 (46474) #56 | South of Boundary > 650 | CHECK |
| B_40090BELLS3 | OPEN Bus BELL S3_230.0 (40090) |  | CHECK |
| B_40090BELLS3 | OPEN Gen LANCAS G_ 18.0 (47568) #1 |  | ALWAYS |
| B_40090BELLS3 | OPEN Gen LANCAS S_ 13.8 (47569) #1 |  | ALWAYS |
| B_40090BELLS3 | OPEN Gen BOUNDG55_ 14.4 (46472) #55 | South of Boundary > 650 | CHECK |
| B_40090BELLS3 | OPEN Gen BOUNDG56_ 14.4 (46474) #56 | South of Boundary > 650 | CHECK |
| B_40091BELLBPA | OPEN Shunt GARRISON_500.0 (40459) #r |  | ALWAYS |
| B_40091BELLBPA | OPEN Bus BELL BPA_500.0 (40091) |  | ALWAYS |
| B_40091BELLBPA | OPEN Load MILCTYDC_230.0 (63010) #D1 |  | ALWAYS |
| B_40091BELLBPA | OPEN Bus LIB PH1_230.0 (44200) | West MT Hydro > 1000 | CHECK |
| B_40091BELLBPA | OPEN Bus LIB PH2_230.0 (44201) | West MT Hydro > 1000 | CHECK |
| B_40091BELLBPA | OPEN Gen LANCAS S_ 13.8 (47569) #1 | WEST OF HATWAI > 3500 | CHECK |
| B_40091BELLBPA | OPEN Gen LANCAS G_ 18.0 (47568) #1 | WEST OF HATWAI > 3500 | CHECK |
| B_40092BELLS4 | OPEN Bus BELL S4_230.0 (40092) |  | CHECK |
| B_40094ADDBEL11 | OPEN Bus ADDBEL11_230.0 (40094) |  | CHECK |
| B_40094ADDBEL11 | OPEN Gen BOUNDG55_ 14.4 (46472) #55 | South of Boundary > 650 | CHECK |
| B_40094ADDBEL11 | OPEN Gen BOUNDG56_ 14.4 (46474) #56 | South of Boundary > 650 | CHECK |
| B_40096BELLSC | OPEN Bus BELL SC_500.0 (40096) |  | CHECK |
| B_40096BELLSC | OPEN Shunt GARRISON_500.0 (40459) #r |  | ALWAYS |
| B_40096BELLSC | OPEN Load MILCTYDC_230.0 (63010) #D1 |  | ALWAYS |
| B_40096BELLSC | OPEN Bus LIB PH1_230.0 (44200) | West MT Hydro > 1000 | CHECK |
| B_40096BELLSC | OPEN Bus LIB PH2_230.0 (44201) | West MT Hydro > 1000 | CHECK |
| B_40113BIGELOW | OPEN Bus BIGELOW_115.0 (40113) |  | CHECK |
| B_40133BONNERS | OPEN Bus BONNERS_115.0 (40133) |  | CHECK |
| B_40145BOUNDARY | OPEN Bus BOUNDARY_230.0 (40145) |  | CHECK |
| B_40145BOUNDARY | OPEN Gen BOUNDG55_ 14.4 (46472) #55 | SoB>650 | CHECK |
| B_40145BOUNDARY | OPEN Gen BOUNDG56_ 14.4 (46474) #56 | SoB>650 | CHECK |
| B_40145BOUNDARY | OPEN Gen BOUNDG54_ 14.4 (46470) #54 | SoB>650 | CHECK |
| B_40145BOUNDARY | OPEN Gen BOUNDG53_ 14.4 (46468) #53 | SoB>650 | CHECK |
| B_40145BOUNDARY | SET GENERATION AT BUS BOUNDG52_ 14.4 (46466) TO 100 MW | SoB>650 | CHECK |
| B_40149BRINKENS | OPEN Bus BRINKENS_115.0 (40149) |  | CHECK |
| B_40215CHENEY | OPEN Bus CHENEY_115.0 (40215) |  | CHECK |
| B_40239CLARKSTN | OPEN Bus CLARKSTN_115.0 (40239) |  | CHECK |
| B_40245CLAYTON | OPEN Bus CLAYTON_115.0 (40245) |  | CHECK |
| B_40255COLBERTT | OPEN Bus COLBERTT_115.0 (40255) |  | CHECK |
| B_40263COLVBPA | OPEN Bus COLV BPA_115.0 (40263) |  | CHECK |
| B_40275COOKMT | OPEN Bus COOK M T_115.0 (40275) |  | CHECK |
| B_40311CRESTN | OPEN Bus CRESTN_115.0 (40311) |  | CHECK |
| B_40317CUSICK | OPEN Bus CUSICK_115.0 (40317) |  | CHECK |
| B_40319CUSICK | OPEN Bus CUSICK_230.0 (40319) |  | CHECK |
| B_40337DEERPRK | OPEN Bus DEER PRK_115.0 (40337) |  | CHECK |
| B_40383EGRANVIL | OPEN Bus EGRANVIL_115.0 (40383) |  | CHECK |
| B_40384EGYPTTP | OPEN Bus EGYPT TP_115.0 (40384) |  | CHECK |
| B_40397FAIRCHLD | OPEN Bus FAIRCHLD_115.0 (40397) |  | CHECK |
| B_40439FOURLKS | OPEN Bus FOURLKS_115.0 (40439) |  | CHECK |
| B_40449GAFFNEY | OPEN Bus GAFFNEY_115.0 (40449) |  | CHECK |
| B_40483GREENBL | OPEN Bus GREEN BL_115.0 (40483) |  | CHECK |
| B_40495HALFMOON | OPEN Bus HALFMOON_115.0 (40495) |  | CHECK |
| B_40525HAYFORD | OPEN Bus HAYFORD_115.0 (40525) |  | CHECK |
| B_40577IRBY | OPEN Bus IRBY_115.0 (40577) |  | CHECK |
| B_40607KETTLET | OPEN Bus KETTLE T_115.0 (40607) |  | CHECK |
| B_40617LACLEDE | OPEN Bus LACLEDE_115.0 (40617) |  | CHECK |
| B_40624LANCASTR | OPEN Bus LANCASTR_230.0 (40624) |  | CHECK |
| B_40624LANCASTR | OPEN Gen LANCAS G_ 18.0 (47568) #1 |  | CHECK |
| B_40624LANCASTR | OPEN Gen LANCAS S_ 13.8 (47569) #1 |  | CHECK |
| B_40624LANCASTR | OPEN Bus LIB PH2_230.0 (44201) |  | CHECK |
| B_40730MEADTAP | OPEN Bus MEAD TAP_115.0 (40730) |  | CHECK |
| B_40731METALINE | OPEN Bus METALINE_115.0 (40731) |  | CHECK |
| B_40732METLNTAP | OPEN Bus METLNTAP_115.0 (40732) |  | CHECK |
| B_40779NEWPORTB | OPEN Bus NEWPORTB_115.0 (40779) |  | CHECK |
| B_40787NOXONBPA | OPEN Bus NOXONBPA_230.0 (40787) |  | CHECK |
| B_40787NOXONBPA | OPEN Bus LIB PH2_230.0 (44201) |  | CHECK |
| B_40855PRAIRIEB | OPEN Bus PRAIRIEB_115.0 (40855) |  | CHECK |
| B_40857PRIEST | OPEN Bus PRIEST_115.0 (40857) |  | CHECK |
| B_40879REPUBLIC | OPEN Bus REPUBLIC_115.0 (40879) |  | CHECK |
| B_40907SACHEEN | OPEN Bus SACHEEN_115.0 (40907) |  | CHECK |
| B_40909SACHEEN | OPEN Bus SACHEEN_230.0 (40909) |  | CHECK |
| B_40927SAMUEL &1 | OPEN Bus SAMUELS_115.0 (40927) |  | CHECK |
| B_40927SAMUELS | OPEN Bus SAMUELS_115.0 (40927) |  | CHECK |
| B_40928BONSAM11 | OPEN Bus BONSAM11_115.0 (40928) |  | CHECK |
| B_40929SANDCRK | OPEN Bus SAND CRK_115.0 (40929) |  | CHECK |
| B_40930BONSAM12 | OPEN Bus BONSAM12_115.0 (40930) |  | CHECK |
| B_40930SAMUEL &2 | OPEN Bus BONSAM12_115.0 (40930) |  | CHECK |
| B_40931SANDTP | OPEN Bus SAND TP_115.0 (40931) |  | CHECK |
| B_40933SANDPONT | OPEN Bus SANDPONT_115.0 (40933) |  | CHECK |
| B_40934SAND C&1 | OPEN Bus SANSAN11_115.0 (40934) |  | CHECK |
| B_40934SANSAN11 | OPEN Bus SANSAN11_115.0 (40934) |  | CHECK |
| B_40953SCARCELO | OPEN Bus SCARCELO_115.0 (40953) |  | CHECK |
| B_40965SELLE | OPEN Bus SELLE_115.0 (40965) |  | CHECK |
| B_41015SPRNGHIL | OPEN Bus SPRNGHIL_115.0 (41015) |  | CHECK |
| B_41089TRENTWOD | OPEN Bus TRENTWOD_115.0 (41089) |  | CHECK |
| B_41091TROUTCR | OPEN Bus TROUT CR_230.0 (41091) |  | CHECK |
| B_41097TROY | OPEN Bus TROY_115.0 (41097) |  | CHECK |
| B_41099TUMTUM | OPEN Bus TUM TUM_115.0 (41099) |  | CHECK |
| B_41107VALYWAY | OPEN Bus VALY WAY_115.0 (41107) |  | CHECK |
| B_41115VERA | OPEN Bus VERA_115.0 (41115) |  | CHECK |
| B_41117VERATAP | OPEN Bus VERA TAP_115.0 (41117) |  | CHECK |
| B_41125WAGNERLK | OPEN Bus WAGNERLK_115.0 (41125) |  | CHECK |
| B_41127WAGNERLT | OPEN Bus WAGNERLT_115.0 (41127) |  | CHECK |
| B_41169YAAK | OPEN Bus YAAK_115.0 (41169) |  | CHECK |
| B_41190BOXTAP | OPEN Bus BOX TAP_115.0 (41190) |  | CHECK |
| B_41239MOYIET | OPEN Bus MOYIE T_115.0 (41239) |  | CHECK |
| B_41240MOYIETX | OPEN Bus MOYIE TX_115.0 (41240) |  | CHECK |
| B_41241NBENCH | OPEN Bus N BENCH_115.0 (41241) |  | CHECK |
| B_41260SULLIVNB | OPEN Bus SULLIVNB_115.0 (41260) |  | CHECK |
| B_41275WESTBPA1 | OPEN Bus WESTBPA1_230.0 (41275) |  | CHECK |
| B_41276WESTBPA2 | OPEN Bus WESTBPA2_230.0 (41276) |  | CHECK |
| B_41298SMITHFLS | OPEN Bus SMITHFLS_ 13.8 (41298) |  | CHECK |
| B_41299SMITHFLS | OPEN Bus SMITHFLS_115.0 (41299) |  | CHECK |
| B_46151LARSON 230 | OPEN Bus LARSON_230.0 (46151) |  | CHECK |
| B_46156ROCKYFD 230 | OPEN Bus ROCKYFD_230.0 (46156) |  | CHECK |
| B_46619HEADWORK | OPEN Bus HEADWORK_ 13.8 (46619) |  | CHECK |
| B_46653SUMERFA1 | OPEN Bus SUMERFA1_ 13.8 (46653) |  | CHECK |
| B_46655SUMERFA2 | OPEN Bus SUMERFA2_ 13.8 (46655) |  | CHECK |
| B_47009BOXCANY | OPEN Bus BOX CANY_115.0 (47009) |  | CHECK |
| B_47010BOXCAN1 | OPEN Bus BOX CAN1_ 13.2 (47010) |  | CHECK |
| B_47012BOXCAN2 | OPEN Bus BOX CAN2_ 13.2 (47012) |  | CHECK |
| B_47014BOXCAN3 | OPEN Bus BOX CAN3_ 13.2 (47014) |  | CHECK |
| B_47016BOXCAN4 | OPEN Bus BOX CAN4_ 13.2 (47016) |  | CHECK |
| B_47025DELIGHT | OPEN Bus DELIGHT_115.0 (47025) |  | CHECK |
| B_47027DIAMLAK | OPEN Bus DIAM LAK_115.0 (47027) |  | CHECK |
| B_47033DOWERRD | OPEN Bus DOWER RD_115.0 (47033) |  | CHECK |
| B_47038EGYPT | OPEN Bus EGYPT_115.0 (47038) |  | CHECK |
| B_47073RALSTONB | OPEN Bus RALSTONB_115.0 (47073) |  | CHECK |
| B_47086PINEST | OPEN Bus PINE ST_115.0 (47086) |  | CHECK |
| B_47091USK | OPEN Bus USK_230.0 (47091) |  | CHECK |
| B_47126BOXPS | OPEN Bus BOX PS_115.0 (47126) |  | CHECK |
| B_47194MTHALL | OPEN Bus MT HALL_115.0 (47194) |  | CHECK |
| B_47254USK | OPEN Bus USK_115.0 (47254) |  | CHECK |
| B_47501ARMSTRNG | OPEN Bus ARMSTRNG_115.0 (47501) |  | CHECK |
| B_47503CHAMBERS | OPEN Bus CHAMBERS_115.0 (47503) |  | CHECK |
| B_47505HOODOO | OPEN Bus HOODOO_115.0 (47505) |  | CHECK |
| B_47507HOPKINSB | OPEN Bus HOPKINSB_115.0 (47507) |  | CHECK |
| B_47509MICA | OPEN Bus MICA_115.0 (47509) |  | CHECK |
| B_47511MOAB | OPEN Bus MOAB_115.0 (47511) |  | CHECK |
| B_47513W.PLAINS | OPEN Bus W.PLAINS_115.0 (47513) |  | CHECK |
| B_47568LANCASG | OPEN Bus LANCAS G_ 18.0 (47568) |  | CHECK |
| B_47569LANCASS | OPEN Bus LANCAS S_ 13.8 (47569) |  | CHECK |
| B_480014LAKETP | OPEN Bus 4LAKE TP_115.0 (48001) |  | CHECK |
| B_48003NELSONSB | OPEN Bus NELSONSB_115.0 (48003) |  | CHECK |
| B_48005NELSONTP | OPEN Bus NELSONT_115.0 (48005) |  | CHECK |
| B_48007ADDYAVA | OPEN Bus ADDY AVA_ 23.0 (48007) |  | CHECK |
| B_48009AIRWAYHT | OPEN Bus AIRWAYHT_115.0 (48009) |  | CHECK |
| B_48011APPLETAP | OPEN Bus APPLETAP_115.0 (48011) |  | CHECK |
| B_48013APPLEWAY | OPEN Bus APPLEWAY_115.0 (48013) |  | CHECK |
| B_48015ARDEN | OPEN Bus ARDEN_115.0 (48015) |  | CHECK |
| B_48017ATHOLTAP | OPEN Bus ATHOLTAP_115.0 (48017) |  | CHECK |
| B_48019AVONDALE | OPEN Bus AVONDALE_115.0 (48019) |  | CHECK |
| B_48021BARKER | OPEN Bus BARKER_115.0 (48021) |  | CHECK |
| B_48023BEACONN | OPEN Bus BEACON N_115.0 (48023) |  | CHECK |
| B_48025BEACONN | OPEN Bus BEACON N_230.0 (48025) |  | CHECK |
| B_48027BEACONS | OPEN Bus BEACON S_ 13.8 (48027) |  | CHECK |
| B_48029BEACONS | OPEN Bus BEACON S_115.0 (48029) |  | CHECK |
| B_48031BEACONS | OPEN Bus BEACON S_230.0 (48031) |  | CHECK |
| B_48033BELLTAP | OPEN Bus BELL TAP_115.0 (48033) |  | CHECK |
| B_48035BENEWAH | OPEN Bus BENEWAH_115.0 (48035) |  | CHECK |
| B_48037BENEWAH | OPEN Bus BENEWAH_230.0 (48037) |  | CHECK |
| B_48037BENEWAH | OPEN Gen NOXON34_ 14.4 (48287) #3 |  | CHECK |
| B_48037BENEWAH | OPEN Gen NOXON34_ 14.4 (48287) #4 |  | CHECK |
| B_48039BENTNAVA | OPEN Bus BENTNAVA_115.0 (48039) |  | CHECK |
| B_48041BIGCREEK | OPEN Bus BIGCREEK_115.0 (48041) |  | CHECK |
| B_48043BLANCHRD | OPEN Bus BLANCHRD_115.0 (48043) |  | CHECK |
| B_48045BLUECRK | OPEN Bus BLUECRK_115.0 (48045) |  | CHECK |
| B_48047BRONX | OPEN Bus BRONX_115.0 (48047) |  | CHECK |
| B_48049BUNKRHIL | OPEN Bus BUNKRHIL_115.0 (48049) |  | CHECK |
| B_48051BURKE | OPEN Bus BURKE_115.0 (48051) |  | CHECK |
| B_48053BURKAVAA | Unlinked Action: BUS 48053 OPEN |  | CHECK |
| B_48055BURKAVAB | Unlinked Action: BUS 48055 OPEN |  | CHECK |
| B_48057CABGORG | OPEN Bus CAB GORG_115.0 (48057) |  | CHECK |
| B_48059CABGORG | OPEN Bus CAB GORG_230.0 (48059) |  | CHECK |
| B_48059CABGORG | OPEN Gen NOXON12_ 14.4 (48285) #1 |  | CHECK |
| B_48059CABGORG | OPEN Gen NOXON12_ 14.4 (48285) #2 |  | CHECK |
| B_48059CABGORG | OPEN Gen NOXON34_ 14.4 (48287) #3 |  | CHECK |
| B_48059CABGORG | OPEN Gen NOXON34_ 14.4 (48287) #4 |  | CHECK |
| B_48061CABGOR12 | OPEN Bus CABGOR12_ 13.8 (48061) |  | CHECK |
| B_48063CABGOR34 | OPEN Bus CABGOR34_ 13.8 (48063) |  | CHECK |
| B_48065CABINETG | OPEN Bus CABINETG_115.0 (48065) |  | CHECK |
| B_48067CDA | OPEN Bus CDA_115.0 (48067) |  | CHECK |
| B_48069CHESTER | OPEN Bus CHESTER_115.0 (48069) |  | CHECK |
| B_48071CHEWELAH | OPEN Bus CHEWELAH_115.0 (48071) |  | CHECK |
| B_48073CHMBRSTP | OPEN Bus CHMBRSTP_115.0 (48073) |  | CHECK |
| B_48075CLEARWTR | OPEN Bus CLEARWTR_115.0 (48075) |  | CHECK |
| B_48077CLRKFORK | OPEN Bus CLRKFORK_115.0 (48077) |  | CHECK |
| B_48079COLBERT | OPEN Bus COLBERT_115.0 (48079) |  | CHECK |
| B_48081COLLWALN | OPEN Bus COLLWALN_115.0 (48081) |  | CHECK |
| B_48083COLVAVA | OPEN Bus COLV AVA_115.0 (48083) |  | CHECK |
| B_48085COLVILLE | OPEN Bus COLVILLE_ 13.8 (48085) |  | CHECK |
| B_48087COTTNWDT | OPEN Bus COTTNWDT_115.0 (48087) |  | CHECK |
| B_48089COTTNWOD | OPEN Bus COTTNWOD_115.0 (48089) |  | CHECK |
| B_48091CRAIGMNT | OPEN Bus CRAIGMNT_115.0 (48091) |  | CHECK |
| B_48093DALTONA | OPEN Bus DALTON A_115.0 (48093) |  | CHECK |
| B_48095DALTON2T | OPEN Bus DALTON2T_115.0 (48095) |  | CHECK |
| B_48097DALTONT | OPEN Bus DALTONT_115.0 (48097) |  | CHECK |
| B_48099DAVENPRT | OPEN Bus DAVENPRT_115.0 (48099) |  | CHECK |
| B_48101DEARY | OPEN Bus DEARY_115.0 (48101) |  | CHECK |
| B_48103DEVILGP | OPEN Bus DEVIL GP_115.0 (48103) |  | CHECK |
| B_48105DEVILGP2 | OPEN Bus DEVILGP2_115.0 (48105) |  | CHECK |
| B_48109DIAMOND | OPEN Bus DIAMOND_115.0 (48109) |  | CHECK |
| B_48111DOWERRDT | OPEN Bus DOWERRDT_115.0 (48111) |  | CHECK |
| B_48113DRYGULCH | OPEN Bus DRYGULCH_115.0 (48113) |  | CHECK |
| B_48115EASCOLFX | OPEN Bus EASCOLFX_115.0 (48115) |  | CHECK |
| B_48117EASTFARM | OPEN Bus EASTFARM_115.0 (48117) |  | CHECK |
| B_48119EGRANTAP | OPEN Bus EGRANTAP_115.0 (48119) |  | CHECK |
| B_48121EWAN | OPEN Bus EWAN_115.0 (48121) |  | CHECK |
| B_48122FAIRS | OPEN Bus FAIR S_115.0 (48122) |  | CHECK |
| B_48123FORD | OPEN Bus FORD_115.0 (48123) |  | CHECK |
| B_48125FOURLBPA | OPEN Bus FOURLBPA_115.0 (48125) |  | CHECK |
| B_48127FRANCEDR | OPEN Bus FRANCEDR_115.0 (48127) |  | CHECK |
| B_48129FTWRIGHT | OPEN Bus FTWRIGHT_115.0 (48129) |  | CHECK |
| B_48131GARDENSP | OPEN Bus GARDENSP_115.0 (48131) |  | CHECK |
| B_48132HAL&WHIT | OPEN Bus HAL&WHIT_115.0 (48132) |  | CHECK |
| B_48133GARFIELD | OPEN Bus GARFIELD_115.0 (48133) |  | CHECK |
| B_48135GIFFORD | OPEN Bus GIFFORD_115.0 (48135) |  | CHECK |
| B_48137GLENROSE | OPEN Bus GLENROSE_115.0 (48137) |  | CHECK |
| B_48139GLENTAP | OPEN Bus GLENTAP_115.0 (48139) |  | CHECK |
| B_48141GRANGVIL | OPEN Bus GRANGVIL_115.0 (48141) |  | CHECK |
| B_48143GREENWDA | OPEN Bus GREENWDA_115.0 (48143) |  | CHECK |
| B_48145HANGMAN | OPEN Bus HANGMAN_115.0 (48145) |  | CHECK |
| B_48147HARRNGTN | OPEN Bus HARRNGTN_115.0 (48147) |  | CHECK |
| B_48148HAYDEN | OPEN Bus HAYDEN_115.0 (48148) |  | CHECK |
| B_48149HEADWORK | OPEN Bus HEADWORK_115.0 (48149) |  | CHECK |
| B_48151HECLA | OPEN Bus HECLA_115.0 (48151) |  | CHECK |
| B_48153HECLAT | OPEN Bus HECLAT_115.0 (48153) |  | CHECK |
| B_48155HERN | OPEN Bus HERN_115.0 (48155) |  | CHECK |
| B_48157HOLBROOK | OPEN Bus HOLBROOK_115.0 (48157) |  | CHECK |
| B_48159HUETTER | OPEN Bus HUETTER_115.0 (48159) |  | CHECK |
| B_48163I.E.PAPR | OPEN Bus I.E.PAPR_115.0 (48163) |  | CHECK |
| B_48165IRVIN | OPEN Bus IRVIN_115.0 (48165) |  | CHECK |
| B_48167JAYPE | OPEN Bus JAYPE_115.0 (48167) |  | CHECK |
| B_48169JULIAETT | OPEN Bus JULIAETT_115.0 (48169) |  | CHECK |
| B_48171KAMIAH | OPEN Bus KAMIAH_115.0 (48171) |  | CHECK |
| B_48173KETTLEAV | OPEN Bus KETTLEAV_ 13.8 (48173) |  | CHECK |
| B_48175KETTLEAV | OPEN Bus KETTLEAV_115.0 (48175) |  | CHECK |
| B_48177KOOSKIA | OPEN Bus KOOSKIA_115.0 (48177) |  | CHECK |
| B_48179LAKEVIEW | OPEN Bus LAKEVIEW_230.0 (48179) |  | CHECK |
| B_48179LAKEVIEW | OPEN Gen NOXON12_ 14.4 (48285) #1 |  | CHECK |
| B_48179LAKEVIEW | OPEN Gen NOXON12_ 14.4 (48285) #2 |  | CHECK |
| B_48179LAKEVIEW | OPEN Gen NOXON34_ 14.4 (48287) #3 |  | CHECK |
| B_48179LAKEVIEW | OPEN Gen NOXON34_ 14.4 (48287) #4 |  | CHECK |
| B_48181LATAH | OPEN Bus LATAH_115.0 (48181) |  | CHECK |
| B_48183LEON | OPEN Bus LEON_115.0 (48183) |  | CHECK |
| B_48185LIBTYLK | OPEN Bus LIBTYLK_115.0 (48185) |  | CHECK |
| B_48187LIND | OPEN Bus LIND_115.0 (48187) |  | CHECK |
| B_48189LITFAL12 | OPEN Bus LITFAL12_ 4.0 (48189) |  | CHECK |
| B_48191LITFAL34 | OPEN Bus LITFAL34_ 4.0 (48191) |  | CHECK |
| B_48193LITTFALL | OPEN Bus LITTFALL_115.0 (48193) |  | CHECK |
| B_48194LOCUST | OPEN Bus LOCUST_115.0 (48194) |  | CHECK |
| B_48195LOLO | OPEN Bus LOLO_115.0 (48195) |  | CHECK |
| B_48197LOLO | OPEN Bus LOLO_230.0 (48197) |  | CHECK |
| B_48199LONGLAKA | OPEN Bus LONGLAKA_115.0 (48199) |  | CHECK |
| B_48201LONGLAKB | OPEN Bus LONGLAKB_115.0 (48201) |  | CHECK |
| B_48203LONGLAKT | OPEN Bus LONGLAKT_115.0 (48203) |  | CHECK |
| B_48205LONGLKG1 | OPEN Bus LONGLKG1_ 4.0 (48205) |  | CHECK |
| B_48207LONGLKG2 | OPEN Bus LONGLKG2_ 4.0 (48207) |  | CHECK |
| B_48209LONGLKG3 | OPEN Bus LONGLKG3_ 4.0 (48209) |  | CHECK |
| B_48211LONGLKG4 | OPEN Bus LONGLKG4_ 4.0 (48211) |  | CHECK |
| B_48213LOONLK | OPEN Bus LOON LK_115.0 (48213) |  | CHECK |
| B_48215LUCKYF | OPEN Bus LUCKY F_115.0 (48215) |  | CHECK |
| B_48217LUCKYFTP | OPEN Bus LUCKYFTP_115.0 (48217) |  | CHECK |
| B_48219LYONSTND | OPEN Bus LYONSTND_115.0 (48219) |  | CHECK |
| B_48221MARENGO | OPEN Bus MARENGO_115.0 (48221) |  | CHECK |
| B_48222MEADSUB | OPEN Bus MEAD SUB_115.0 (48222) |  | CHECK |
| B_48223METCHIP | OPEN Bus METCHIP_115.0 (48223) |  | CHECK |
| B_48225METRO | OPEN Bus METRO_115.0 (48225) |  | CHECK |
| B_48227MEYERSFL | OPEN Bus MEYERSFL_ 11.0 (48227) |  | CHECK |
| B_48229MEYERSFL | OPEN Bus MEYERSFL_ 13.0 (48229) |  | CHECK |
| B_48231MICATAP | OPEN Bus MICA TAP_115.0 (48231) |  | CHECK |
| B_48233MILAN | OPEN Bus MILAN_115.0 (48233) |  | CHECK |
| B_48235MILANTP | OPEN Bus MILAN TP_115.0 (48235) |  | CHECK |
| B_48237MILLWOOD | OPEN Bus MILLWOOD_115.0 (48237) |  | CHECK |
| B_48239MISSION | OPEN Bus MISSION_115.0 (48239) |  | CHECK |
| B_48241MONROEA | OPEN Bus MONROEA_ 13.8 (48241) |  | CHECK |
| B_48243MOSCCITY | OPEN Bus MOSCCITY_115.0 (48243) |  | CHECK |
| B_48245MOSCITYT | OPEN Bus MOSCITYT_115.0 (48245) |  | CHECK |
| B_48247MOSCOW | OPEN Bus MOSCOW_115.0 (48247) |  | CHECK |
| B_48249MOSCOW | OPEN Bus MOSCOW_230.0 (48249) |  | CHECK |
| B_48251MOSCOWX | OPEN Bus MOSCOWX_115.0 (48251) |  | CHECK |
| B_48253NLEWIST | OPEN Bus N LEWIST_115.0 (48253) |  | CHECK |
| B_48255NLEWIST | OPEN Bus N LEWIST_230.0 (48255) |  | CHECK |
| B_48258NEWPORTT | OPEN Bus NEWPORTT_115.0 (48258) |  | CHECK |
| B_48261NEZPERCE | OPEN Bus NEZPERCE_115.0 (48261) |  | CHECK |
| B_48263NINEFLSE | OPEN Bus NINEFLSE_ 30.0 (48263) |  | CHECK |
| B_48265NINEMI12 | OPEN Bus NINEMI12_ 2.3 (48265) |  | CHECK |
| B_48267NINEMI34 | OPEN Bus NINEMI34_ 13.8 (48267) |  | CHECK |
| B_48269NINEMILE | OPEN Bus NINEMILE_115.0 (48269) |  | CHECK |
| B_48271NINTHCNT | OPEN Bus NINTHCNT_115.0 (48271) |  | CHECK |
| B_48273NMOSCOW | OPEN Bus NMOSCOW_115.0 (48273) |  | CHECK |
| B_48275NORTHEAS | OPEN Bus NORTHEAS_ 13.8 (48275) |  | CHECK |
| B_48277NORTHEAS | OPEN Bus NORTHEAS_115.0 (48277) |  | CHECK |
| B_48279NORTHWES | OPEN Bus NORTHWES_115.0 (48279) |  | CHECK |
| B_48281NOXON | OPEN Bus NOXON_230.0 (48281) |  | CHECK |
| B_48281NOXON | OPEN Gen NOXON12_ 14.4 (48285) #1 |  | CHECK |
| B_48281NOXON | OPEN Gen NOXON12_ 14.4 (48285) #2 |  | CHECK |
| B_48281NOXON | OPEN Gen NOXON34_ 14.4 (48287) #3 |  | CHECK |
| B_48281NOXON | OPEN Gen NOXON34_ 14.4 (48287) #4 |  | CHECK |
| B_48283NOXON5 | OPEN Bus NOXON 5_ 14.4 (48283) |  | CHECK |
| B_48285NOXON12 | OPEN Bus NOXON12_ 14.4 (48285) |  | CHECK |
| B_48287NOXON34 | OPEN Bus NOXON34_ 14.4 (48287) |  | CHECK |
| B_48289NOXONCON | OPEN Bus NOXONCON_230.0 (48289) |  | CHECK |
| B_48291NPULLMAN | OPEN Bus NPULLMAN_115.0 (48291) |  | CHECK |
| B_48293ODEN | OPEN Bus ODEN_115.0 (48293) |  | CHECK |
| B_48295ODESSA | OPEN Bus ODESSA_115.0 (48295) |  | CHECK |
| B_48297OGARA | OPEN Bus OGARA_115.0 (48297) |  | CHECK |
| B_48298OLDTOWN | OPEN Bus OLDTOWN_115.0 (48298) |  | CHECK |
| B_48299OPPORTUN | OPEN Bus OPPORTUN_115.0 (48299) |  | CHECK |
| B_48300OLDTOWNA | OPEN Bus OLDTOWNA_115.0 (48300) |  | CHECK |
| B_48301ORIN | OPEN Bus ORIN_115.0 (48301) |  | CHECK |
| B_48303OROFINO | OPEN Bus OROFINO_115.0 (48303) |  | CHECK |
| B_48305OSBURN | OPEN Bus OSBURN_115.0 (48305) |  | CHECK |
| B_48307OTHELLO | OPEN Bus OTHELLO_115.0 (48307) |  | CHECK |
| B_48308LEE&REYN | OPEN Bus LEE&REYN_115.0 (48308) |  | CHECK |
| B_48309OTHELOSS | OPEN Bus OTHELOSS_115.0 (48309) |  | CHECK |
| B_48311OTIS | OPEN Bus OTIS_115.0 (48311) |  | CHECK |
| B_48313PALOUSE | OPEN Bus PALOUSE_115.0 (48313) |  | CHECK |
| B_48315PINECRK | OPEN Bus PINE CRK_115.0 (48315) |  | CHECK |
| B_48317PINECRK | OPEN Bus PINE CRK_230.0 (48317) |  | CHECK |
| B_48317PINECRK | OPEN Gen NOXON34_ 14.4 (48287) #3 |  | CHECK |
| B_48317PINECRK | OPEN Gen NOXON34_ 14.4 (48287) #4 |  | CHECK |
| B_48319PLEASANT | OPEN Bus PLEASANT_115.0 (48319) |  | CHECK |
| B_48321PLUMMER | OPEN Bus PLUMMER_ 4.2 (48321) |  | CHECK |
| B_48323PLUMMER | OPEN Bus PLUMMER_115.0 (48323) |  | CHECK |
| B_48325PLUMMERG | OPEN Bus PLUMMERG_ 13.8 (48325) |  | CHECK |
| B_48327PLUMMWEA | OPEN Bus PLUMMWEA_ 13.8 (48327) |  | CHECK |
| B_48329POSTFLS | OPEN Bus POST FLS_115.0 (48329) |  | CHECK |
| B_48331POSTFL15 | OPEN Bus POSTFL15_ 2.4 (48331) |  | CHECK |
| B_48333POSTFLS6 | OPEN Bus POSTFLS6_ 2.4 (48333) |  | CHECK |
| B_48335POSTSTRT | OPEN Bus POSTSTRT_ 4.2 (48335) |  | CHECK |
| B_48337POSTSTRT | OPEN Bus POSTSTRT_ 13.8 (48337) |  | CHECK |
| B_48339POSTSTRT | OPEN Bus POSTSTRT_115.0 (48339) |  | CHECK |
| B_48341POTLATA | OPEN Bus POTLAT A_115.0 (48341) |  | CHECK |
| B_48343POUNDLNE | OPEN Bus POUNDLNE_115.0 (48343) |  | CHECK |
| B_48345POUNDTAP | OPEN Bus POUNDTAP_115.0 (48345) |  | CHECK |
| B_48347PRIESTA | OPEN Bus PRIEST A_115.0 (48347) |  | CHECK |
| B_48349RAMSEY | OPEN Bus RAMSEY_115.0 (48349) |  | CHECK |
| B_48351RATHBUS1 | OPEN Bus RATHBUS1_115.0 (48351) |  | CHECK |
| B_48353RATHBUS2 | OPEN Bus RATHBUS2_115.0 (48353) |  | CHECK |
| B_48355RATHDRUM | OPEN Bus RATHDRUM_115.0 (48355) |  | CHECK |
| B_48356RATHDRME | OPEN Bus RATHDRME_115.0 (48356) |  | CHECK |
| B_48359RATHGEN1 | OPEN Bus RATHGEN1_ 13.8 (48359) |  | CHECK |
| B_48361RATHGEN2 | OPEN Bus RATHGEN2_ 13.8 (48361) |  | CHECK |
| B_48363REARDAN | OPEN Bus REARDAN_115.0 (48363) |  | CHECK |
| B_48365RITZVILL | OPEN Bus RITZVILL_115.0 (48365) |  | CHECK |
| B_48367ROCKFORD | OPEN Bus ROCKFORD_115.0 (48367) |  | CHECK |
| B_48369ROSALIA | OPEN Bus ROSALIA_115.0 (48369) |  | CHECK |
| B_48371ROSSPARK | OPEN Bus ROSSPARK_115.0 (48371) |  | CHECK |
| B_48373ROUNDLKT | OPEN Bus ROUNDLKT_115.0 (48373) |  | CHECK |
| B_48375ROXBORO | OPEN Bus ROXBORO_115.0 (48375) |  | CHECK |
| B_48376SAGLE | OPEN Bus SAGLE_115.0 (48376) |  | CHECK |
| B_48377SANDPTA | OPEN Bus SANDPT A_115.0 (48377) |  | CHECK |
| B_48379SCOTPAPR | OPEN Bus SCOTPAPR_115.0 (48379) |  | CHECK |
| B_48381SEVENTAP | OPEN Bus SEVENTAP_115.0 (48381) |  | CHECK |
| B_48383SHAWNEE | OPEN Bus SHAWNEE_115.0 (48383) |  | CHECK |
| B_48385SHAWNEE | OPEN Bus SHAWNEE_230.0 (48385) |  | CHECK |
| B_48387SILVRLAK | OPEN Bus SILVRLAK_115.0 (48387) |  | CHECK |
| B_48388SILVRLK2 | OPEN Bus SILVRLK2_115.0 (48388) |  | CHECK |
| B_48389SLEWIST | OPEN Bus SLEWIST_115.0 (48389) |  | CHECK |
| B_48391SOTHELLO | OPEN Bus SOTHELLO_115.0 (48391) |  | CHECK |
| B_48393SOTHELOT | OPEN Bus SOTHELOT_115.0 (48393) |  | CHECK |
| B_48395SOUTHEAS | OPEN Bus SOUTHEAS_115.0 (48395) |  | CHECK |
| B_48397SPANGLE | OPEN Bus SPANGLE_115.0 (48397) |  | CHECK |
| B_48399SPIRIT | OPEN Bus SPIRIT_115.0 (48399) |  | CHECK |
| B_48401SPIRITLK | OPEN Bus SPIRITLK_115.0 (48401) |  | CHECK |
| B_48403SPIRITLT | OPEN Bus SPIRITLT_115.0 (48403) |  | CHECK |
| B_48405SPKINDPK | OPEN Bus SPKINDPK_115.0 (48405) |  | CHECK |
| B_48407SPKWASTE | OPEN Bus SPKWASTE_ 13.8 (48407) |  | CHECK |
| B_48409SPKWASTE | OPEN Bus SPKWASTE_115.0 (48409) |  | CHECK |
| B_48411SPRAGUE | OPEN Bus SPRAGUE_115.0 (48411) |  | CHECK |
| B_48413SPULLMAN | OPEN Bus SPULLMAN_115.0 (48413) |  | CHECK |
| B_48417STMARIES | OPEN Bus STMARIES_115.0 (48417) |  | CHECK |
| B_48419STRATFRD | OPEN Bus STRATFRD_115.0 (48419) |  | CHECK |
| B_48421SUNSET | OPEN Bus SUNSET_115.0 (48421) |  | CHECK |
| B_48423SWEETWTR | OPEN Bus SWEETWTR_115.0 (48423) |  | CHECK |
| B_48425TAUNTON | OPEN Bus TAUNTON_115.0 (48425) |  | CHECK |
| B_48427TEKOA | OPEN Bus TEKOA_115.0 (48427) |  | CHECK |
| B_48429TENTHSTW | OPEN Bus TENTHSTW_115.0 (48429) |  | CHECK |
| B_48430TERRVIEW | OPEN Bus TERRVIEW_115.0 (48430) |  | CHECK |
| B_48431THIRHACH | OPEN Bus THIRHACH_115.0 (48431) |  | CHECK |
| B_48433UPRIVER | OPEN Bus UPRIVER_ 2.4 (48433) |  | CHECK |
| B_48435UPRIVER | OPEN Bus UPRIVER_ 4.2 (48435) |  | CHECK |
| B_48437UPRIVER | OPEN Bus UPRIVER_ 13.8 (48437) |  | CHECK |
| B_48439VAAGEN | OPEN Bus VAAGEN_ 4.2 (48439) |  | CHECK |
| B_48441VALLEYA | OPEN Bus VALLEY A_115.0 (48441) |  | CHECK |
| B_48443VANTAVA | OPEN Bus VANT AVA_230.0 (48443) |  | CHECK |
| B_48445VIOLA | OPEN Bus VIOLA_115.0 (48445) |  | CHECK |
| B_48447WAIKIKI | OPEN Bus WAIKIKI_115.0 (48447) |  | CHECK |
| B_48449WAIKIKIT | OPEN Bus WAIKIKIT_115.0 (48449) |  | CHECK |
| B_48451WALAAVA | OPEN Bus WALA AVA_230.0 (48451) |  | CHECK |
| B_48453WALLACE | OPEN Bus WALLACE_115.0 (48453) |  | CHECK |
| B_48455WARDENA | OPEN Bus WARDEN A_115.0 (48455) |  | CHECK |
| B_48457WASHTUNA | OPEN Bus WASHTUNA_115.0 (48457) |  | CHECK |
| B_48459WEIPPE | OPEN Bus WEIPPE_115.0 (48459) |  | CHECK |
| B_48461WEST | OPEN Bus WEST_115.0 (48461) |  | CHECK |
| B_48463WEST | OPEN Bus WEST_230.0 (48463) |  | CHECK |
| B_48465WICKES | OPEN Bus WICKES_115.0 (48465) |  | CHECK |
| B_48467WILBUR | OPEN Bus WILBUR_115.0 (48467) |  | CHECK |
| B_48469WILBURT | OPEN Bus WILBURT_115.0 (48469) |  | CHECK |
| B_48471WILSNCKT | OPEN Bus WILSNCKT_115.0 (48471) |  | CHECK |
| B_48475CLWTR1 | OPEN Bus CLWTR1_ 34.5 (48475) |  | CHECK |
| B_48476CLWTR2 | OPEN Bus CLWTR2_ 34.5 (48476) |  | CHECK |
| B_48477CLWTR3 | OPEN Bus CLWTR3_ 34.5 (48477) |  | CHECK |
| B_48478CLWTR4 | OPEN Bus CLWTR4_ 34.5 (48478) |  | CHECK |
| B_48479CLWTR5 | OPEN Bus CLWTR5_ 34.5 (48479) |  | CHECK |
| B_48480CLWTR6 | OPEN Bus CLWTR6_ 34.5 (48480) |  | CHECK |
| B_48481CLWTR7 | OPEN Bus CLWTR7_ 34.5 (48481) |  | CHECK |
| B_48482CWGEN3 | OPEN Bus CWGEN3_ 12.0 (48482) |  | CHECK |
| B_48483CWGEN4 | OPEN Bus CWGEN4_ 12.0 (48483) |  | CHECK |
| B_48484CWTW1 | OPEN Bus CWTW1_ 12.0 (48484) |  | CHECK |
| B_48485CWTW2 | OPEN Bus CWTW2_ 12.0 (48485) |  | CHECK |
| B_48486CWTW3 | OPEN Bus CWTW3_ 12.0 (48486) |  | CHECK |
| B_48487CWTW4 | OPEN Bus CWTW4_ 12.0 (48487) |  | CHECK |
| B_48488CWTW5 | OPEN Bus CWTW5_ 12.0 (48488) |  | CHECK |
| B_48489CWTW6 | OPEN Bus CWTW6_ 12.0 (48489) |  | CHECK |
| B_48490CWBUS1 | OPEN Bus CWBUS1_ 12.0 (48490) |  | CHECK |
| B_48491CWBUS2 | OPEN Bus CWBUS2_ 12.0 (48491) |  | CHECK |
| B_48492CWBUS3 | OPEN Bus CWBUS3_ 12.0 (48492) |  | CHECK |
| B_48493CWBUS4 | OPEN Bus CWBUS4_ 12.0 (48493) |  | CHECK |
| B_48494CWBUS5 | OPEN Bus CWBUS5_ 12.0 (48494) |  | CHECK |
| B_48495CWBUS6 | OPEN Bus CWBUS6_ 12.0 (48495) |  | CHECK |
| B_48496CWBUS7 | OPEN Bus CWBUS7_ 12.0 (48496) |  | CHECK |
| B_48497CWBUS8 | OPEN Bus CWBUS8_ 12.0 (48497) |  | CHECK |
| B_48510DRYCREEK | OPEN Bus DRYCREEK_115.0 (48510) |  | CHECK |
| B_48512DRYCREEK | OPEN Bus DRYCREEK_230.0 (48512) |  | CHECK |
| B_48514CRCHFELD | OPEN Bus CRCHFELD_115.0 (48514) |  | CHECK |
| B_48520BOULDERW | OPEN Bus BOULDERW_115.0 (48520) |  | CHECK |
| B_48522BOULDERE | OPEN Bus BOULDERE_115.0 (48522) |  | CHECK |
| B_48524BOULDER | OPEN Bus BOULDER_230.0 (48524) |  | CHECK |
| B_48526BOULDERG | OPEN Bus BOULDERG_ 13.8 (48526) |  | CHECK |
| B_Hatwai 230 Bus (BPA) | OPEN Bus HATWAI_230.0 (40519) |  | CHECK |
| B_Hot Springs 230 Bus (BPA) | OPEN Bus HOT SPR_230.0 (40551) |  | CHECK |
| B_Hot Springs 230 Bus (BPA) | OPEN Gen HUNGHR34_ 13.8 (40556) #3 |  | ALWAYS |
| B_Hot Springs 230 Bus (BPA) | OPEN Gen HUNGHR34_ 13.8 (40556) #4 |  | ALWAYS |
| B_Hot Springs 230 Bus (BPA) | OPEN Bus LIB PH2_230.0 (44201) |  | CHECK |
| BKR_BEACON 115 BUS TIE BREAKER FAIL | OPEN Bus BEACON N_115.0 (48023) |  | CHECK |
| BKR_BEACON 115 BUS TIE BREAKER FAIL | OPEN Bus BEACON S_115.0 (48029) |  | CHECK |
| BKR_BEACON 230 BUS TIE BREAKER FAIL | OPEN Bus BEACON S_230.0 (48031) |  | CHECK |
| BKR_BEACON 230 BUS TIE BREAKER FAIL | OPEN Bus BEACON N_230.0 (48025) |  | CHECK |
| BKR_DWORSHAK 500 BREAKER FAIL (BPA) | OPEN Bus DWORSHAK_500.0 (40369) |  | CHECK |
| BKR_DWORSHAK 500 BREAKER FAIL (BPA) | OPEN Branch DWOR 1_ 13.8 (40361) TO DWOR 2_ 13.8 (40363) CKT 1 |  | CHECK |
| BKR_DWORSHAK 500 BREAKER FAIL (BPA) | OPEN Gen DWOR 2_ 13.8 (40363) #1 |  | CHECK |
| BKR_DWORSHAK 500 BREAKER FAIL (BPA) | OPEN Gen DWOR 3_ 13.8 (40365) #1 |  | CHECK |
| BKR_DWORSHAK 500 BREAKER FAIL (BPA) | OPEN Load MILCTYDC_230.0 (63010) #D1 |  | CHECK |
| BKR_DWORSHAK 500 BREAKER FAIL (BPA) | OPEN Shunt GARRISON_500.0 (40459) #r |  | CHECK |
| BKR_DWORSHAK 500 BREAKER FAIL (BPA) | OPEN Bus LIB PH1_230.0 (44200) | West MT Hydro > 1000 | CHECK |
| BKR_DWORSHAK 500 BREAKER FAIL (BPA) | OPEN Bus LIB PH2_230.0 (44201) | West MT Hydro > 1000 | CHECK |
| BKR_HATWAI 500 BREAKER FAIL (BPA) | OPEN Shunt GARRISON_500.0 (40459) #r |  | CHECK |
| BKR_HATWAI 500 BREAKER FAIL (BPA) | OPEN Branch DWOR 1_ 13.8 (40361) TO DWOR 2_ 13.8 (40363) CKT 1 |  | CHECK |
| BKR_HATWAI 500 BREAKER FAIL (BPA) | OPEN Bus HATWAI_500.0 (40521) |  | CHECK |
| BKR_HATWAI 500 BREAKER FAIL (BPA) | OPEN Gen DWOR 3_ 13.8 (40365) #1 |  | CHECK |
| BKR_HATWAI 500 BREAKER FAIL (BPA) | OPEN Gen DWOR 2_ 13.8 (40363) #1 |  | CHECK |
| BKR_HATWAI 500 BREAKER FAIL (BPA) | OPEN Load MILCTYDC_230.0 (63010) #D1 |  | CHECK |
| BKR_HATWAI 500 BREAKER FAIL (BPA) | OPEN Bus LIB PH2_230.0 (44201) | West MT Hydro > 1000 | CHECK |
| BKR_HATWAI 500 BREAKER FAIL (BPA) | OPEN Bus LIB PH1_230.0 (44200) | West MT Hydro > 1000 | CHECK |
| BKR_HATWAI 500 BREAKER FAIL (BPA) | OPEN Gen LANCAS S_ 13.8 (47569) #1 | WEST OF HATWAI > 3500 | CHECK |
| BKR_HATWAI 500 BREAKER FAIL (BPA) | OPEN Gen LANCAS G_ 18.0 (47568) #1 | WEST OF HATWAI > 3500 | CHECK |
| BKR_NOXON 230 BUS TIE BREAKER FAIL | OPEN Bus NOXON_230.0 (48281) |  | CHECK |
| BKR_NOXON 230 BUS TIE BREAKER FAIL | OPEN Bus NOXONBPA_230.0 (40787) |  | CHECK |
| BKR_NOXON 230 BUS TIE BREAKER FAIL | OPEN Gen NOXON12_ 14.4 (48285) #1 |  | CHECK |
| BKR_NOXON 230 BUS TIE BREAKER FAIL | OPEN Gen NOXON12_ 14.4 (48285) #2 |  | CHECK |
| BKR_NOXON 230 BUS TIE BREAKER FAIL | OPEN Gen NOXON34_ 14.4 (48287) #3 |  | CHECK |
| BKR_NOXON 230 BUS TIE BREAKER FAIL | OPEN Gen NOXON34_ 14.4 (48287) #4 |  | CHECK |
| BKR_NOXON 230 BUS TIE BREAKER FAIL | OPEN Bus LIB PH2_230.0 (44201) |  | CHECK |
| L_40017ADDY-40263COLVBPAC1 | OPEN Branch ADDY_115.0 (40017) TO COLV BPA_115.0 (40263) CKT 1 |  | CHECK |
| L_40017ADDY-48071CHEWELAHC1 | OPEN Branch ADDY_115.0 (40017) TO CHEWELAH_115.0 (48071) CKT 1 |  | CHECK |
| L_40017ADDY-48135GIFFORDC1 | OPEN Branch ADDY_115.0 (40017) TO GIFFORD_115.0 (48135) CKT 1 |  | CHECK |
| L_40017ADDY-48213LOONLKC1 | OPEN Branch ADDY_115.0 (40017) TO LOON LK_115.0 (48213) CKT 1 |  | CHECK |
| L_40017ADDY-48223METCHIPC1 | OPEN Branch ADDY_115.0 (40017) TO METCHIP_115.0 (48223) CKT 1 |  | CHECK |
| L_40019ADDY-40021ADDY2C1 | OPEN Branch ADDY_230.0 (40019) TO ADDY 2_230.0 (40021) CKT 1 |  | CHECK |
| L_40019ADDY-40319CUSICKC1 | OPEN Branch ADDY_230.0 (40019) TO CUSICK_230.0 (40319) CKT 1 |  | CHECK |
| L_40021ADDY2-40090BELLS3C1_MS | OPEN MultiSectionLine ADDY 2_230.0 (40021) TO BELL S3_230.0 (40090) CKT 1 |  | CHECK |
| L_40021ADDY2-40090BELLS3C1_MS | OPEN Gen BOUNDG56_ 14.4 (46474) #56 | South of Boundary > 650 | CHECK |
| L_40021ADDY2-40090BELLS3C1_MS | OPEN Gen BOUNDG55_ 14.4 (46472) #55 | South of Boundary > 650 | CHECK |
| L_40021ADDY2-40145BOUNDARYC1_MS | OPEN MultiSectionLine ADDY 2_230.0 (40021) TO BOUNDARY_230.0 (40145) CKT 1 |  | CHECK |
| L_40021ADDY2-40145BOUNDARYC1_MS | OPEN Gen BOUNDG56_ 14.4 (46474) #56 | South of Boundary > 650 | CHECK |
| L_40021ADDY2-40145BOUNDARYC1_MS | OPEN Gen BOUNDG55_ 14.4 (46472) #55 | South of Boundary > 650 | CHECK |
| L_40023AHSAHKA-40367DWORSHAKC1 | OPEN Branch AHSAHKA_115.0 (40023) TO DWORSHAK_115.0 (40367) CKT 1 |  | CHECK |
| L_40023AHSAHKA-48303OROFINOC1 | OPEN Branch AHSAHKA_115.0 (40023) TO OROFINO_115.0 (48303) CKT 1 |  | CHECK |
| L_40029ALBENIF-40779NEWPORTBC1 | OPEN Branch ALBENI F_115.0 (40029) TO NEWPORTB_115.0 (40779) CKT 1 |  | CHECK |
| L_40029ALBENIF-47027DIAMLAKC1 | OPEN Branch ALBENI F_115.0 (40029) TO DIAM LAK_115.0 (47027) CKT 1 |  | CHECK |
| L_40029ALBENIF-48347PRIESTAC1 | OPEN Branch ALBENI F_115.0 (40029) TO PRIEST A_115.0 (48347) CKT 1 |  | CHECK |
| L_40067ATHOL-48017ATHOLTAPC1 | OPEN Branch ATHOL_115.0 (40067) TO ATHOLTAP_115.0 (48017) CKT 1 |  | CHECK |
| L_40086BELLS1-40088BELLS2C1 | OPEN Branch BELL S1_230.0 (40086) TO BELL S2_230.0 (40088) CKT 1 |  | CHECK |
| L_40086BELLS1-40092BELLS4C1 | OPEN Branch BELL S1_230.0 (40086) TO BELL S4_230.0 (40092) CKT 1 |  | CHECK |
| L_40086BELLS1-40909SACHEENC1 | OPEN Branch BELL S1_230.0 (40086) TO SACHEEN_230.0 (40909) CKT 1 |  | CHECK |
| L_40086BELLS1-40909SACHEENC1 | OPEN Gen BOUNDG55_ 14.4 (46472) #55 | South of Boundary > 650 | CHECK |
| L_40086BELLS1-40909SACHEENC1 | OPEN Gen BOUNDG56_ 14.4 (46474) #56 | South of Boundary > 650 | CHECK |
| L_40086BELLS1-41275WESTBPA1C1 | OPEN Branch BELL S1_230.0 (40086) TO WESTBPA1_230.0 (41275) CKT 1 |  | CHECK |
| L_40087BELLBPA-40113BIGELOWC1 | OPEN Branch BELL BPA_115.0 (40087) TO BIGELOW_115.0 (40113) CKT 1 |  | CHECK |
| L_40087BELLBPA-40730MEADTAPC1 | OPEN Branch BELL BPA_115.0 (40087) TO MEAD TAP_115.0 (40730) CKT 1 |  | CHECK |
| L_40087BELLBPA-41015SPRNGHILC1 | OPEN Branch BELL BPA_115.0 (40087) TO SPRNGHIL_115.0 (41015) CKT 1 |  | CHECK |
| L_40087BELLBPA-41089TRENTWODC1 | OPEN Branch BELL BPA_115.0 (40087) TO TRENTWOD_115.0 (41089) CKT 1 |  | CHECK |
| L_40087BELLBPA-48029BEACONSC1 | OPEN Branch BEACON S_115.0 (48029) TO BELL BPA_115.0 (40087) CKT 1 |  | CHECK |
| L_40087BELLBPA-48033BELLTAPC1 | OPEN Branch BELL BPA_115.0 (40087) TO BELL TAP_115.0 (48033) CKT 1 |  | CHECK |
| L_40087BELLBPA-48449WAIKIKITC1 | OPEN Branch BELL BPA_115.0 (40087) TO WAIKIKIT_115.0 (48449) CKT 1 |  | CHECK |
| L_40088BELLS2-40090BELLS3C1 | OPEN Branch BELL S2_230.0 (40088) TO BELL S3_230.0 (40090) CKT 1 |  | CHECK |
| L_40088BELLS2-41358COULEES3C5_MS | OPEN MultiSectionLine BELL S2_230.0 (40088) TO COULEES3_230.0 (41358) CKT 5 |  | CHECK |
| L_40088BELLS2-47091USK | OPEN Branch BELL S2_230.0 (40088) TO USK_230.0 (47091) CKT 1 |  | CHECK |
| L_40090BELLS3-40092BELLS4C1 | OPEN Branch BELL S3_230.0 (40090) TO BELL S4_230.0 (40092) CKT 1 |  | CHECK |
| L_40090BELLS3-40624LANCASTRC1_MS | OPEN Gen LANCAS G_ 18.0 (47568) #1 |  | ALWAYS |
| L_40090BELLS3-40624LANCASTRC1_MS | OPEN Gen LANCAS S_ 13.8 (47569) #1 |  | ALWAYS |
| L_40090BELLS3-40624LANCASTRC1_MS | OPEN MultiSectionLine BELL S3_230.0 (40090) TO LANCASTR_230.0 (40624) CKT 1 |  | ALWAYS |
| L_40090BELLS3-40624LANCASTRC1_MS | OPEN Bus LIB PH2_230.0 (44201) |  | CHECK |
| L_40090BELLS3-41356COULEES1C3_MS | OPEN MultiSectionLine BELL S3_230.0 (40090) TO COULEES1_230.0 (41356) CKT 3 |  | CHECK |
| L_40090BELLS3-48025BEACONNC5 | OPEN Branch BEACON N_230.0 (48025) TO BELL S3_230.0 (40090) CKT 5 |  | CHECK |
| L_40091BELLBPA-40096BELLSCC1 | OPEN Branch BELL BPA_500.0 (40091) TO BELL SC_500.0 (40096) CKT 1 |  | CHECK |
| L_40091BELLBPA-40096BELLSCC1 | OPEN Load MILCTYDC_230.0 (63010) #D1 |  | CHECK |
| L_40091BELLBPA-40096BELLSCC1 | OPEN Shunt GARRISON_500.0 (40459) #r |  | CHECK |
| L_40091BELLBPA-40096BELLSCC1 | OPEN Bus LIB PH1_230.0 (44200) | West MT Hydro > 1000 | CHECK |
| L_40091BELLBPA-40096BELLSCC1 | OPEN Bus LIB PH2_230.0 (44201) | West MT Hydro > 1000 | CHECK |
| L_40091BELLBPA-40288COULER1C6 | OPEN Branch BELL BPA_500.0 (40091) TO COULE R1_500.0 (40288) CKT 6 |  | ALWAYS |
| L_40091BELLBPA-40288COULER1C6 | OPEN Load MILCTYDC_230.0 (63010) #D1 |  | ALWAYS |
| L_40091BELLBPA-40288COULER1C6 | OPEN Bus LIB PH2_230.0 (44201) | West MT Hydro > 1000 | CHECK |
| L_40091BELLBPA-40288COULER1C6 | OPEN Bus LIB PH1_230.0 (44200) | West MT Hydro > 1000 | CHECK |
| L_40091BELLBPA-40288COULER1C6 | OPEN Gen LANCAS G_ 18.0 (47568) #1 | WEST OF HATWAI > 3500 | CHECK |
| L_40091BELLBPA-40288COULER1C6 | OPEN Gen LANCAS S_ 13.8 (47569) #1 | WEST OF HATWAI > 3500 | CHECK |
| L_40092BELLS4-48031BEACONSC4 | OPEN Branch BEACON S_230.0 (48031) TO BELL S4_230.0 (40092) CKT 4 |  | CHECK |
| L_40096BELLSC-41057TAFTC1_MS | OPEN MultiSectionLine BELL SC_500.0 (40096) TO TAFT_500.0 (41057) CKT 1 |  | CHECK |
| L_40096BELLSC-41057TAFTC1_MS | OPEN Load MILCTYDC_230.0 (63010) #D1 |  | CHECK |
| L_40096BELLSC-41057TAFTC1_MS | OPEN Shunt GARRISON_500.0 (40459) #r |  | CHECK |
| L_40096BELLSC-41057TAFTC1_MS | OPEN Bus LIB PH1_230.0 (44200) | West MT Hydro > 1000 | CHECK |
| L_40096BELLSC-41057TAFTC1_MS | OPEN Bus LIB PH2_230.0 (44201) | West MT Hydro > 1000 | CHECK |
| L_40113BIGELOW-40483GREENBLC1 | OPEN Branch BIGELOW_115.0 (40113) TO GREEN BL_115.0 (40483) CKT 1 |  | CHECK |
| L_40113BIGELOW-41089TRENTWODC1 | OPEN Branch BIGELOW_115.0 (40113) TO TRENTWOD_115.0 (41089) CKT 1 |  | CHECK |
| L_40133BONNERS-40927SAMUELSC1_MS | OPEN MultiSectionLine BONNERS_115.0 (40133) TO SAMUELS_115.0 (40927) CKT 1 |  | CHECK |
| L_40133BONNERS-41239MOYIETC1 | OPEN Branch BONNERS_115.0 (40133) TO MOYIE T_115.0 (41239) CKT 1 |  | CHECK |
| L_40133BONNERS-47194MTHALLC1 | OPEN Branch BONNERS_115.0 (40133) TO MT HALL_115.0 (47194) CKT 1 |  | CHECK |
| L_40145BOUNDARY-40319CUSICKC1 | OPEN Branch BOUNDARY_230.0 (40145) TO CUSICK_230.0 (40319) CKT 1 |  | CHECK |
| L_40145BOUNDARY-40909SACHEENC1 | OPEN Branch BOUNDARY_230.0 (40145) TO SACHEEN_230.0 (40909) CKT 1 |  | CHECK |
| L_40145BOUNDARY-46476BOUNDPH1C1 | OPEN Branch BOUNDARY_230.0 (40145) TO BOUNDPH1_230.0 (46476) CKT 1 |  | CHECK |
| L_40145BOUNDARY-46478BOUNDPH2C1 | OPEN Branch BOUNDARY_230.0 (40145) TO BOUNDPH2_230.0 (46478) CKT 1 |  | CHECK |
| L_40145BOUNDARY-46480BOUNDPH3C1 | OPEN Branch BOUNDARY_230.0 (40145) TO BOUNDPH3_230.0 (46480) CKT 1 |  | CHECK |
| L_40145BOUNDARY-46482BOUNDPH4C1 | OPEN Branch BOUNDARY_230.0 (40145) TO BOUNDPH4_230.0 (46482) CKT 1 |  | CHECK |
| L_40145BOUNDARY-46484BOUNDPH5C1 | OPEN Branch BOUNDARY_230.0 (40145) TO BOUNDPH5_230.0 (46484) CKT 1 |  | CHECK |
| L_40145BOUNDARY-46486BOUNDPH6C1 | OPEN Branch BOUNDARY_230.0 (40145) TO BOUNDPH6_230.0 (46486) CKT 1 |  | CHECK |
| L_40149BRINKENS-48341POTLATAC1 | OPEN Branch BRINKENS_115.0 (40149) TO POTLAT A_115.0 (48341) CKT 1 |  | CHECK |
| L_40149BRINKENS-48445VIOLAC1 | OPEN Branch BRINKENS_115.0 (40149) TO VIOLA_115.0 (48445) CKT 1 |  | CHECK |
| L_40215CHENEY-40439FOURLKSC1 | OPEN Branch CHENEY_115.0 (40215) TO FOURLKS_115.0 (40439) CKT 1 |  | CHECK |
| L_40239CLARKSTN-40835POMEROYC1 | OPEN Branch CLARKSTN_115.0 (40239) TO POMEROY_115.0 (40835) CKT 1 |  | CHECK |
| L_40239CLARKSTN-48253NLEWISTC1 | OPEN Branch CLARKSTN_115.0 (40239) TO N LEWIST_115.0 (48253) CKT 1 |  | CHECK |
| L_40239CLARKSTN-48253NLEWISTC1 | SET INJECTION GROUP HOPKINS RIDGE TO 50 MW |  | CHECK |
| L_40245CLAYTON-40337DEERPRKC1 | OPEN Branch CLAYTON_115.0 (40245) TO DEER PRK_115.0 (40337) CKT 1 |  | CHECK |
| L_40245CLAYTON-48213LOONLKC1 | OPEN Branch CLAYTON_115.0 (40245) TO LOON LK_115.0 (48213) CKT 1 |  | CHECK |
| L_40255COLBERTT-40495HALFMOONC1 | OPEN Branch COLBERTT_115.0 (40255) TO HALFMOON_115.0 (40495) CKT 1 |  | CHECK |
| L_40255COLBERTT-40730MEADTAPC1 | OPEN Branch COLBERTT_115.0 (40255) TO MEAD TAP_115.0 (40730) CKT 1 |  | CHECK |
| L_40263COLVBPA-40607KETTLETC1 | OPEN Branch COLV BPA_115.0 (40263) TO KETTLE T_115.0 (40607) CKT 1 |  | CHECK |
| L_40263COLVBPA-48399SPIRITC1 | OPEN Branch COLV BPA_115.0 (40263) TO SPIRIT_115.0 (48399) CKT 1 |  | CHECK |
| L_40275COOKMT-40607KETTLETC1 | OPEN Branch COOK M T_115.0 (40275) TO KETTLE T_115.0 (40607) CKT 1 |  | CHECK |
| L_40275COOKMT-40879REPUBLICC1 | OPEN Branch COOK M T_115.0 (40275) TO REPUBLIC_115.0 (40879) CKT 1 |  | CHECK |
| L_40288COULER1-40287COULEEC6 | OPEN Branch COULE R1_500.0 (40288) TO COULEE_500.0 (40287) CKT 6 |  | ALWAYS |
| L_40288COULER1-40287COULEEC6 | OPEN Load MILCTYDC_230.0 (63010) #D1 |  | ALWAYS |
| L_40288COULER1-40287COULEEC6 | OPEN Bus LIB PH2_230.0 (44201) | West MT Hydro > 1000 | CHECK |
| L_40288COULER1-40287COULEEC6 | OPEN Bus LIB PH1_230.0 (44200) | West MT Hydro > 1000 | CHECK |
| L_40288COULER1-40287COULEEC6 | OPEN Gen LANCAS G_ 18.0 (47568) #1 | WEST OF HATWAI > 3500 | CHECK |
| L_40288COULER1-40287COULEEC6 | OPEN Gen LANCAS S_ 13.8 (47569) #1 | WEST OF HATWAI > 3500 | CHECK |
| L_40311CRESTN-40384EGYPTTPC1 | OPEN Branch CRESTN_115.0 (40311) TO EGYPT TP_115.0 (40384) CKT 1 |  | CHECK |
| L_40311CRESTN-41127WAGNERLTC1 | OPEN Branch CRESTN_115.0 (40311) TO WAGNERLT_115.0 (41127) CKT 1 |  | CHECK |
| L_40317CUSICK-47254USKC1 | OPEN Branch CUSICK_115.0 (40317) TO USK_115.0 (47254) CKT 1 |  | CHECK |
| L_40319CUSICK-47091USKC1_MS | OPEN MultiSectionLine CUSICK_230.0 (40319) TO USK_230.0 (47091) CKT 1 |  | CHECK |
| L_40337DEERPRK-48235MILANTPC1 | OPEN Branch DEER PRK_115.0 (40337) TO MILAN TP_115.0 (48235) CKT 1 |  | CHECK |
| L_40383EGRANVIL-48119EGRANTAPC1 | OPEN Branch EGRANTAP_115.0 (48119) TO EGRANVIL_115.0 (40383) CKT 1 |  | CHECK |
| L_40384EGYPTTP-40637LARENEC1 | OPEN Branch EGYPT TP_115.0 (40384) TO LARENE_115.0 (40637) CKT 1 |  | CHECK |
| L_40397FAIRCHLD-48009AIRWAYHTC1 | OPEN Branch AIRWAYHT_115.0 (48009) TO FAIRCHLD_115.0 (40397) CKT 1 |  | CHECK |
| L_40397FAIRCHLD-48388SILVRLK2C1 | OPEN Branch FAIRCHLD_115.0 (40397) TO SILVRLK2_115.0 (48388) CKT 1 |  | CHECK |
| L_40449GAFFNEY-48363REARDANC1 | OPEN Branch GAFFNEY_115.0 (40449) TO REARDAN_115.0 (48363) CKT 1 |  | CHECK |
| L_40449GAFFNEY-48411SPRAGUEC1 | OPEN Branch GAFFNEY_115.0 (40449) TO SPRAGUE_115.0 (48411) CKT 1 |  | CHECK |
| L_40495HALFMOON-41099TUMTUMC1 | OPEN Branch HALFMOON_115.0 (40495) TO TUM TUM_115.0 (41099) CKT 1 |  | CHECK |
| L_40519HATWAI-48197LOLOC1 | OPEN Branch HATWAI_230.0 (40519) TO LOLO_230.0 (48197) CKT 1 |  | CHECK |
| L_40519HATWAI-48249MOSCOWC1 | OPEN Branch HATWAI_230.0 (40519) TO MOSCOW_230.0 (48249) CKT 1 |  | CHECK |
| L_40519HATWAI-48255NLEWISTC1 | OPEN Branch HATWAI_230.0 (40519) TO N LEWIST_230.0 (48255) CKT 1 |  | CHECK |
| L_40525HAYFORD-48125FOURLBPAC1 | OPEN Branch FOURLBPA_115.0 (48125) TO HAYFORD_115.0 (40525) CKT 1 |  | CHECK |
| L_40551HOTSPR-41091TROUTCRC1 | OPEN Branch HOT SPR_230.0 (40551) TO TROUT CR_230.0 (41091) CKT 1 |  | CHECK |
| L_40551HOTSPR-48281NOXONC2 | OPEN Branch HOT SPR_230.0 (40551) TO NOXON_230.0 (48281) CKT 2 |  | CHECK |
| L_40577IRBY-48295ODESSAC1 | OPEN Branch IRBY_115.0 (40577) TO ODESSA_115.0 (48295) CKT 1 |  | CHECK |
| L_40577IRBY-48471WILSNCKTC1 | OPEN Branch IRBY_115.0 (40577) TO WILSNCKT_115.0 (48471) CKT 1 |  | CHECK |
| L_40607KETTLET-48175KETTLEAVC1 | OPEN Branch KETTLE T_115.0 (40607) TO KETTLEAV_115.0 (48175) CKT 1 |  | CHECK |
| L_40617LACLEDE-40857PRIESTC1 | OPEN Branch LACLEDE_115.0 (40617) TO PRIEST_115.0 (40857) CKT 1 |  | CHECK |
| L_40617LACLEDE-40933SANDPONTC1 | OPEN Branch LACLEDE_115.0 (40617) TO SANDPONT_115.0 (40933) CKT 1 |  | CHECK |
| L_40624LANCASTR-40787NOXONBPAC1_MS | OPEN MultiSectionLine LANCASTR_230.0 (40624) TO NOXONBPA_230.0 (40787) CKT 1 |  | CHECK |
| L_40624LANCASTR-40787NOXONBPAC1_MS | OPEN Bus LIB PH2_230.0 (44201) |  | CHECK |
| L_40637LARENE-41015SPRNGHILC1 | OPEN Branch LARENE_115.0 (40637) TO SPRNGHIL_115.0 (41015) CKT 1 |  | CHECK |
| L_40657LIBBY-40787NOXONBPAC1_MS | OPEN MultiSectionLine LIBBY_230.0 (40657) TO NOXONBPA_230.0 (40787) CKT 1 |  | CHECK |
| L_40657LIBBY-40787NOXONBPAC1_MS | OPEN Bus LIB PH2_230.0 (44201) |  | CHECK |
| L_40730MEADTAP-48222MEADSUBC1 | OPEN Branch MEAD SUB_115.0 (48222) TO MEAD TAP_115.0 (40730) CKT 1 |  | CHECK |
| L_40731METALINE-40732METLNTAPC1 | OPEN Branch METALINE_115.0 (40731) TO METLNTAP_115.0 (40732) CKT 1 |  | CHECK |
| L_40779NEWPORTB-47086PINESTC1 | OPEN Branch NEWPORTB_115.0 (40779) TO PINE ST_115.0 (47086) CKT 1 |  | CHECK |
| L_40787NOXONBPA-48289NOXONCONC1 | OPEN Branch NOXONBPA_230.0 (40787) TO NOXONCON_230.0 (48289) CKT 1 |  | CHECK |
| L_40855PRAIRIEB-48329POSTFLSC1 | OPEN Branch POST FLS_115.0 (48329) TO PRAIRIEB_115.0 (40855) CKT 1 |  | CHECK |
| L_40855PRAIRIEB-48349RAMSEYC1 | OPEN Branch PRAIRIEB_115.0 (40855) TO RAMSEY_115.0 (48349) CKT 1 |  | CHECK |
| L_40857PRIEST-48347PRIESTAC1 | OPEN Branch PRIEST_115.0 (40857) TO PRIEST A_115.0 (48347) CKT 1 |  | CHECK |
| L_40927SAMUELS-40965SELLEC1_MS | OPEN MultiSectionLine SAMUELS_115.0 (40927) TO SELLE_115.0 (40965) CKT 1 |  | CHECK |
| L_40929SANDCRK-40931SANDTPC1 | OPEN Branch SAND CRK_115.0 (40929) TO SAND TP_115.0 (40931) CKT 1 |  | CHECK |
| L_40929SANDCRK-40965SELLEC1_MS | OPEN MultiSectionLine SAND CRK_115.0 (40929) TO SELLE_115.0 (40965) CKT 1 |  | CHECK |
| L_40929SANDCRK-48377SANDPTAC1_MS | OPEN MultiSectionLine SAND CRK_115.0 (40929) TO SANDPT A_115.0 (48377) CKT 1 |  | CHECK |
| L_40931SANDTP-40933SANDPONTC1_MS | OPEN MultiSectionLine SAND TP_115.0 (40931) TO SANDPONT_115.0 (40933) CKT 1 |  | CHECK |
| L_40933SANDPONT-48376SAGLEC1 | OPEN Branch SANDPONT_115.0 (40933) TO SAGLE_115.0 (48376) CKT 1 |  | CHECK |
| L_40953SCARCELO-48356RATHDRMEC1 | OPEN Branch RATHDRME_115.0 (48356) TO SCARCELO_115.0 (40953) CKT 1 |  | CHECK |
| L_41089TRENTWOD-41117VERATAPC1 | OPEN Branch TRENTWOD_115.0 (41089) TO VERA TAP_115.0 (41117) CKT 1 |  | CHECK |
| L_41097TROY-41169YAAKC1 | OPEN Branch TROY_115.0 (41097) TO YAAK_115.0 (41169) CKT 1 |  | CHECK |
| L_41107VALYWAY-41117VERATAPC1 | OPEN Branch VALY WAY_115.0 (41107) TO VERA TAP_115.0 (41117) CKT 1 |  | CHECK |
| L_41125WAGNERLK-48469WILBURTC1 | OPEN Branch WAGNERLK_115.0 (41125) TO WILBURT_115.0 (48469) CKT 1 |  | CHECK |
| L_41127WAGNERLT-48469WILBURTC1 | OPEN Branch WAGNERLT_115.0 (41127) TO WILBURT_115.0 (48469) CKT 1 |  | CHECK |
| L_41190BOXTAP-40732METLNTAPC1 | OPEN Branch BOX TAP_115.0 (41190) TO METLNTAP_115.0 (40732) CKT 1 |  | CHECK |
| L_41190BOXTAP-48399SPIRITC1 | OPEN Branch BOX TAP_115.0 (41190) TO SPIRIT_115.0 (48399) CKT 1 |  | CHECK |
| L_41239MOYIET-41169YAAKC1 | OPEN Branch MOYIE T_115.0 (41239) TO YAAK_115.0 (41169) CKT 1 |  | CHECK |
| L_41239MOYIET-41240MOYIETXC1 | OPEN Branch MOYIE T_115.0 (41239) TO MOYIE TX_115.0 (41240) CKT 1 |  | CHECK |
| L_41240MOYIETX-41241NBENCHC1 | OPEN Branch MOYIE TX_115.0 (41240) TO N BENCH_115.0 (41241) CKT 1 |  | CHECK |
| L_41260SULLIVNB-41115VERAC1 | OPEN Branch SULLIVNB_115.0 (41260) TO VERA_115.0 (41115) CKT 1 |  | CHECK |
| L_41260SULLIVNB-41117VERATAPC1 | OPEN Branch SULLIVNB_115.0 (41260) TO VERA TAP_115.0 (41117) CKT 1 |  | CHECK |
| L_41357COULEES2-41276WESTBPA2C1 | OPEN Branch COULEES2_230.0 (41357) TO WESTBPA2_230.0 (41276) CKT 1 |  | CHECK |
| L_46021COULECTY-48149HEADWORKC1 | OPEN Branch COULECTY_115.0 (46021) TO HEADWORK_115.0 (48149) CKT 1 |  | CHECK |
| L_46021COULECTY-48419STRATFRDC1 | OPEN Branch COULECTY_115.0 (46021) TO STRATFRD_115.0 (48419) CKT 1 |  | CHECK |
| L_46039LARSON-48373ROUNDLKTC1 | OPEN Branch LARSON_115.0 (46039) TO ROUNDLKT_115.0 (48373) CKT 1 |  | CHECK |
| L_46077ROUNDLK-48373ROUNDLKTC1 | OPEN Branch ROUND LK_115.0 (46077) TO ROUNDLKT_115.0 (48373) CKT 1 |  | CHECK |
| L_46087SANDUNES-48455WARDENAC1 | OPEN Branch SANDUNES_115.0 (46087) TO WARDEN A_115.0 (48455) CKT 1 |  | CHECK |
| L_46150COUL2GPD-41127WAGNERLTC1 | OPEN Branch COUL2GPD_115.0 (46150) TO WAGNERLT_115.0 (41127) CKT 1 |  | CHECK |
| L_46151Larson-46156Rockyfd 230 | OPEN Branch LARSON_230.0 (46151) TO ROCKYFD_230.0 (46156) CKT 1 |  | CHECK |
| L_46805CHELAN-48149HEADWORKC1 | OPEN Branch CHELAN_115.0 (46805) TO HEADWORK_115.0 (48149) CKT 1 |  | CHECK |
| L_47009BOXCANY-40317CUSICKC1 | OPEN Branch BOX CANY_115.0 (47009) TO CUSICK_115.0 (40317) CKT 1 |  | CHECK |
| L_47025DELIGHT-48187LINDC1 | OPEN Branch DELIGHT_115.0 (47025) TO LIND_115.0 (48187) CKT 1 |  | CHECK |
| L_47025DELIGHT-48457WASHTUNAC1 | OPEN Branch DELIGHT_115.0 (47025) TO WASHTUNA_115.0 (48457) CKT 1 |  | CHECK |
| L_47027DIAMLAK-40907SACHEENC1 | OPEN Branch DIAM LAK_115.0 (47027) TO SACHEEN_115.0 (40907) CKT 1 |  | CHECK |
| L_47033DOWERRD-48111DOWERRDTC1 | OPEN Branch DOWER RD_115.0 (47033) TO DOWERRDT_115.0 (48111) CKT 1 |  | CHECK |
| L_47038EGYPT-40384EGYPTTPC1 | OPEN Branch EGYPT_115.0 (47038) TO EGYPT TP_115.0 (40384) CKT 1 |  | CHECK |
| L_47086PINEST-47254USKC1 | OPEN Branch PINE ST_115.0 (47086) TO USK_115.0 (47254) CKT 1 |  | CHECK |
| L_47086PINEST-48258NEWPORTTC1 | OPEN Branch NEWPORTT_115.0 (48258) TO PINE ST_115.0 (47086) CKT 1 |  | CHECK |
| L_47126BOXPS-41190BOXTAPC1 | OPEN Branch BOX PS_115.0 (47126) TO BOX TAP_115.0 (41190) CKT 1 |  | CHECK |
| L_47194MTHALL-41299SMITHFLSC1 | OPEN Branch MT HALL_115.0 (47194) TO SMITHFLS_115.0 (41299) CKT 1 |  | CHECK |
| L_47278LIBBYFEC-41097TROYC1 | OPEN Branch LIBBYFEC_115.0 (47278) TO TROY_115.0 (41097) CKT 1 |  | CHECK |
| L_47501ARMSTRNG-48383SHAWNEEC1 | OPEN Branch ARMSTRNG_115.0 (47501) TO SHAWNEE_115.0 (48383) CKT 1 |  | CHECK |
| L_47501ARMSTRNG-48413SPULLMANC1 | OPEN Branch ARMSTRNG_115.0 (47501) TO SPULLMAN_115.0 (48413) CKT 1 |  | CHECK |
| L_47503CHAMBERS-48073CHMBRSTPC1 | OPEN Branch CHAMBERS_115.0 (47503) TO CHMBRSTP_115.0 (48073) CKT 1 |  | CHECK |
| L_47505HOODOO-48043BLANCHRDC1 | OPEN Branch BLANCHRD_115.0 (48043) TO HOODOO_115.0 (47505) CKT 1 |  | CHECK |
| L_47505HOODOO-48403SPIRITLTC1 | OPEN Branch HOODOO_115.0 (47505) TO SPIRITLT_115.0 (48403) CKT 1 |  | CHECK |
| L_47507HOPKINSB-48231MICATAPC1 | OPEN Branch HOPKINSB_115.0 (47507) TO MICA TAP_115.0 (48231) CKT 1 |  | CHECK |
| L_47507HOPKINSB-48271NINTHCNTC1 | OPEN Branch HOPKINSB_115.0 (47507) TO NINTHCNT_115.0 (48271) CKT 1 |  | CHECK |
| L_47509MICA-48231MICATAPC1 | OPEN Branch MICA_115.0 (47509) TO MICA TAP_115.0 (48231) CKT 1 |  | CHECK |
| L_47511MOAB-48319PLEASANTC1 | OPEN Branch MOAB_115.0 (47511) TO PLEASANT_115.0 (48319) CKT 1 |  | CHECK |
| L_47511MOAB-48522BOULDEREC1 | OPEN Branch BOULDERE_115.0 (48522) TO MOAB_115.0 (47511) CKT 1 |  | CHECK |
| L_480014LAKETP-40439FOURLKSC1 | OPEN Branch 4LAKE TP_115.0 (48001) TO FOURLKS_115.0 (40439) CKT 1 |  | CHECK |
| L_480014LAKETP-48145HANGMANC1 | OPEN Branch 4LAKE TP_115.0 (48001) TO HANGMAN_115.0 (48145) CKT 1 |  | CHECK |
| L_480014LAKETP-48397SPANGLEC1 | OPEN Branch 4LAKE TP_115.0 (48001) TO SPANGLE_115.0 (48397) CKT 1 |  | CHECK |
| L_48003NELSONSB-48005NELSONTPC1 | OPEN Branch NELSONSB_115.0 (48003) TO NELSONT_115.0 (48005) CKT 1 |  | CHECK |
| L_48005NELSONTP-48069CHESTERC1 | OPEN Branch NELSONT_115.0 (48005) TO CHESTER_115.0 (48069) CKT 1 |  | CHECK |
| L_48005NELSONTP-48271NINTHCNTC1 | OPEN Branch NELSONT_115.0 (48005) TO NINTHCNT_115.0 (48271) CKT 1 |  | CHECK |
| L_48009AIRWAYHT-47513W.PLAINSC1 | OPEN Branch AIRWAYHT_115.0 (48009) TO W.PLAINS_115.0 (47513) CKT 1 |  | CHECK |
| L_48009AIRWAYHT-48421SUNSETC1 | OPEN Branch AIRWAYHT_115.0 (48009) TO SUNSET_115.0 (48421) CKT 1 |  | CHECK |
| L_48011APPLETAP-48013APPLEWAYC1 | OPEN Branch APPLETAP_115.0 (48011) TO APPLEWAY_115.0 (48013) CKT 1 |  | CHECK |
| L_48011APPLETAP-48095DALTON2TC1 | OPEN Branch APPLETAP_115.0 (48011) TO DALTON2T_115.0 (48095) CKT 1 |  | CHECK |
| L_48011APPLETAP-48349RAMSEYC1 | OPEN Branch APPLETAP_115.0 (48011) TO RAMSEY_115.0 (48349) CKT 1 |  | CHECK |
| L_48015ARDEN-48223METCHIPC1 | OPEN Branch ARDEN_115.0 (48015) TO METCHIP_115.0 (48223) CKT 1 |  | CHECK |
| L_48015ARDEN-48301ORINC1 | OPEN Branch ARDEN_115.0 (48015) TO ORIN_115.0 (48301) CKT 1 |  | CHECK |
| L_48017ATHOLTAP-40953SCARCELOC1 | OPEN Branch ATHOLTAP_115.0 (48017) TO SCARCELO_115.0 (40953) CKT 1 |  | CHECK |
| L_48017ATHOLTAP-48403SPIRITLTC1 | OPEN Branch ATHOLTAP_115.0 (48017) TO SPIRITLT_115.0 (48403) CKT 1 |  | CHECK |
| L_48019AVONDALE-48095DALTON2TC1 | OPEN Branch AVONDALE_115.0 (48019) TO DALTON2T_115.0 (48095) CKT 1 |  | CHECK |
| L_48019AVONDALE-48356RATHDRMEC1 | OPEN Branch AVONDALE_115.0 (48019) TO RATHDRME_115.0 (48356) CKT 1 |  | CHECK |
| L_48021BARKER-48311OTISC1 | OPEN Branch BARKER_115.0 (48021) TO OTIS_115.0 (48311) CKT 1 |  | CHECK |
| L_48023BEACONN-48029BEACONSC1 | OPEN Branch BEACON N_115.0 (48023) TO BEACON S_115.0 (48029) CKT 1 |  | CHECK |
| L_48023BEACONN-48271NINTHCNTC1 | OPEN Branch BEACON N_115.0 (48023) TO NINTHCNT_115.0 (48271) CKT 1 |  | CHECK |
| L_48023BEACONN-48277NORTHEASC1 | OPEN Branch BEACON N_115.0 (48023) TO NORTHEAS_115.0 (48277) CKT 1 |  | CHECK |
| L_48023BEACONN-48371ROSSPARKC1 | OPEN Branch BEACON N_115.0 (48023) TO ROSSPARK_115.0 (48371) CKT 1 |  | CHECK |
| L_48023BEACONN-48405SPKINDPKC1 | OPEN Branch BEACON N_115.0 (48023) TO SPKINDPK_115.0 (48405) CKT 1 |  | CHECK |
| L_48025BEACONN-48031BEACONSC1 | OPEN Branch BEACON N_230.0 (48025) TO BEACON S_230.0 (48031) CKT 1 |  | CHECK |
| L_48025BEACONN-48357RATHDRUMC2 | OPEN Branch BEACON N_230.0 (48025) TO RATHDRUM_230.0 (48357) CKT 2 |  | CHECK |
| L_48027BEACONS-48437UPRIVERC1 | OPEN Branch BEACON S_ 13.8 (48027) TO UPRIVER_ 13.8 (48437) CKT 1 |  | CHECK |
| L_48029BEACONS-48033BELLTAPC1 | OPEN Branch BEACON S_115.0 (48029) TO BELL TAP_115.0 (48033) CKT 1 |  | CHECK |
| L_48029BEACONS-48194LOCUSTC1 | OPEN Branch BEACON S_115.0 (48029) TO LOCUST_115.0 (48194) CKT 1 |  | CHECK |
| L_48029BEACONS-48271NINTHCNTC2 | OPEN Branch BEACON S_115.0 (48029) TO NINTHCNT_115.0 (48271) CKT 2 |  | CHECK |
| L_48031BEACONS-48524BOULDERC1 | OPEN Branch BEACON S_230.0 (48031) TO BOULDER_230.0 (48524) CKT 1 |  | CHECK |
| L_48033BELLTAP-48381SEVENTAPC1 | OPEN Branch BELL TAP_115.0 (48033) TO SEVENTAP_115.0 (48381) CKT 1 |  | CHECK |
| L_48035BENEWAH-48181LATAHC1 | OPEN Branch BENEWAH_115.0 (48035) TO LATAH_115.0 (48181) CKT 1 |  | CHECK |
| L_48035BENEWAH-48323PLUMMERC1 | OPEN Branch BENEWAH_115.0 (48035) TO PLUMMER_115.0 (48323) CKT 1 |  | CHECK |
| L_48037BENEWAH-48249MOSCOWC1 | OPEN Branch BENEWAH_230.0 (48037) TO MOSCOW_230.0 (48249) CKT 1 |  | CHECK |
| L_48037BENEWAH-48317PINECRKC1 | OPEN Branch BENEWAH_230.0 (48037) TO PINE CRK_230.0 (48317) CKT 1 |  | CHECK |
| L_48037BENEWAH-48317PINECRKC1 | OPEN Gen NOXON34_ 14.4 (48287) #3 |  | CHECK |
| L_48037BENEWAH-48317PINECRKC1 | OPEN Gen NOXON34_ 14.4 (48287) #4 |  | CHECK |
| L_48037BENEWAH-48385SHAWNEEC1 | OPEN Branch BENEWAH_230.0 (48037) TO SHAWNEE_230.0 (48385) CKT 1 |  | CHECK |
| L_48037BENEWAH-48524BOULDERC1 | OPEN Branch BOULDER_230.0 (48524) TO BENEWAH_230.0 (48037) CKT 1 |  | CHECK |
| L_48039BENTNAVA-40097BENTONC1 | OPEN Branch BENTNAVA_115.0 (48039) TO BENTON_115.0 (40097) CKT 1 |  | CHECK |
| L_48039BENTNAVA-48425TAUNTONC1 | OPEN Branch BENTNAVA_115.0 (48039) TO TAUNTON_115.0 (48425) CKT 1 |  | CHECK |
| L_48041BIGCREEK-48049BUNKRHILC1 | OPEN Branch BIGCREEK_115.0 (48041) TO BUNKRHIL_115.0 (48049) CKT 1 |  | CHECK |
| L_48041BIGCREEK-48153HECLATC1 | OPEN Branch BIGCREEK_115.0 (48041) TO HECLAT_115.0 (48153) CKT 1 |  | CHECK |
| L_48043BLANCHRD-48258NEWPORTTC1 | OPEN Branch BLANCHRD_115.0 (48043) TO NEWPORTT_115.0 (48258) CKT 1 |  | CHECK |
| L_48045BLUECRK-48067CDAC1 | OPEN Branch BLUECRK_115.0 (48045) TO CDA_115.0 (48067) CKT 1 |  | CHECK |
| L_48045BLUECRK-48239MISSIONC1 | OPEN Branch BLUECRK_115.0 (48045) TO MISSION_115.0 (48239) CKT 1 |  | CHECK |
| L_48047BRONX-48293ODENC1 | OPEN Branch BRONX_115.0 (48047) TO ODEN_115.0 (48293) CKT 1 |  | CHECK |
| L_48047BRONX-48377SANDPTAC1 | OPEN Branch BRONX_115.0 (48047) TO SANDPT A_115.0 (48377) CKT 1 |  | CHECK |
| L_48049BUNKRHIL-48315PINECRKC1 | OPEN Branch BUNKRHIL_115.0 (48049) TO PINE CRK_115.0 (48315) CKT 1 |  | CHECK |
| L_48051BURKE-48053BURKAVAAC1 | Unlinked Action: BRANCH 48053 48051 1 OPEN |  | CHECK |
| L_48051BURKE-48055BURKAVABC1 | Unlinked Action: BRANCH 48055 48051 1 OPEN |  | CHECK |
| L_48051BURKE-48151HECLAC1 | OPEN Branch BURKE_115.0 (48051) TO HECLA_115.0 (48151) CKT 1 |  | CHECK |
| L_48051BURKE-48217LUCKYFTPC1 | OPEN Branch BURKE_115.0 (48051) TO LUCKYFTP_115.0 (48217) CKT 1 |  | CHECK |
| L_48057CABGORG-48065CABINETGC1 | OPEN Branch CAB GORG_115.0 (48057) TO CABINETG_115.0 (48065) CKT 1 |  | CHECK |
| L_48059CABGORG-48179LAKEVIEWC1 | OPEN Branch CAB GORG_230.0 (48059) TO LAKEVIEW_230.0 (48179) CKT 1 |  | CHECK |
| L_48059CABGORG-48179LAKEVIEWC1 | OPEN Gen NOXON12_ 14.4 (48285) #1 |  | CHECK |
| L_48059CABGORG-48179LAKEVIEWC1 | OPEN Gen NOXON12_ 14.4 (48285) #2 |  | CHECK |
| L_48059CABGORG-48179LAKEVIEWC1 | OPEN Gen NOXON34_ 14.4 (48287) #3 |  | CHECK |
| L_48059CABGORG-48179LAKEVIEWC1 | OPEN Gen NOXON34_ 14.4 (48287) #4 |  | CHECK |
| L_48059CABGORG-48281NOXONC1 | OPEN Branch CAB GORG_230.0 (48059) TO NOXON_230.0 (48281) CKT 1 |  | ALWAYS |
| L_48059CABGORG-48281NOXONC1 | OPEN Gen NOXON34_ 14.4 (48287) #3 | WMH > 1450 | CHECK |
| L_48059CABGORG-48281NOXONC1 | OPEN Gen NOXON34_ 14.4 (48287) #4 | WMH > 1450 | CHECK |
| L_48065CABINETG-48077CLRKFORKC1 | OPEN Branch CABINETG_115.0 (48065) TO CLRKFORK_115.0 (48077) CKT 1 |  | CHECK |
| L_48067CDA-48097DALTONTC1 | OPEN Branch CDA_115.0 (48067) TO DALTONT_115.0 (48097) CKT 1 |  | CHECK |
| L_48067CDA-48349RAMSEYC1 | OPEN Branch CDA_115.0 (48067) TO RAMSEY_115.0 (48349) CKT 1 |  | CHECK |
| L_48069CHESTER-48299OPPORTUNC1 | OPEN Branch CHESTER_115.0 (48069) TO OPPORTUN_115.0 (48299) CKT 1 |  | CHECK |
| L_48071CHEWELAH-48441VALLEYAC1 | OPEN Branch CHEWELAH_115.0 (48071) TO VALLEY A_115.0 (48441) CKT 1 |  | CHECK |
| L_48073CHMBRSTP-48115EASCOLFXC1 | OPEN Branch CHMBRSTP_115.0 (48073) TO EASCOLFX_115.0 (48115) CKT 1 |  | CHECK |
| L_48073CHMBRSTP-48383SHAWNEEC1 | OPEN Branch CHMBRSTP_115.0 (48073) TO SHAWNEE_115.0 (48383) CKT 1 |  | CHECK |
| L_48075CLEARWTR-48195LOLOC1 | OPEN Branch CLEARWTR_115.0 (48075) TO LOLO_115.0 (48195) CKT 1 |  | CHECK |
| L_48075CLEARWTR-48253NLEWISTC1 | OPEN Branch CLEARWTR_115.0 (48075) TO N LEWIST_115.0 (48253) CKT 1 |  | CHECK |
| L_48075CLEARWTR-48429TENTHSTWC1 | OPEN Branch CLEARWTR_115.0 (48075) TO TENTHSTW_115.0 (48429) CKT 1 |  | CHECK |
| L_48077CLRKFORK-48293ODENC1 | OPEN Branch CLRKFORK_115.0 (48077) TO ODEN_115.0 (48293) CKT 1 |  | CHECK |
| L_48079COLBERT-40255COLBERTTC1 | OPEN Branch COLBERT_115.0 (48079) TO COLBERTT_115.0 (40255) CKT 1 |  | CHECK |
| L_48081COLLWALN-48129FTWRIGHTC1 | OPEN Branch COLLWALN_115.0 (48081) TO FTWRIGHT_115.0 (48129) CKT 1 |  | CHECK |
| L_48081COLLWALN-48339POSTSTRTC1 | OPEN Branch COLLWALN_115.0 (48081) TO POSTSTRT_115.0 (48339) CKT 1 |  | CHECK |
| L_48083COLVAVA-48143GREENWDAC1 | OPEN Branch COLV AVA_115.0 (48083) TO GREENWDA_115.0 (48143) CKT 1 |  | CHECK |
| L_48083COLVAVA-48301ORINC1 | OPEN Branch COLV AVA_115.0 (48083) TO ORIN_115.0 (48301) CKT 1 |  | CHECK |
| L_48087COTTNWDT-48089COTTNWODC1 | OPEN Branch COTTNWDT_115.0 (48087) TO COTTNWOD_115.0 (48089) CKT 1 |  | CHECK |
| L_48087COTTNWDT-48261NEZPERCEC1 | OPEN Branch COTTNWDT_115.0 (48087) TO NEZPERCE_115.0 (48261) CKT 1 |  | CHECK |
| L_48087COTTNWDT-48465WICKESC1 | OPEN Branch COTTNWDT_115.0 (48087) TO WICKES_115.0 (48465) CKT 1 |  | CHECK |
| L_48091CRAIGMNT-48261NEZPERCEC1 | OPEN Branch CRAIGMNT_115.0 (48091) TO NEZPERCE_115.0 (48261) CKT 1 |  | CHECK |
| L_48091CRAIGMNT-48423SWEETWTRC1 | OPEN Branch CRAIGMNT_115.0 (48091) TO SWEETWTR_115.0 (48423) CKT 1 |  | CHECK |
| L_48093DALTONA-48097DALTONTC1 | OPEN Branch DALTON A_115.0 (48093) TO DALTONT_115.0 (48097) CKT 1 |  | CHECK |
| L_48097DALTONT-48148HAYDENC1 | OPEN Branch DALTONT_115.0 (48097) TO HAYDEN_115.0 (48148) CKT 1 |  | CHECK |
| L_48099DAVENPRT-48105DEVILGP2C1 | OPEN Branch DAVENPRT_115.0 (48099) TO DEVILGP2_115.0 (48105) CKT 1 |  | CHECK |
| L_48099DAVENPRT-48147HARRNGTNC1 | OPEN Branch DAVENPRT_115.0 (48099) TO HARRNGTN_115.0 (48147) CKT 1 |  | CHECK |
| L_48101DEARY-48169JULIAETTC1 | OPEN Branch DEARY_115.0 (48101) TO JULIAETT_115.0 (48169) CKT 1 |  | CHECK |
| L_48103DEVILGP-47513W.PLAINSC1 | OPEN Branch DEVIL GP_115.0 (48103) TO W.PLAINS_115.0 (47513) CKT 1 |  | CHECK |
| L_48103DEVILGP-48105DEVILGP2C1 | OPEN Branch DEVIL GP_115.0 (48103) TO DEVILGP2_115.0 (48105) CKT 1 |  | CHECK |
| L_48103DEVILGP-48199LONGLAKAC1 | OPEN Branch DEVIL GP_115.0 (48103) TO LONGLAKA_115.0 (48199) CKT 1 |  | CHECK |
| L_48103DEVILGP-48201LONGLAKBC1 | OPEN Branch DEVIL GP_115.0 (48103) TO LONGLAKB_115.0 (48201) CKT 1 |  | CHECK |
| L_48103DEVILGP-48203LONGLAKTC1 | OPEN Branch DEVIL GP_115.0 (48103) TO LONGLAKT_115.0 (48203) CKT 1 |  | CHECK |
| L_48103DEVILGP-48269NINEMILEC1 | OPEN Branch DEVIL GP_115.0 (48103) TO NINEMILE_115.0 (48269) CKT 1 |  | CHECK |
| L_48105DEVILGP2-48193LITTFALLC1 | OPEN Branch DEVILGP2_115.0 (48105) TO LITTFALL_115.0 (48193) CKT 1 |  | CHECK |
| L_48105DEVILGP2-48193LITTFALLC2 | OPEN Branch DEVILGP2_115.0 (48105) TO LITTFALL_115.0 (48193) CKT 2 |  | CHECK |
| L_48105DEVILGP2-48363REARDANC1 | OPEN Branch DEVILGP2_115.0 (48105) TO REARDAN_115.0 (48363) CKT 1 |  | CHECK |
| L_48109DIAMOND-48121EWANC1 | OPEN Branch DIAMOND_115.0 (48109) TO EWAN_115.0 (48121) CKT 1 |  | CHECK |
| L_48109DIAMOND-48383SHAWNEEC1 | OPEN Branch DIAMOND_115.0 (48109) TO SHAWNEE_115.0 (48383) CKT 1 |  | CHECK |
| L_48111DOWERRDT-48329POSTFLSC1 | OPEN Branch DOWERRDT_115.0 (48111) TO POST FLS_115.0 (48329) CKT 1 |  | CHECK |
| L_48113DRYGULCH-48253NLEWISTC1 | OPEN Branch DRYGULCH_115.0 (48113) TO N LEWIST_115.0 (48253) CKT 1 |  | CHECK |
| L_48115EASCOLFX-48369ROSALIAC1 | OPEN Branch EASCOLFX_115.0 (48115) TO ROSALIA_115.0 (48369) CKT 1 |  | CHECK |
| L_48117EASTFARM-48311OTISC1 | OPEN Branch EASTFARM_115.0 (48117) TO OTIS_115.0 (48311) CKT 1 |  | CHECK |
| L_48117EASTFARM-48329POSTFLSC1 | OPEN Branch EASTFARM_115.0 (48117) TO POST FLS_115.0 (48329) CKT 1 |  | CHECK |
| L_48119EGRANTAP-48141GRANGVILC1 | OPEN Branch EGRANTAP_115.0 (48119) TO GRANGVIL_115.0 (48141) CKT 1 |  | CHECK |
| L_48119EGRANTAP-48177KOOSKIAC1 | OPEN Branch EGRANTAP_115.0 (48119) TO KOOSKIA_115.0 (48177) CKT 1 |  | CHECK |
| L_48121EWAN-48221MARENGOC1 | OPEN Branch EWAN_115.0 (48121) TO MARENGO_115.0 (48221) CKT 1 |  | CHECK |
| L_48122FAIRS-48387SILVRLAKC1 | OPEN Branch FAIR S_115.0 (48122) TO SILVRLAK_115.0 (48387) CKT 1 |  | CHECK |
| L_48123FORD-48203LONGLAKTC1 | OPEN Branch FORD_115.0 (48123) TO LONGLAKT_115.0 (48203) CKT 1 |  | CHECK |
| L_48123FORD-48441VALLEYAC1 | OPEN Branch FORD_115.0 (48123) TO VALLEY A_115.0 (48441) CKT 1 |  | CHECK |
| L_48125FOURLBPA-40439FOURLKSC1 | OPEN Branch FOURLBPA_115.0 (48125) TO FOURLKS_115.0 (40439) CKT 1 |  | CHECK |
| L_48125FOURLBPA-40525HAYFORDC1 | OPEN Branch FOURLBPA_115.0 (48125) TO HAYFORD_115.0 (40525) CKT 1 |  | CHECK |
| L_48125FOURLBPA-48132HAL&WHITC1 | OPEN Branch FOURLBPA_115.0 (48125) TO HAL&WHIT_115.0 (48132) CKT 1 |  | CHECK |
| L_48127FRANCEDR-48219LYONSTNDC1 | OPEN Branch FRANCEDR_115.0 (48127) TO LYONSTND_115.0 (48219) CKT 1 |  | CHECK |
| L_48127FRANCEDR-48279NORTHWESC1 | OPEN Branch FRANCEDR_115.0 (48127) TO NORTHWES_115.0 (48279) CKT 1 |  | CHECK |
| L_48127FRANCEDR-48381SEVENTAPC1 | OPEN Branch FRANCEDR_115.0 (48127) TO SEVENTAP_115.0 (48381) CKT 1 |  | CHECK |
| L_48129FTWRIGHT-48461WESTC1 | OPEN Branch FTWRIGHT_115.0 (48129) TO WEST_115.0 (48461) CKT 1 |  | CHECK |
| L_48131GARDENSP-40525HAYFORDC1 | OPEN Branch GARDENSP_115.0 (48131) TO HAYFORD_115.0 (40525) CKT 1 |  | CHECK |
| L_48131GARDENSP-48409SPKWASTEC1 | OPEN Branch GARDENSP_115.0 (48131) TO SPKWASTE_115.0 (48409) CKT 1 |  | CHECK |
| L_48131GARDENSP-48421SUNSETC1 | OPEN Branch GARDENSP_115.0 (48131) TO SUNSET_115.0 (48421) CKT 1 |  | CHECK |
| L_48132HAL&WHIT-48387SILVRLAKC1 | OPEN Branch HAL&WHIT_115.0 (48132) TO SILVRLAK_115.0 (48387) CKT 1 |  | CHECK |
| L_48133GARFIELD-48313PALOUSEC1 | OPEN Branch GARFIELD_115.0 (48133) TO PALOUSE_115.0 (48313) CKT 1 |  | CHECK |
| L_48133GARFIELD-48427TEKOAC1 | OPEN Branch GARFIELD_115.0 (48133) TO TEKOA_115.0 (48427) CKT 1 |  | CHECK |
| L_48137GLENROSE-48139GLENTAPC1 | OPEN Branch GLENROSE_115.0 (48137) TO GLENTAP_115.0 (48139) CKT 1 |  | CHECK |
| L_48139GLENTAP-48271NINTHCNTC1 | OPEN Branch GLENTAP_115.0 (48139) TO NINTHCNT_115.0 (48271) CKT 1 |  | CHECK |
| L_48139GLENTAP-48395SOUTHEASC1 | OPEN Branch GLENTAP_115.0 (48139) TO SOUTHEAS_115.0 (48395) CKT 1 |  | CHECK |
| L_48141GRANGVIL-48465WICKESC1 | OPEN Branch GRANGVIL_115.0 (48141) TO WICKES_115.0 (48465) CKT 1 |  | CHECK |
| L_48143GREENWDA-48175KETTLEAVC1 | OPEN Branch GREENWDA_115.0 (48143) TO KETTLEAV_115.0 (48175) CKT 1 |  | CHECK |
| L_48145HANGMAN-48421SUNSETC1 | OPEN Branch HANGMAN_115.0 (48145) TO SUNSET_115.0 (48421) CKT 1 |  | CHECK |
| L_48147HARRNGTN-48295ODESSAC1 | OPEN Branch HARRNGTN_115.0 (48147) TO ODESSA_115.0 (48295) CKT 1 |  | CHECK |
| L_48148HAYDEN-48356RATHDRMEC1 | OPEN Branch HAYDEN_115.0 (48148) TO RATHDRME_115.0 (48356) CKT 1 |  | CHECK |
| L_48151HECLA-48453WALLACEC1 | OPEN Branch HECLA_115.0 (48151) TO WALLACE_115.0 (48453) CKT 1 |  | CHECK |
| L_48153HECLAT-48217LUCKYFTPC1 | OPEN Branch HECLAT_115.0 (48153) TO LUCKYFTP_115.0 (48217) CKT 1 |  | CHECK |
| L_48155HERN-48159HUETTERC1 | OPEN Branch HERN_115.0 (48155) TO HUETTER_115.0 (48159) CKT 1 |  | CHECK |
| L_48155HERN-48349RAMSEYC1 | OPEN Branch HERN_115.0 (48155) TO RAMSEY_115.0 (48349) CKT 1 |  | CHECK |
| L_48157HOLBROOK-48253NLEWISTC1 | OPEN Branch HOLBROOK_115.0 (48157) TO N LEWIST_115.0 (48253) CKT 1 |  | CHECK |
| L_48157HOLBROOK-48389SLEWISTC1 | OPEN Branch HOLBROOK_115.0 (48157) TO SLEWIST_115.0 (48389) CKT 1 |  | CHECK |
| L_48159HUETTER-48355RATHDRUMC1 | OPEN Branch HUETTER_115.0 (48159) TO RATHDRUM_115.0 (48355) CKT 1 |  | CHECK |
| L_48163I.E.PAPR-48237MILLWOODC1 | OPEN Branch I.E.PAPR_115.0 (48163) TO MILLWOOD_115.0 (48237) CKT 1 |  | CHECK |
| L_48165IRVIN-48237MILLWOODC1 | OPEN Branch IRVIN_115.0 (48165) TO MILLWOOD_115.0 (48237) CKT 1 |  | CHECK |
| L_48165IRVIN-48299OPPORTUNC1 | OPEN Branch IRVIN_115.0 (48165) TO OPPORTUN_115.0 (48299) CKT 1 |  | CHECK |
| L_48167JAYPE-48459WEIPPEC1 | OPEN Branch JAYPE_115.0 (48167) TO WEIPPE_115.0 (48459) CKT 1 |  | CHECK |
| L_48169JULIAETT-48247MOSCOWC1 | OPEN Branch JULIAETT_115.0 (48169) TO MOSCOW_115.0 (48247) CKT 1 |  | CHECK |
| L_48169JULIAETT-48303OROFINOC1 | OPEN Branch JULIAETT_115.0 (48169) TO OROFINO_115.0 (48303) CKT 1 |  | CHECK |
| L_48171KAMIAH-48261NEZPERCEC1 | OPEN Branch KAMIAH_115.0 (48171) TO NEZPERCE_115.0 (48261) CKT 1 |  | CHECK |
| L_48171KAMIAH-48379SCOTPAPRC1 | OPEN Branch KAMIAH_115.0 (48171) TO SCOTPAPR_115.0 (48379) CKT 1 |  | CHECK |
| L_48177KOOSKIA-48379SCOTPAPRC1 | OPEN Branch KOOSKIA_115.0 (48177) TO SCOTPAPR_115.0 (48379) CKT 1 |  | CHECK |
| L_48179LAKEVIEW-48357RATHDRUMC1 | OPEN Branch LAKEVIEW_230.0 (48179) TO RATHDRUM_230.0 (48357) CKT 1 |  | CHECK |
| L_48179LAKEVIEW-48357RATHDRUMC1 | OPEN Gen NOXON12_ 14.4 (48285) #1 |  | CHECK |
| L_48179LAKEVIEW-48357RATHDRUMC1 | OPEN Gen NOXON12_ 14.4 (48285) #2 |  | CHECK |
| L_48179LAKEVIEW-48357RATHDRUMC1 | OPEN Gen NOXON34_ 14.4 (48287) #3 |  | CHECK |
| L_48179LAKEVIEW-48357RATHDRUMC1 | OPEN Gen NOXON34_ 14.4 (48287) #4 |  | CHECK |
| L_48181LATAH-48367ROCKFORDC1 | OPEN Branch LATAH_115.0 (48181) TO ROCKFORD_115.0 (48367) CKT 1 |  | CHECK |
| L_48181LATAH-48427TEKOAC1 | OPEN Branch LATAH_115.0 (48181) TO TEKOA_115.0 (48427) CKT 1 |  | CHECK |
| L_48183LEON-48243MOSCCITYC1 | OPEN Branch LEON_115.0 (48183) TO MOSCCITY_115.0 (48243) CKT 1 |  | CHECK |
| L_48183LEON-48253NLEWISTC1 | OPEN Branch LEON_115.0 (48183) TO N LEWIST_115.0 (48253) CKT 1 |  | CHECK |
| L_48185LIBTYLK-48299OPPORTUNC1 | OPEN Branch LIBTYLK_115.0 (48185) TO OPPORTUN_115.0 (48299) CKT 1 |  | CHECK |
| L_48187LIND-47073RALSTONBC1 | OPEN Branch LIND_115.0 (48187) TO RALSTONB_115.0 (47073) CKT 1 |  | CHECK |
| L_48187LIND-48365RITZVILLC1 | OPEN Branch LIND_115.0 (48187) TO RITZVILL_115.0 (48365) CKT 1 |  | CHECK |
| L_48187LIND-48375ROXBOROC1 | OPEN Branch LIND_115.0 (48187) TO ROXBORO_115.0 (48375) CKT 1 |  | CHECK |
| L_48194LOCUST-48237MILLWOODC1 | OPEN Branch LOCUST_115.0 (48194) TO MILLWOOD_115.0 (48237) CKT 1 |  | CHECK |
| L_48195LOLO-48345POUNDTAPC1 | OPEN Branch LOLO_115.0 (48195) TO POUNDTAP_115.0 (48345) CKT 1 |  | CHECK |
| L_48195LOLO-48423SWEETWTRC1 | OPEN Branch LOLO_115.0 (48195) TO SWEETWTR_115.0 (48423) CKT 1 |  | CHECK |
| L_48195LOLO-48429TENTHSTWC1 | OPEN Branch LOLO_115.0 (48195) TO TENTHSTW_115.0 (48429) CKT 1 |  | CHECK |
| L_48197LOLO-48512DRYCREEKC1 | OPEN Branch DRYCREEK_230.0 (48512) TO LOLO_230.0 (48197) CKT 1 |  | CHECK |
| L_48197LOLO-60278IMNAHAC1 | OPEN Branch LOLO_230.0 (48197) TO IMNAHA_230.0 (60278) CKT 1 |  | CHECK |
| L_48199LONGLAKA-48201LONGLAKBC1 | OPEN Branch LONGLAKA_115.0 (48199) TO LONGLAKB_115.0 (48201) CKT 1 |  | CHECK |
| L_48215LUCKYF-48217LUCKYFTPC1 | OPEN Branch LUCKY F_115.0 (48215) TO LUCKYFTP_115.0 (48217) CKT 1 |  | CHECK |
| L_48219LYONSTND-48371ROSSPARKC1 | OPEN Branch LYONSTND_115.0 (48219) TO ROSSPARK_115.0 (48371) CKT 1 |  | CHECK |
| L_48221MARENGO-47073RALSTONBC1 | OPEN Branch MARENGO_115.0 (48221) TO RALSTONB_115.0 (47073) CKT 1 |  | CHECK |
| L_48225METRO-48339POSTSTRTC1 | OPEN Branch METRO_115.0 (48225) TO POSTSTRT_115.0 (48339) CKT 1 |  | CHECK |
| L_48225METRO-48421SUNSETC1 | OPEN Branch METRO_115.0 (48225) TO SUNSET_115.0 (48421) CKT 1 |  | CHECK |
| L_48231MICATAP-48367ROCKFORDC1 | OPEN Branch MICA TAP_115.0 (48231) TO ROCKFORD_115.0 (48367) CKT 1 |  | CHECK |
| L_48233MILAN-48235MILANTPC1 | OPEN Branch MILAN_115.0 (48233) TO MILAN TP_115.0 (48235) CKT 1 |  | CHECK |
| L_48235MILANTP-41099TUMTUMC1 | OPEN Branch MILAN TP_115.0 (48235) TO TUM TUM_115.0 (41099) CKT 1 |  | CHECK |
| L_48239MISSION-48315PINECRKC1 | OPEN Branch MISSION_115.0 (48239) TO PINE CRK_115.0 (48315) CKT 1 |  | CHECK |
| L_48243MOSCCITY-48245MOSCITYTC1 | OPEN Branch MOSCCITY_115.0 (48243) TO MOSCITYT_115.0 (48245) CKT 1 |  | CHECK |
| L_48245MOSCITYT-48247MOSCOWC1 | OPEN Branch MOSCITYT_115.0 (48245) TO MOSCOW_115.0 (48247) CKT 1 |  | CHECK |
| L_48245MOSCITYT-48413SPULLMANC1 | OPEN Branch MOSCITYT_115.0 (48245) TO SPULLMAN_115.0 (48413) CKT 1 |  | CHECK |
| L_48247MOSCOW-48273NMOSCOWC1 | OPEN Branch MOSCOW_115.0 (48247) TO NMOSCOW_115.0 (48273) CKT 1 |  | CHECK |
| L_48247MOSCOW-48445VIOLAC1 | OPEN Branch MOSCOW_115.0 (48247) TO VIOLA_115.0 (48445) CKT 1 |  | CHECK |
| L_48255NLEWIST-48385SHAWNEEC1 | OPEN Branch N LEWIST_230.0 (48255) TO SHAWNEE_230.0 (48385) CKT 1 |  | CHECK |
| L_48255NLEWIST-48512DRYCREEKC1 | OPEN Branch DRYCREEK_230.0 (48512) TO N LEWIST_230.0 (48255) CKT 1 |  | CHECK |
| L_48258NEWPORTT-48298OLDTOWNC1 | OPEN Branch NEWPORTT_115.0 (48258) TO OLDTOWN_115.0 (48298) CKT 1 |  | CHECK |
| L_48261NEZPERCE-48303OROFINOC1 | OPEN Branch NEZPERCE_115.0 (48261) TO OROFINO_115.0 (48303) CKT 1 |  | CHECK |
| L_48271NINTHCNT-48431THIRHACHC1 | OPEN Branch NINTHCNT_115.0 (48271) TO THIRHACH_115.0 (48431) CKT 1 |  | CHECK |
| L_48277NORTHEAS-48449WAIKIKITC1 | OPEN Branch NORTHEAS_115.0 (48277) TO WAIKIKIT_115.0 (48449) CKT 1 |  | CHECK |
| L_48279NORTHWES-48461WESTC1 | OPEN Branch NORTHWES_115.0 (48279) TO WEST_115.0 (48461) CKT 1 |  | CHECK |
| L_48281NOXON-40787NOXONBPAC1 | OPEN Branch NOXON_230.0 (48281) TO NOXONBPA_230.0 (40787) CKT 1 |  | CHECK |
| L_48281NOXON-48317PINECRKC1 | OPEN Branch NOXON_230.0 (48281) TO PINE CRK_230.0 (48317) CKT 1 |  | CHECK |
| L_48281NOXON-48317PINECRKC1 | OPEN Gen NOXON34_ 14.4 (48287) #3 |  | CHECK |
| L_48281NOXON-48317PINECRKC1 | OPEN Gen NOXON34_ 14.4 (48287) #4 |  | CHECK |
| L_48289NOXONCON-41091TROUTCRC1 | OPEN Branch NOXONCON_230.0 (48289) TO TROUT CR_230.0 (41091) CKT 1 |  | CHECK |
| L_48291NPULLMAN-48383SHAWNEEC1 | OPEN Branch NPULLMAN_115.0 (48291) TO SHAWNEE_115.0 (48383) CKT 1 |  | CHECK |
| L_48297OGARA-48315PINECRKC1 | OPEN Branch OGARA_115.0 (48297) TO PINE CRK_115.0 (48315) CKT 1 |  | CHECK |
| L_48297OGARA-48323PLUMMERC1 | OPEN Branch OGARA_115.0 (48297) TO PLUMMER_115.0 (48323) CKT 1 |  | CHECK |
| L_48297OGARA-48417STMARIESC1 | OPEN Branch OGARA_115.0 (48297) TO STMARIES_115.0 (48417) CKT 1 |  | CHECK |
| L_48298OLDTOWN-48300OLDTOWNAC1 | OPEN Branch OLDTOWN_115.0 (48298) TO OLDTOWNA_115.0 (48300) CKT 1 |  | CHECK |
| L_48299OPPORTUN-41107VALYWAYC1 | OPEN Branch OPPORTUN_115.0 (48299) TO VALY WAY_115.0 (41107) CKT 1 |  | CHECK |
| L_48303OROFINO-48459WEIPPEC1 | OPEN Branch OROFINO_115.0 (48303) TO WEIPPE_115.0 (48459) CKT 1 |  | CHECK |
| L_48305OSBURN-48315PINECRKC1 | OPEN Branch OSBURN_115.0 (48305) TO PINE CRK_115.0 (48315) CKT 1 |  | CHECK |
| L_48305OSBURN-48453WALLACEC1 | OPEN Branch OSBURN_115.0 (48305) TO WALLACE_115.0 (48453) CKT 1 |  | CHECK |
| L_48307OTHELLO-48308LEE&REYNC1 | OPEN Branch LEE&REYN_115.0 (48308) TO OTHELLO_115.0 (48307) CKT 1 |  | CHECK |
| L_48307OTHELLO-48309OTHELOSSC1 | OPEN Branch OTHELLO_115.0 (48307) TO OTHELOSS_115.0 (48309) CKT 1 |  | CHECK |
| L_48308LEE&REYN-48455WARDENAC1 | OPEN Branch LEE&REYN_115.0 (48308) TO WARDEN A_115.0 (48455) CKT 1 |  | CHECK |
| L_48309OTHELOSS-48393SOTHELOTC1 | OPEN Branch OTHELOSS_115.0 (48309) TO SOTHELOT_115.0 (48393) CKT 1 |  | CHECK |
| L_48309OTHELOSS-48455WARDENAC1 | OPEN Branch OTHELOSS_115.0 (48309) TO WARDEN A_115.0 (48455) CKT 1 |  | CHECK |
| L_48311OTIS-48185LIBTYLKC1 | OPEN Branch OTIS_115.0 (48311) TO LIBTYLK_115.0 (48185) CKT 1 |  | CHECK |
| L_48313PALOUSE-48445VIOLAC1 | OPEN Branch PALOUSE_115.0 (48313) TO VIOLA_115.0 (48445) CKT 1 |  | CHECK |
| L_48319PLEASANT-48355RATHDRUMC1 | OPEN Branch PLEASANT_115.0 (48319) TO RATHDRUM_115.0 (48355) CKT 1 |  | CHECK |
| L_48325PLUMMERG-48327PLUMMWEAC1 | OPEN Branch PLUMMERG_ 13.8 (48325) TO PLUMMWEA_ 13.8 (48327) CKT 1 |  | CHECK |
| L_48339POSTSTRT-48431THIRHACHC1 | OPEN Branch POSTSTRT_115.0 (48339) TO THIRHACH_115.0 (48431) CKT 1 |  | CHECK |
| L_48343POUNDLNE-48345POUNDTAPC1 | OPEN Branch POUNDLNE_115.0 (48343) TO POUNDTAP_115.0 (48345) CKT 1 |  | CHECK |
| L_48343POUNDLNE-48510DRYCREEKC1 | OPEN Branch DRYCREEK_115.0 (48510) TO POUNDLNE_115.0 (48343) CKT 1 |  | CHECK |
| L_48345POUNDTAP-48389SLEWISTC1 | OPEN Branch POUNDTAP_115.0 (48345) TO SLEWIST_115.0 (48389) CKT 1 |  | CHECK |
| L_48351RATHBUS1-48355RATHDRUMC1 | OPEN Branch RATHBUS1_115.0 (48351) TO RATHDRUM_115.0 (48355) CKT 1 |  | CHECK |
| L_48353RATHBUS2-48356RATHDRMEC1 | OPEN Branch RATHBUS2_115.0 (48353) TO RATHDRME_115.0 (48356) CKT 1 |  | CHECK |
| L_48356RATHDRME-48355RATHDRUMC1 | OPEN Branch RATHDRME_115.0 (48356) TO RATHDRUM_115.0 (48355) CKT 1 |  | CHECK |
| L_48357RATHDRUM-48524BOULDERC1 | OPEN Branch BOULDER_230.0 (48524) TO RATHDRUM_230.0 (48357) CKT 1 |  | CHECK |
| L_48365RITZVILL-48411SPRAGUEC1 | OPEN Branch RITZVILL_115.0 (48365) TO SPRAGUE_115.0 (48411) CKT 1 |  | CHECK |
| L_48369ROSALIA-48397SPANGLEC1 | OPEN Branch ROSALIA_115.0 (48369) TO SPANGLE_115.0 (48397) CKT 1 |  | CHECK |
| L_48371ROSSPARK-48431THIRHACHC1 | OPEN Branch ROSSPARK_115.0 (48371) TO THIRHACH_115.0 (48431) CKT 1 |  | CHECK |
| L_48373ROUNDLKT-48419STRATFRDC1 | OPEN Branch ROUNDLKT_115.0 (48373) TO STRATFRD_115.0 (48419) CKT 1 |  | CHECK |
| L_48375ROXBORO-48455WARDENAC1 | OPEN Branch ROXBORO_115.0 (48375) TO WARDEN A_115.0 (48455) CKT 1 |  | CHECK |
| L_48381SEVENTAP-48447WAIKIKIC1 | OPEN Branch SEVENTAP_115.0 (48381) TO WAIKIKI_115.0 (48447) CKT 1 |  | CHECK |
| L_48388SILVRLK2-48387SILVRLAKC1 | OPEN Branch SILVRLAK_115.0 (48387) TO SILVRLK2_115.0 (48388) CKT 1 |  | CHECK |
| L_48391SOTHELLO-48393SOTHELOTC1 | OPEN Branch SOTHELLO_115.0 (48391) TO SOTHELOT_115.0 (48393) CKT 1 |  | CHECK |
| L_48393SOTHELOT-48425TAUNTONC1 | OPEN Branch SOTHELOT_115.0 (48393) TO TAUNTON_115.0 (48425) CKT 1 |  | CHECK |
| L_48395SOUTHEAS-48421SUNSETC1 | OPEN Branch SOUTHEAS_115.0 (48395) TO SUNSET_115.0 (48421) CKT 1 |  | CHECK |
| L_48401SPIRITLK-48403SPIRITLTC1 | OPEN Branch SPIRITLK_115.0 (48401) TO SPIRITLT_115.0 (48403) CKT 1 |  | CHECK |
| L_48405SPKINDPK-48520BOULDERWC1 | OPEN Branch BOULDERW_115.0 (48520) TO SPKINDPK_115.0 (48405) CKT 1 |  | CHECK |
| L_48409SPKWASTE-48461WESTC1 | OPEN Branch SPKWASTE_115.0 (48409) TO WEST_115.0 (48461) CKT 1 |  | CHECK |
| L_48419STRATFRD-46447SUMERFALC1 | OPEN Branch STRATFRD_115.0 (48419) TO SUMERFAL_115.0 (46447) CKT 1 |  | CHECK |
| L_48419STRATFRD-48471WILSNCKTC1 | OPEN Branch STRATFRD_115.0 (48419) TO WILSNCKT_115.0 (48471) CKT 1 |  | CHECK |
| L_48430TERRVIEW-48273NMOSCOWC1 | OPEN Branch NMOSCOW_115.0 (48273) TO TERRVIEW_115.0 (48430) CKT 1 |  | CHECK |
| L_48430TERRVIEW-48291NPULLMANC1 | OPEN Branch TERRVIEW_115.0 (48430) TO NPULLMAN_115.0 (48291) CKT 1 |  | CHECK |
| L_48443VANTAVA-45327WALAWALAC1 | OPEN Branch VANT AVA_230.0 (48443) TO WALAWALA_230.0 (45327) CKT 1 |  | CHECK |
| L_48443VANTAVA-46169WANAPUMC1 | OPEN Branch VANT AVA_230.0 (48443) TO WANAPUM_230.0 (46169) CKT 1 |  | CHECK |
| L_48447WAIKIKI-48449WAIKIKITC1 | OPEN Branch WAIKIKI_115.0 (48447) TO WAIKIKIT_115.0 (48449) CKT 1 |  | CHECK |
| L_48451WALAAVA-45327WALAWALAC1 | OPEN Branch WALA AVA_230.0 (48451) TO WALAWALA_230.0 (45327) CKT 1 |  | CHECK |
| L_48451WALAAVA-48512DRYCREEKC1 | OPEN Branch DRYCREEK_230.0 (48512) TO WALA AVA_230.0 (48451) CKT 1 |  | CHECK |
| L_48451WALAAVA-48512DRYCREEKC1 | SET INJECTION GROUP HOPKINS RIDGE TO 120 MW |  | CHECK |
| L_48451WALAAVA-48512DRYCREEKC1 | SET INJECTION GROUP NINE MILE WIND TO 80 MW |  | CHECK |
| L_48455WARDENA-46117WARDENTC1 | OPEN Branch WARDEN A_115.0 (48455) TO WARDEN T_115.0 (46117) CKT 1 |  | CHECK |
| L_48463WEST-41275WESTBPA1C1 | OPEN Branch WEST_230.0 (48463) TO WESTBPA1_230.0 (41275) CKT 1 |  | CHECK |
| L_48463WEST-41276WESTBPA2C1 | OPEN Branch WEST_230.0 (48463) TO WESTBPA2_230.0 (41276) CKT 1 |  | CHECK |
| L_48467WILBUR-48469WILBURTC1 | OPEN Branch WILBUR_115.0 (48467) TO WILBURT_115.0 (48469) CKT 1 |  | CHECK |
| L_48471WILSNCKT-46129WILSONCKC1 | OPEN Branch WILSNCKT_115.0 (48471) TO WILSONCK_115.0 (46129) CKT 1 |  | CHECK |
| L_48475CLWTR1-48476CLWTR2C1 | OPEN Branch CLWTR1_ 34.5 (48475) TO CLWTR2_ 34.5 (48476) CKT 1 |  | CHECK |
| L_48475CLWTR1-48481CLWTR7C1 | OPEN Branch CLWTR1_ 34.5 (48475) TO CLWTR7_ 34.5 (48481) CKT 1 |  | CHECK |
| L_48476CLWTR2-48477CLWTR3C1 | OPEN Branch CLWTR2_ 34.5 (48476) TO CLWTR3_ 34.5 (48477) CKT 1 |  | CHECK |
| L_48477CLWTR3-48478CLWTR4C1 | OPEN Branch CLWTR3_ 34.5 (48477) TO CLWTR4_ 34.5 (48478) CKT 1 |  | CHECK |
| L_48478CLWTR4-48479CLWTR5C1 | OPEN Branch CLWTR4_ 34.5 (48478) TO CLWTR5_ 34.5 (48479) CKT 1 |  | CHECK |
| L_48479CLWTR5-48480CLWTR6C1 | OPEN Branch CLWTR5_ 34.5 (48479) TO CLWTR6_ 34.5 (48480) CKT 1 |  | CHECK |
| L_48480CLWTR6-48481CLWTR7C1 | OPEN Branch CLWTR6_ 34.5 (48480) TO CLWTR7_ 34.5 (48481) CKT 1 |  | CHECK |
| L_48490CWBUS1-48492CWBUS3C1 | OPEN Branch CWBUS1_ 12.0 (48490) TO CWBUS3_ 12.0 (48492) CKT 1 |  | CHECK |
| L_48491CWBUS2-48493CWBUS4C1 | OPEN Branch CWBUS2_ 12.0 (48491) TO CWBUS4_ 12.0 (48493) CKT 1 |  | CHECK |
| L_48494CWBUS5-48496CWBUS7C1 | OPEN Branch CWBUS5_ 12.0 (48494) TO CWBUS7_ 12.0 (48496) CKT 1 |  | CHECK |
| L_48495CWBUS6-48497CWBUS8C1 | OPEN Branch CWBUS6_ 12.0 (48495) TO CWBUS8_ 12.0 (48497) CKT 1 |  | CHECK |
| L_48510DRYCREEK-48113DRYGULCHC1 | OPEN Branch DRYCREEK_115.0 (48510) TO DRYGULCH_115.0 (48113) CKT 1 |  | CHECK |
| L_48510DRYCREEK-48514CRCHFELDC1 | OPEN Branch DRYCREEK_115.0 (48510) TO CRCHFELD_115.0 (48514) CKT 1 |  | CHECK |
| L_48520BOULDERW-48021BARKERC1 | OPEN Branch BOULDERW_115.0 (48520) TO BARKER_115.0 (48021) CKT 1 |  | CHECK |
| L_48520BOULDERW-48311OTISC1 | OPEN Branch BOULDERW_115.0 (48520) TO OTIS_115.0 (48311) CKT 1 |  | CHECK |
| L_48522BOULDERE-48165IRVINC1 | OPEN Branch BOULDERE_115.0 (48522) TO IRVIN_115.0 (48165) CKT 1 |  | CHECK |
| L_48522BOULDERE-48520BOULDERWC1 | OPEN Branch BOULDERE_115.0 (48522) TO BOULDERW_115.0 (48520) CKT 1 |  | CHECK |
| L_50822NLYPHS-40145BOUNDARYC1 | OPEN Branch NLYPHS_230.0 (50822) TO BOUNDARY_230.0 (40145) CKT 1 |  | CHECK |
| L_52219WAN230-40145BOUNDARYC1 | Unlinked Action: BRANCH 52219 40145 1 OPEN |  | CHECK |
| L_62085CROWCRB-48055BURKAVABC1 | Unlinked Action: BRANCH 62085 48055 1 OPEN |  | CHECK |
| L_62086THOMSON-48053BURKAVAAC1 | Unlinked Action: BRANCH 62086 48053 1 OPEN |  | CHECK |
| L_Addy - Bell 230 & Addy - Bell 115 (BPA) | OPEN Bus LOON LK_115.0 (48213) |  | CHECK |
| L_Addy - Bell 230 & Addy - Bell 115 (BPA) | OPEN Bus CLAYTON_115.0 (40245) |  | CHECK |
| L_Addy - Bell 230 & Addy - Bell 115 (BPA) | OPEN Bus DEER PRK_115.0 (40337) |  | CHECK |
| L_Addy - Bell 230 & Addy - Bell 115 (BPA) | OPEN Bus MILAN TP_115.0 (48235) |  | CHECK |
| L_Addy - Bell 230 & Addy - Bell 115 (BPA) | OPEN Bus MILAN_115.0 (48233) |  | CHECK |
| L_Addy - Bell 230 & Addy - Bell 115 (BPA) | OPEN Bus TUM TUM_115.0 (41099) |  | CHECK |
| L_Addy - Bell 230 & Addy - Bell 115 (BPA) | OPEN Bus HALFMOON_115.0 (40495) |  | CHECK |
| L_Addy - Bell 230 & Addy - Bell 115 (BPA) | OPEN Bus COLBERTT_115.0 (40255) |  | CHECK |
| L_Addy - Bell 230 & Addy - Bell 115 (BPA) | OPEN Bus COLBERT_115.0 (48079) |  | CHECK |
| L_Addy - Bell 230 & Addy - Bell 115 (BPA) | OPEN Bus MEAD TAP_115.0 (40730) |  | CHECK |
| L_Addy - Bell 230 & Addy - Bell 115 (BPA) | OPEN Bus MEAD SUB_115.0 (48222) |  | CHECK |
| L_Addy - Bell 230 & Addy - Bell 115 (BPA) | OPEN MultiSectionLine ADDY 2_230.0 (40021) TO BELL S3_230.0 (40090) CKT 1 |  | CHECK |
| L_Addy - Bell 230 & Addy - Bell 115 (BPA) | OPEN Bus BOUNDPH6_230.0 (46486) | SoB>650 | CHECK |
| L_Addy - Bell 230 & Addy - Bell 115 (BPA) | OPEN Bus BOUNDPH5_230.0 (46484) | SoB>650 | CHECK |
| L_Beacon S - Boulder & Beacon N - Rathdrum 230 (AVA) | OPEN Branch BEACON S_230.0 (48031) TO BOULDER_230.0 (48524) CKT 1 |  | CHECK |
| L_Beacon S - Boulder & Beacon N - Rathdrum 230 (AVA) | OPEN Branch BEACON N_230.0 (48025) TO RATHDRUM_230.0 (48357) CKT 2 |  | CHECK |
| L_Beacon S - Boulder 230 & Beacon N - Boulder 115 (AVA) | OPEN Branch BEACON S_230.0 (48031) TO BOULDER_230.0 (48524) CKT 1 |  | CHECK |
| L_Beacon S - Boulder 230 & Beacon N - Boulder 115 (AVA) | OPEN Bus SPKINDPK_115.0 (48405) |  | CHECK |
| L_Beacon S - Boulder 230 & Beacon S - Boulder 115 (AVA) | OPEN Branch BEACON S_230.0 (48031) TO BOULDER_230.0 (48524) CKT 1 |  | CHECK |
| L_Beacon S - Boulder 230 & Beacon S - Boulder 115 (AVA) | OPEN Bus LOCUST_115.0 (48194) |  | CHECK |
| L_Beacon S - Boulder 230 & Beacon S - Boulder 115 (AVA) | OPEN Bus MILLWOOD_115.0 (48237) |  | CHECK |
| L_Beacon S - Boulder 230 & Beacon S - Boulder 115 (AVA) | OPEN Bus I.E.PAPR_115.0 (48163) |  | CHECK |
| L_Beacon S - Boulder 230 & Beacon S - Boulder 115 (AVA) | OPEN Bus IRVIN_115.0 (48165) |  | CHECK |
| L_Bell - Coulee #3 & #5 230 (BPA) | OPEN MultiSectionLine BELL S2_230.0 (40088) TO COULEES3_230.0 (41358) CKT 5 |  | CHECK |
| L_Bell - Coulee #3 & #5 230 (BPA) | OPEN MultiSectionLine BELL S3_230.0 (40090) TO COULEES1_230.0 (41356) CKT 3 |  | CHECK |
| L_Bell - Coulee 500 & Bell - Westside 230 (BPA) | OPEN Bus WESTBPA1_230.0 (41275) |  | CHECK |
| L_Bell - Coulee 500 & Bell - Westside 230 (BPA) | OPEN Branch BELL BPA_500.0 (40091) TO COULE R1_500.0 (40288) CKT 6 |  | CHECK |
| L_Bell - Coulee 500 & Bell - Westside 230 (BPA) | OPEN Load MILCTYDC_230.0 (63010) #D1 |  | CHECK |
| L_Bell - Coulee 500 & Bell - Westside 230 (BPA) | OPEN Bus LIB PH1_230.0 (44200) | WMH > 1000 | CHECK |
| L_Bell - Coulee 500 & Bell - Westside 230 (BPA) | OPEN Bus LIB PH2_230.0 (44201) | WMH > 1000 | CHECK |
| L_Bell - Coulee 500 & Westside - Coulee 230 (BPA) | OPEN Bus WESTBPA2_230.0 (41276) |  | CHECK |
| L_Bell - Coulee 500 & Westside - Coulee 230 (BPA) | OPEN Load MILCTYDC_230.0 (63010) #D1 |  | CHECK |
| L_Bell - Coulee 500 & Westside - Coulee 230 (BPA) | OPEN Branch BELL BPA_500.0 (40091) TO COULE R1_500.0 (40288) CKT 6 |  | CHECK |
| L_Bell - Coulee 500 & Westside - Coulee 230 (BPA) | OPEN Bus LIB PH1_230.0 (44200) | WMH > 1000 | CHECK |
| L_Bell - Coulee 500 & Westside - Coulee 230 (BPA) | OPEN Bus LIB PH2_230.0 (44201) | WMH > 1000 | CHECK |
| L_Bell - Sacheen & Bell - Usk 230 (BPA) | OPEN Branch BELL S1_230.0 (40086) TO SACHEEN_230.0 (40909) CKT 1 |  | CHECK |
| L_Bell - Sacheen & Bell - Usk 230 (BPA) | OPEN Branch BELL S2_230.0 (40088) TO USK_230.0 (47091) CKT 1 |  | CHECK |
| L_Bell - Sacheen & Bell - Usk 230 (BPA) | OPEN Bus BOUNDPH6_230.0 (46486) | SoB>650 | CHECK |
| L_Bell - Sacheen & Bell - Usk 230 (BPA) | OPEN Bus BOUNDPH5_230.0 (46484) | SoB>650 | CHECK |
| L_Bell - Westside & Bell - Coulee #3 230 (AVA/BPA) | OPEN Bus WESTBPA1_230.0 (41275) |  | CHECK |
| L_Bell - Westside & Bell - Coulee #3 230 (AVA/BPA) | OPEN MultiSectionLine BELL S3_230.0 (40090) TO COULEES1_230.0 (41356) CKT 3 |  | CHECK |
| L_Bell - Westside 230 kV (BPA) | OPEN Branch BELL S1_230.0 (40086) TO WESTBPA1_230.0 (41275) CKT 1 |  | CHECK |
| L_Bell S3 - Lancaster & Beacon N - Rathdrum 230 (AVA/BPA) | OPEN Branch BEACON N_230.0 (48025) TO RATHDRUM_230.0 (48357) CKT 2 |  | CHECK |
| L_Bell S3 - Lancaster & Beacon N - Rathdrum 230 (AVA/BPA) | OPEN Gen LANCAS G_ 18.0 (47568) #1 |  | CHECK |
| L_Bell S3 - Lancaster & Beacon N - Rathdrum 230 (AVA/BPA) | OPEN Gen LANCAS S_ 13.8 (47569) #1 |  | CHECK |
| L_Bell S3 - Lancaster & Beacon N - Rathdrum 230 (AVA/BPA) | OPEN MultiSectionLine BELL S3_230.0 (40090) TO LANCASTR_230.0 (40624) CKT 1 |  | CHECK |
| L_Bell S3 - Lancaster 230 & Bell - Taft 500 (BPA) | OPEN Gen LANCAS G_ 18.0 (47568) #1 |  | CHECK |
| L_Bell S3 - Lancaster 230 & Bell - Taft 500 (BPA) | OPEN Gen LANCAS S_ 13.8 (47569) #1 |  | CHECK |
| L_Bell S3 - Lancaster 230 & Bell - Taft 500 (BPA) | OPEN Load MILCTYDC_230.0 (63010) #D1 |  | CHECK |
| L_Bell S3 - Lancaster 230 & Bell - Taft 500 (BPA) | OPEN Shunt GARRISON_500.0 (40459) #r |  | CHECK |
| L_Bell S3 - Lancaster 230 & Bell - Taft 500 (BPA) | OPEN MultiSectionLine BELL S3_230.0 (40090) TO LANCASTR_230.0 (40624) CKT 1 |  | CHECK |
| L_Bell S3 - Lancaster 230 & Bell - Taft 500 (BPA) | OPEN MultiSectionLine BELL SC_500.0 (40096) TO TAFT_500.0 (41057) CKT 1 |  | CHECK |
| L_Bell S3 - Lancaster 230 & Bell - Taft 500 (BPA) | OPEN Bus LIB PH1_230.0 (44200) | WMH > 1000 | CHECK |
| L_Bell S3 - Lancaster 230 & Bell - Taft 500 (BPA) | OPEN Bus LIB PH2_230.0 (44201) | WMH > 1000 | CHECK |
| L_Boulder - Otis 115 1 & 2 (AVA) | OPEN Branch BOULDERW_115.0 (48520) TO OTIS_115.0 (48311) CKT 1 |  | CHECK |
| L_Boulder - Otis 115 1 & 2 (AVA) | OPEN Bus BARKER_115.0 (48021) |  | CHECK |
| L_Boulder - Rathdrum & Beacon N - Rathdrum 230 (AVA) | OPEN Branch BOULDER_230.0 (48524) TO RATHDRUM_230.0 (48357) CKT 1 |  | CHECK |
| L_Boulder - Rathdrum & Beacon N - Rathdrum 230 (AVA) | OPEN Branch BEACON N_230.0 (48025) TO RATHDRUM_230.0 (48357) CKT 2 |  | CHECK |
| L_Boulder - Rathdrum 230 & Boulder - Rathdrum 115 (AVA) | OPEN Branch BOULDER_230.0 (48524) TO RATHDRUM_230.0 (48357) CKT 1 |  | CHECK |
| L_Boulder - Rathdrum 230 & Boulder - Rathdrum 115 (AVA) | OPEN Bus MOAB_115.0 (47511) |  | CHECK |
| L_Boulder - Rathdrum 230 & Boulder - Rathdrum 115 (AVA) | OPEN Bus PLEASANT_115.0 (48319) |  | CHECK |
| L_Bridger - Goshen & Bridger - Kinport 345 | OPEN Gen BRIDGER1_ 22.0 (60086) #1 |  | CHECK |
| L_Bridger - Goshen & Bridger - Kinport 345 | OPEN Gen BRIDGER2_ 22.0 (60087) #1 |  | CHECK |
| L_Bridger - Goshen & Bridger - Kinport 345 | SET SWITCHED SHUNT AT BUS GOSHEN_161.0 (65670) TO 100 MVR |  | CHECK |
| L_Bridger - Goshen & Bridger - Kinport 345 | OPEN MultiSectionLine BRIDGER_345.0 (60085) TO KINPORT_345.0 (60190) CKT 1 |  | CHECK |
| L_Brownlee - Hells Canyon & Oxbow - Lolo 230 | OPEN Branch HELLSCYN_230.0 (60150) TO BROWNLEE_230.0 (60095) CKT 1 |  | CHECK |
| L_Brownlee - Hells Canyon & Oxbow - Lolo 230 | OPEN Gen HELSCYN1_ 14.4 (60151) #1 |  | CHECK |
| L_Brownlee - Hells Canyon & Oxbow - Lolo 230 | OPEN Branch LOLO_230.0 (48197) TO IMNAHA_230.0 (60278) CKT 1 |  | CHECK |
| L_Brownlee - Hells Canyon & Oxbow - Lolo 230 | OPEN MultiSectionLine OXBOW_230.0 (60275) TO IMNAHA_230.0 (60278) CKT 1 |  | CHECK |
| L_Brownlee - Oxbow #1 & Brownlee - Hells Canyon 230 | OPEN Branch OXBOW_230.0 (60275) TO BROWNLEE_230.0 (60095) CKT 1 |  | CHECK |
| L_Brownlee - Oxbow #1 & Brownlee - Hells Canyon 230 | OPEN Branch HELLSCYN_230.0 (60150) TO BROWNLEE_230.0 (60095) CKT 1 |  | CHECK |
| L_Brownlee - Oxbow #1 & Brownlee - Hells Canyon 230 | OPEN Gen HELSCYN1_ 14.4 (60151) #1 |  | CHECK |
| L_Brownlee - Quartz - LaGrande 230 (IDA) | OPEN Bus QUARTZTP_230.0 (60310) |  | CHECK |
| L_Cab Gorg - Rathdrum & Noxon - Lancaster 230 (AVA/BPA) | OPEN MultiSectionLine LANCASTR_230.0 (40624) TO NOXONBPA_230.0 (40787) CKT 1 |  | CHECK |
| L_Cab Gorg - Rathdrum & Noxon - Lancaster 230 (AVA/BPA) | OPEN Bus LIB PH2_230.0 (44201) |  | CHECK |
| L_Cab Gorg - Rathdrum & Noxon - Lancaster 230 (AVA/BPA) | OPEN Bus LAKEVIEW_230.0 (48179) |  | CHECK |
| L_Cab Gorg - Rathdrum & Noxon - Lancaster 230 (AVA/BPA) | OPEN Gen NOXON12_ 14.4 (48285) #2 | WMH > 1450 | CHECK |
| L_Cab Gorg - Rathdrum & Noxon - Lancaster 230 (AVA/BPA) | OPEN Gen NOXON34_ 14.4 (48287) #4 | WMH > 1450 | CHECK |
| L_Cab Gorg - Rathdrum & Noxon - Lancaster 230 (AVA/BPA) | OPEN Gen NOXON34_ 14.4 (48287) #3 | WMH > 1450 | CHECK |
| L_Cab Gorg - Rathdrum & Noxon - Lancaster 230 (AVA/BPA) | OPEN Gen NOXON12_ 14.4 (48285) #1 | WMH > 1450 | CHECK |
| L_CDA - Ramsey & Ramsey - Rathdrum #2 115 (AVA) | OPEN Branch CDA_115.0 (48067) TO RAMSEY_115.0 (48349) CKT 1 |  | CHECK |
| L_CDA - Ramsey & Ramsey - Rathdrum #2 115 (AVA) | OPEN Bus HERN_115.0 (48155) |  | CHECK |
| L_CDA - Ramsey & Ramsey - Rathdrum #2 115 (AVA) | OPEN Bus HUETTER_115.0 (48159) |  | CHECK |
| L_CDA - Rathdrum & Pine St - Rathdrum 115 (AVA) | OPEN Bus HAYDEN_115.0 (48148) |  | CHECK |
| L_CDA - Rathdrum & Pine St - Rathdrum 115 (AVA) | OPEN Bus DALTONT_115.0 (48097) |  | CHECK |
| L_CDA - Rathdrum & Pine St - Rathdrum 115 (AVA) | OPEN Bus DALTON A_115.0 (48093) |  | CHECK |
| L_CDA - Rathdrum & Pine St - Rathdrum 115 (AVA) | OPEN Bus SCARCELO_115.0 (40953) |  | CHECK |
| L_CDA - Rathdrum & Pine St - Rathdrum 115 (AVA) | OPEN Bus ATHOL_115.0 (40067) |  | CHECK |
| L_CDA - Rathdrum & Pine St - Rathdrum 115 (AVA) | OPEN Bus SPIRITLT_115.0 (48403) |  | CHECK |
| L_CDA - Rathdrum & Pine St - Rathdrum 115 (AVA) | OPEN Bus ATHOLTAP_115.0 (48017) |  | CHECK |
| L_CDA - Rathdrum & Pine St - Rathdrum 115 (AVA) | OPEN Bus SPIRITLK_115.0 (48401) |  | CHECK |
| L_CDA - Rathdrum & Pine St - Rathdrum 115 (AVA) | OPEN Bus HOODOO_115.0 (47505) |  | CHECK |
| L_CDA - Rathdrum & Pine St - Rathdrum 115 (AVA) | OPEN Bus BLANCHRD_115.0 (48043) |  | CHECK |
| L_CDA - Rathdrum & Pine St - Rathdrum 115 (AVA) | OPEN Bus NEWPORTT_115.0 (48258) |  | CHECK |
| L_CDA - Rathdrum & Pine St - Rathdrum 115 (AVA) | OPEN Bus OLDTOWN_115.0 (48298) |  | CHECK |
| L_CDA - Rathdrum & Pine St - Rathdrum 115 (AVA) | OPEN Bus OLDTOWNA_115.0 (48300) |  | CHECK |
| L_Columbia Falls - Kalispel 115 (BPA) | OPEN Branch COL FALL_115.0 (40247) TO KALISPEL_115.0 (40589) CKT 1 |  | CHECK |
| L_Dworshak - Hatwai 500 kV (BPA) | OPEN Shunt GARRISON_500.0 (40459) #r |  | CHECK |
| L_Dworshak - Hatwai 500 kV (BPA) | OPEN Branch DWOR 1_ 13.8 (40361) TO DWOR 2_ 13.8 (40363) CKT 1 |  | CHECK |
| L_Dworshak - Hatwai 500 kV (BPA) | OPEN Branch DWORSHAK_500.0 (40369) TO HATWAI_500.0 (40521) CKT 1 |  | CHECK |
| L_Dworshak - Hatwai 500 kV (BPA) | OPEN Gen DWOR 3_ 13.8 (40365) #1 |  | ALWAYS |
| L_Dworshak - Hatwai 500 kV (BPA) | OPEN Gen DWOR 2_ 13.8 (40363) #1 |  | ALWAYS |
| L_Dworshak - Hatwai 500 kV (BPA) | OPEN Load MILCTYDC_230.0 (63010) #D1 |  | CHECK |
| L_Dworshak - Hatwai 500 kV (BPA) | OPEN Bus LIB PH2_230.0 (44201) | West MT Hydro > 1000 | CHECK |
| L_Dworshak - Hatwai 500 kV (BPA) | OPEN Bus LIB PH1_230.0 (44200) | West MT Hydro > 1000 | CHECK |
| L_Dworshak - Hatwai 500 kV (BPA) | OPEN Gen LANCAS S_ 13.8 (47569) #1 | WEST OF HATWAI > 3500 | CHECK |
| L_Dworshak - Hatwai 500 kV (BPA) | OPEN Gen LANCAS G_ 18.0 (47568) #1 | WEST OF HATWAI > 3500 | CHECK |
| L_Dworshak - Taft 500 kV (BPA) | OPEN MultiSectionLine DWORSHAK_500.0 (40369) TO TAFT_500.0 (41057) CKT 1 |  | CHECK |
| L_Dworshak - Taft 500 kV (BPA) | OPEN Shunt GARRISON_500.0 (40459) #r |  | CHECK |
| L_Dworshak - Taft 500 kV (BPA) | OPEN Load MILCTYDC_230.0 (63010) #D1 |  | CHECK |
| L_Dworshak - Taft 500 kV (BPA) | OPEN Bus LIB PH1_230.0 (44200) | West MT Hydro > 1000 | CHECK |
| L_Dworshak - Taft 500 kV (BPA) | OPEN Bus LIB PH2_230.0 (44201) | West MT Hydro > 1000 | CHECK |
| L_Dworshak - Taft 500 kV (BPA) | OPEN Gen LANCAS S_ 13.8 (47569) #1 | WEST OF HATWAI > 3500 | CHECK |
| L_Dworshak - Taft 500 kV (BPA) | OPEN Gen LANCAS G_ 18.0 (47568) #1 | WEST OF HATWAI > 3500 | CHECK |
| L_Flathead - Columbia Falls 230 (BPA) | OPEN Branch COL FALL_230.0 (40249) TO FLATHEAD_230.0 (40421) CKT 1 |  | CHECK |
| L_Flathead - Columbia Falls 230 (BPA) | OPEN Gen HUNGHR34_ 13.8 (40556) #3 |  | ALWAYS |
| L_Flathead - Columbia Falls 230 (BPA) | OPEN Gen HUNGHR34_ 13.8 (40556) #4 |  | ALWAYS |
| L_Flathead - Columbia Falls 230 (BPA) | OPEN Bus LIB PH2_230.0 (44201) |  | CHECK |
| L_Hatwai - Lower Granite 500 kV (BPA) | OPEN Gen DWOR 3_ 13.8 (40365) #1 |  | ALWAYS |
| L_Hatwai - Lower Granite 500 kV (BPA) | SET INJECTION GROUP NINE MILE WIND TO 85 MW |  | CHECK |
| L_Hatwai - Lower Granite 500 kV (BPA) | OPEN Gen DWOR 2_ 13.8 (40363) #1 |  | ALWAYS |
| L_Hatwai - Lower Granite 500 kV (BPA) | OPEN Branch HATWAI_500.0 (40521) TO LOW GRAN_500.0 (40679) CKT 1 |  | CHECK |
| L_Hatwai - Lower Granite 500 kV (BPA) | OPEN Branch DWOR 1_ 13.8 (40361) TO DWOR 2_ 13.8 (40363) CKT 1 |  | ALWAYS |
| L_Hatwai - Lower Granite 500 kV (BPA) | OPEN Load MILCTYDC_230.0 (63010) #D1 |  | CHECK |
| L_Hatwai - Lower Granite 500 kV (BPA) | OPEN Shunt GARRISON_500.0 (40459) #r |  | CHECK |
| L_Hatwai - Lower Granite 500 kV (BPA) | SET INJECTION GROUP HOPKINS RIDGE TO 135 MW |  | CHECK |
| L_Hatwai - Lower Granite 500 kV (BPA) | OPEN Bus LIB PH2_230.0 (44201) | West MT Hydro > 1000 | CHECK |
| L_Hatwai - Lower Granite 500 kV (BPA) | OPEN Bus LIB PH1_230.0 (44200) | West MT Hydro > 1000 | CHECK |
| L_Hatwai - Lower Granite 500 kV (BPA) | OPEN Gen LANCAS S_ 13.8 (47569) #1 | WEST OF HATWAI > 3500 | CHECK |
| L_Hatwai - Lower Granite 500 kV (BPA) | OPEN Gen LANCAS G_ 18.0 (47568) #1 | WEST OF HATWAI > 3500 | CHECK |
| L_Hatwai - N Lewiston 230 & Clearwater - Lolo #1 115 (AVA) | OPEN Branch HATWAI_230.0 (40519) TO N LEWIST_230.0 (48255) CKT 1 |  | CHECK |
| L_Hatwai - N Lewiston 230 & Clearwater - Lolo #1 115 (AVA) | OPEN Branch CLEARWTR_115.0 (48075) TO LOLO_115.0 (48195) CKT 1 |  | CHECK |
| L_Hatwai - N Lewiston 230 & Clearwater - N Lewiston 115 | OPEN Branch HATWAI_230.0 (40519) TO N LEWIST_230.0 (48255) CKT 1 |  | CHECK |
| L_Hatwai - N Lewiston 230 & Clearwater - N Lewiston 115 | OPEN Branch CLEARWTR_115.0 (48075) TO N LEWIST_115.0 (48253) CKT 1 |  | CHECK |
| L_Hells Canyon - Brownlee 230 (IDA) | OPEN Branch HELLSCYN_230.0 (60150) TO BROWNLEE_230.0 (60095) CKT 1 |  | CHECK |
| L_Hells Canyon - Brownlee 230 (IDA) | OPEN Gen HELSCYN1_ 14.4 (60151) #1 |  | CHECK |
| L_Hot Springs - Flathead 230 (BPA) | OPEN Bus LION MTN_230.0 (47359) |  | CHECK |
| L_Hot Springs - Flathead 230 (BPA) | OPEN Gen HUNGHR34_ 13.8 (40556) #3 |  | ALWAYS |
| L_Hot Springs - Flathead 230 (BPA) | OPEN Gen HUNGHR34_ 13.8 (40556) #4 |  | ALWAYS |
| L_Hot Springs - Flathead 230 (BPA) | OPEN Bus LIB PH2_230.0 (44201) |  | CHECK |
| L_Libby - Conkelly 230 (BPA) | OPEN Bus HASKILL_230.0 (40513) |  | CHECK |
| L_Libby - Conkelly 230 (BPA) | OPEN Bus LIB PH2_230.0 (44201) |  | CHECK |
| L_Libby - Noxon & Libby - Conkelly 230 (BPA) | OPEN Bus HASKILL_230.0 (40513) |  | CHECK |
| L_Libby - Noxon & Libby - Conkelly 230 (BPA) | OPEN Bus TRUMB CR_230.0 (47360) |  | CHECK |
| L_Libby - Noxon & Libby - Conkelly 230 (BPA) | OPEN MultiSectionLine LIBBY_230.0 (40657) TO NOXONBPA_230.0 (40787) CKT 1 |  | CHECK |
| L_Libby - Noxon & Libby - Conkelly 230 (BPA) | OPEN Bus LIB PH1_230.0 (44200) |  | CHECK |
| L_Libby - Noxon & Libby - Conkelly 230 (BPA) | OPEN Bus LIB PH2_230.0 (44201) |  | CHECK |
| L_Libby - Troy 115 (BPA) | OPEN Branch LIBBY_115.0 (40655) TO LIBBYFEC_115.0 (47278) CKT 1 |  | CHECK |
| L_Lower Granite - Little Goose #1 & #2 500 (BPA) | OPEN Branch LIT GOOS_500.0 (40665) TO LOW GRAN_500.0 (40679) CKT 1 |  | CHECK |
| L_Lower Granite - Little Goose #1 & #2 500 (BPA) | OPEN Branch LIT GOOS_500.0 (40665) TO LOW GRAN_500.0 (40679) CKT 2 |  | CHECK |
| L_Lower Granite - Little Goose #1 & #2 500 (BPA) | OPEN Branch DWOR 1_ 13.8 (40361) TO DWOR 2_ 13.8 (40363) CKT 1 |  | CHECK |
| L_Lower Granite - Little Goose #1 & #2 500 (BPA) | OPEN Gen DWOR 2_ 13.8 (40363) #1 |  | CHECK |
| L_Lower Granite - Little Goose #1 & #2 500 (BPA) | OPEN Gen DWOR 3_ 13.8 (40365) #1 |  | CHECK |
| L_Lower Granite - Little Goose #1 & #2 500 (BPA) | OPEN Load MILCTYDC_230.0 (63010) #D1 |  | CHECK |
| L_Lower Granite - Little Goose #1 & #2 500 (BPA) | OPEN Shunt GARRISON_500.0 (40459) #r |  | CHECK |
| L_Lower Granite - Little Goose #1 & #2 500 (BPA) | OPEN Bus LIB PH1_230.0 (44200) | WMH > 1000 | CHECK |
| L_Lower Granite - Little Goose #1 & #2 500 (BPA) | OPEN Bus LIB PH2_230.0 (44201) | WMH > 1000 | CHECK |
| L_McNary - Roundup 230 (BPA) | OPEN Branch MCNRY S1_230.0 (41351) TO ROUNDUP_230.0 (40905) CKT 1 |  | CHECK |
| L_Midpoint - Summer Lake 500 (BPA) | OPEN Bus BURSUM11_500.0 (45030) |  | CHECK |
| L_Mill Creek - Amps 230 (NWE) | OPEN Bus PTRSNFLT_230.0 (62030) |  | CHECK |
| L_N Lewiston - Dry Creek 230 & N Lewiston - Pound Lane 115 (AVA) | OPEN Branch DRYCREEK_230.0 (48512) TO N LEWIST_230.0 (48255) CKT 1 |  | CHECK |
| L_N Lewiston - Dry Creek 230 & N Lewiston - Pound Lane 115 (AVA) | OPEN Bus SLEWIST_115.0 (48389) |  | CHECK |
| L_N Lewiston - Dry Creek 230 & N Lewiston - Pound Lane 115 (AVA) | OPEN Bus HOLBROOK_115.0 (48157) |  | CHECK |
| L_N Lewiston - Dry Creek 230 & N Lewiston - Pound Lane 115 (AVA) | OPEN Branch POUNDLNE_115.0 (48343) TO POUNDTAP_115.0 (48345) CKT 1 |  | CHECK |
| L_Noxon - Cab Gorg & Noxon - Lancaster 230 (AVA/BPA) | OPEN Branch CAB GORG_230.0 (48059) TO NOXON_230.0 (48281) CKT 1 |  | CHECK |
| L_Noxon - Cab Gorg & Noxon - Lancaster 230 (AVA/BPA) | OPEN Bus LIB PH2_230.0 (44201) |  | CHECK |
| L_Noxon - Cab Gorg & Noxon - Lancaster 230 (AVA/BPA) | OPEN MultiSectionLine LANCASTR_230.0 (40624) TO NOXONBPA_230.0 (40787) CKT 1 |  | CHECK |
| L_Noxon - Cab Gorg & Noxon - Lancaster 230 (AVA/BPA) | OPEN Gen NOXON12_ 14.4 (48285) #2 | WMH > 1450 | CHECK |
| L_Noxon - Cab Gorg & Noxon - Lancaster 230 (AVA/BPA) | OPEN Gen NOXON12_ 14.4 (48285) #1 | WMH > 1450 | CHECK |
| L_Noxon - Hot Spr #1 & Noxon - Libby 230 (BPA) | OPEN Bus NOXONCON_230.0 (48289) |  | CHECK |
| L_Noxon - Hot Spr #1 & Noxon - Libby 230 (BPA) | OPEN Bus TROUT CR_230.0 (41091) |  | CHECK |
| L_Noxon - Hot Spr #1 & Noxon - Libby 230 (BPA) | OPEN MultiSectionLine LIBBY_230.0 (40657) TO NOXONBPA_230.0 (40787) CKT 1 |  | CHECK |
| L_Noxon - Hot Spr #1 & Noxon - Libby 230 (BPA) | OPEN Bus LIB PH1_230.0 (44200) | WMH > 700 | CHECK |
| L_Noxon - Hot Spr #1 & Noxon - Libby 230 (BPA) | OPEN Bus LIB PH2_230.0 (44201) | WMH > 700 | CHECK |
| L_Noxon - Hot Spr 230 1 & 2 (BPA/AVA) | OPEN Branch HOT SPR_230.0 (40551) TO NOXON_230.0 (48281) CKT 2 |  | CHECK |
| L_Noxon - Hot Spr 230 1 & 2 (BPA/AVA) | OPEN Bus NOXONCON_230.0 (48289) |  | CHECK |
| L_Noxon - Hot Spr 230 1 & 2 (BPA/AVA) | OPEN Bus TROUT CR_230.0 (41091) |  | CHECK |
| L_Noxon - Lancaster 230 & Taft - Bell 500 (BPA) | OPEN Load MILCTYDC_230.0 (63010) #D1 |  | CHECK |
| L_Noxon - Lancaster 230 & Taft - Bell 500 (BPA) | OPEN Shunt GARRISON_500.0 (40459) #r |  | CHECK |
| L_Noxon - Lancaster 230 & Taft - Bell 500 (BPA) | OPEN MultiSectionLine LANCASTR_230.0 (40624) TO NOXONBPA_230.0 (40787) CKT 1 |  | CHECK |
| L_Noxon - Lancaster 230 & Taft - Bell 500 (BPA) | OPEN MultiSectionLine BELL SC_500.0 (40096) TO TAFT_500.0 (41057) CKT 1 |  | CHECK |
| L_Noxon - Lancaster 230 & Taft - Bell 500 (BPA) | OPEN Bus LIB PH1_230.0 (44200) | WMH > 1000 | CHECK |
| L_Noxon - Lancaster 230 & Taft - Bell 500 (BPA) | OPEN Bus LIB PH2_230.0 (44201) | WMH > 1000 | CHECK |
| L_Noxon - Pine Creek & Noxon - Hot Spr #2 230 (AVA) | OPEN Branch NOXON_230.0 (48281) TO PINE CRK_230.0 (48317) CKT 1 |  | CHECK |
| L_Noxon - Pine Creek & Noxon - Hot Spr #2 230 (AVA) | OPEN Branch HOT SPR_230.0 (40551) TO NOXON_230.0 (48281) CKT 2 |  | CHECK |
| L_Noxon - Pine Creek & Noxon - Hot Spr #2 230 (AVA) | OPEN Gen NOXON12_ 14.4 (48285) #1 | WMH > 1450 | CHECK |
| L_Noxon - Pine Creek & Noxon - Hot Spr #2 230 (AVA) | OPEN Gen NOXON12_ 14.4 (48285) #2 | WMH > 1450 | CHECK |
| L_Post Falls - Ramsey & Ramsey - Rathdrum #1 115 (AVA) | OPEN Bus PRAIRIE_115.0 (46245) |  | CHECK |
| L_Post Falls - Ramsey & Ramsey - Rathdrum #1 115 (AVA) | OPEN Bus APPLETAP_115.0 (48011) |  | CHECK |
| L_Post Falls - Ramsey & Ramsey - Rathdrum #1 115 (AVA) | OPEN Bus APPLEWAY_115.0 (48013) |  | CHECK |
| L_Post Falls - Ramsey & Ramsey - Rathdrum #1 115 (AVA) | OPEN Bus DALTON2T_115.0 (48095) |  | CHECK |
| L_Post Falls - Ramsey & Ramsey - Rathdrum #1 115 (AVA) | OPEN Bus AVONDALE_115.0 (48019) |  | CHECK |
| L_Ramsey - Rathdrum #1 & Boulder - Rathdrum 115 (AVA) | OPEN Bus APPLETAP_115.0 (48011) |  | CHECK |
| L_Ramsey - Rathdrum #1 & Boulder - Rathdrum 115 (AVA) | OPEN Bus APPLEWAY_115.0 (48013) |  | CHECK |
| L_Ramsey - Rathdrum #1 & Boulder - Rathdrum 115 (AVA) | OPEN Bus DALTON2T_115.0 (48095) |  | CHECK |
| L_Ramsey - Rathdrum #1 & Boulder - Rathdrum 115 (AVA) | OPEN Bus AVONDALE_115.0 (48019) |  | CHECK |
| L_Ramsey - Rathdrum #1 & Boulder - Rathdrum 115 (AVA) | OPEN Bus MOAB_115.0 (47511) |  | CHECK |
| L_Ramsey - Rathdrum #1 & Boulder - Rathdrum 115 (AVA) | OPEN Bus PLEASANT_115.0 (48319) |  | CHECK |
| L_Taft - Hot Springs 500 kV (BPA) | OPEN Branch HOT SPR_500.0 (40553) TO TAFT_500.0 (41057) CKT 1 |  | CHECK |
| L_Taft - Hot Springs 500 kV (BPA) | OPEN Shunt GARRISON_500.0 (40459) #r |  | CHECK |
| L_Taft - Hot Springs 500 kV (BPA) | OPEN Bus LIB PH1_230.0 (44200) | West MT Hydro > 1000 | CHECK |
| L_Taft - Hot Springs 500 kV (BPA) | OPEN Bus LIB PH2_230.0 (44201) | West MT Hydro > 1000 | CHECK |
| L_Westside - Bell & Westside - Coulee 230 (AVA/BPA) | OPEN Bus WESTBPA2_230.0 (41276) |  | CHECK |
| L_Westside - Bell & Westside - Coulee 230 (AVA/BPA) | OPEN Bus WESTBPA1_230.0 (41275) |  | CHECK |
| L_Westside - Coulee & Bell - Coulee #3 230 (AVA/BPA) | OPEN Bus WESTBPA2_230.0 (41276) |  | CHECK |
| L_Westside - Coulee & Bell - Coulee #3 230 (AVA/BPA) | OPEN MultiSectionLine BELL S3_230.0 (40090) TO COULEES1_230.0 (41356) CKT 3 |  | CHECK |
| L_Westside - Waste to Energy & Westside - Ft Wright 115 (AVA) | OPEN Branch FTWRIGHT_115.0 (48129) TO WEST_115.0 (48461) CKT 1 |  | CHECK |
| L_Westside - Waste to Energy & Westside - Ft Wright 115 (AVA) | OPEN Branch SPKWASTE_115.0 (48409) TO WEST_115.0 (48461) CKT 1 |  | CHECK |
| T_40017ADDY-48007ADDYAVAC1 | OPEN Branch ADDY_115.0 (40017) TO ADDY AVA_ 23.0 (48007) CKT 1 |  | CHECK |
| T_40021ADDY2-40017ADDYC1 | OPEN Branch ADDY 2_230.0 (40021) TO ADDY_115.0 (40017) CKT 1 |  | CHECK |
| T_40088BELLS2-40087BELLBPAC1 | OPEN Branch BELL S2_230.0 (40088) TO BELL BPA_115.0 (40087) CKT 1 |  | CHECK |
| T_40091BELLBPA-40092BELLS4C1 | OPEN Branch BELL BPA_500.0 (40091) TO BELL S4_230.0 (40092) CKT 1 |  | CHECK |
| T_40909SACHEEN-40907SACHEENC1 | OPEN Branch SACHEEN_230.0 (40909) TO SACHEEN_115.0 (40907) CKT 1 |  | CHECK |
| T_41298SMITHFLS-41299SMITHFLSC1 | OPEN Branch SMITHFLS_ 13.8 (41298) TO SMITHFLS_115.0 (41299) CKT 1 |  | CHECK |
| T_45097DRYGULCH-48113DRYGULCHC1 | OPEN Branch DRYGULCH_ 69.0 (45097) TO DRYGULCH_115.0 (48113) CKT 1 |  | CHECK |
| T_46447SUMERFAL-46653SUMERFA1C1 | OPEN Branch SUMERFAL_115.0 (46447) TO SUMERFA1_ 13.8 (46653) CKT 1 |  | CHECK |
| T_46447SUMERFAL-46655SUMERFA2C1 | OPEN Branch SUMERFAL_115.0 (46447) TO SUMERFA2_ 13.8 (46655) CKT 1 |  | CHECK |
| T_46619HEADWORK-48149HEADWORKC1 | OPEN Branch HEADWORK_ 13.8 (46619) TO HEADWORK_115.0 (48149) CKT 1 |  | CHECK |
| T_47010BOXCAN1-47009BOXCANYC1 | OPEN Branch BOX CAN1_ 13.2 (47010) TO BOX CANY_115.0 (47009) CKT 1 |  | CHECK |
| T_47012BOXCAN2-47009BOXCANYC1 | OPEN Branch BOX CAN2_ 13.2 (47012) TO BOX CANY_115.0 (47009) CKT 1 |  | CHECK |
| T_47014BOXCAN3-47009BOXCANYC1 | OPEN Branch BOX CAN3_ 13.2 (47014) TO BOX CANY_115.0 (47009) CKT 1 |  | CHECK |
| T_47016BOXCAN4-47009BOXCANYC1 | OPEN Branch BOX CAN4_ 13.2 (47016) TO BOX CANY_115.0 (47009) CKT 1 |  | CHECK |
| T_47126BOXPS-47009BOXCANYC1 | OPEN Branch BOX PS_115.0 (47126) TO BOX CANY_115.0 (47009) CKT 1 |  | CHECK |
| T_47254USK-47091USKC1 | OPEN Branch USK_115.0 (47254) TO USK_230.0 (47091) CKT 1 |  | CHECK |
| T_47568LANCASG-40624LANCASTRC1 | OPEN Branch LANCAS G_ 18.0 (47568) TO LANCASTR_230.0 (40624) CKT 1 |  | CHECK |
| T_47569LANCASS-40624LANCASTRC1 | OPEN Branch LANCAS S_ 13.8 (47569) TO LANCASTR_230.0 (40624) CKT 1 |  | CHECK |
| T_48025BEACONN-48023BEACONNC1 | OPEN Branch BEACON N_230.0 (48025) TO BEACON N_115.0 (48023) CKT 1 |  | CHECK |
| T_48027BEACONS-48029BEACONSC1 | OPEN Branch BEACON S_ 13.8 (48027) TO BEACON S_115.0 (48029) CKT 1 |  | CHECK |
| T_48031BEACONS-48029BEACONSC1 | OPEN Branch BEACON S_230.0 (48031) TO BEACON S_115.0 (48029) CKT 1 |  | CHECK |
| T_48037BENEWAH-48035BENEWAHC1 | OPEN Branch BENEWAH_230.0 (48037) TO BENEWAH_115.0 (48035) CKT 1 |  | CHECK |
| T_48059CABGORG-48057CABGORGC1 | OPEN Branch CAB GORG_230.0 (48059) TO CAB GORG_115.0 (48057) CKT 1 |  | CHECK |
| T_48059CABGORG-48061CABGOR12C1 | OPEN Branch CAB GORG_230.0 (48059) TO CABGOR12_ 13.8 (48061) CKT 1 |  | CHECK |
| T_48059CABGORG-48063CABGOR34C1 | OPEN Branch CAB GORG_230.0 (48059) TO CABGOR34_ 13.8 (48063) CKT 1 |  | CHECK |
| T_48075CLEARWTR-48476CLWTR2C1 | OPEN Branch CLEARWTR_115.0 (48075) TO CLWTR2_ 34.5 (48476) CKT 1 |  | CHECK |
| T_48075CLEARWTR-48481CLWTR7C1 | OPEN Branch CLEARWTR_115.0 (48075) TO CLWTR7_ 34.5 (48481) CKT 1 |  | CHECK |
| T_48083COLVAVA-48085COLVILLEC1 | OPEN Branch COLV AVA_115.0 (48083) TO COLVILLE_ 13.8 (48085) CKT 1 |  | CHECK |
| T_48085COLVILLE-48439VAAGENC1 | OPEN Branch COLVILLE_ 13.8 (48085) TO VAAGEN_ 4.2 (48439) CKT 1 |  | CHECK |
| T_48143GREENWDA-48229MEYERSFLC1 | OPEN Branch GREENWDA_115.0 (48143) TO MEYERSFL_ 13.0 (48229) CKT 1 |  | CHECK |
| T_48173KETTLEAV-48175KETTLEAVC1 | OPEN Branch KETTLEAV_ 13.8 (48173) TO KETTLEAV_115.0 (48175) CKT 1 |  | CHECK |
| T_48189LITFAL12-48193LITTFALLC1 | OPEN Branch LITFAL12_ 4.0 (48189) TO LITTFALL_115.0 (48193) CKT 1 |  | CHECK |
| T_48191LITFAL34-48193LITTFALLC1 | OPEN Branch LITFAL34_ 4.0 (48191) TO LITTFALL_115.0 (48193) CKT 1 |  | CHECK |
| T_48197LOLO-48195LOLOC1 | OPEN Branch LOLO_230.0 (48197) TO LOLO_115.0 (48195) CKT 1 |  | CHECK |
| T_48197LOLO-48195LOLOC2 | OPEN Branch LOLO_230.0 (48197) TO LOLO_115.0 (48195) CKT 2 |  | CHECK |
| T_48199LONGLAKA-48205LONGLKG1C1 | OPEN Branch LONGLAKA_115.0 (48199) TO LONGLKG1_ 4.0 (48205) CKT 1 |  | CHECK |
| T_48199LONGLAKA-48207LONGLKG2C1 | OPEN Branch LONGLAKA_115.0 (48199) TO LONGLKG2_ 4.0 (48207) CKT 1 |  | CHECK |
| T_48201LONGLAKB-48209LONGLKG3C1 | OPEN Branch LONGLAKB_115.0 (48201) TO LONGLKG3_ 4.0 (48209) CKT 1 |  | CHECK |
| T_48201LONGLAKB-48211LONGLKG4C1 | OPEN Branch LONGLAKB_115.0 (48201) TO LONGLKG4_ 4.0 (48211) CKT 1 |  | CHECK |
| T_48227MEYERSFL-48229MEYERSFLC1 | OPEN Branch MEYERSFL_ 11.0 (48227) TO MEYERSFL_ 13.0 (48229) CKT 1 |  | CHECK |
| T_48241MONROEA-48337POSTSTRTC1 | OPEN Branch MONROEA_ 13.8 (48241) TO POSTSTRT_ 13.8 (48337) CKT 1 |  | CHECK |
| T_48249MOSCOW-48251MOSCOWXC1 | OPEN Branch MOSCOW_230.0 (48249) TO MOSCOWX_115.0 (48251) CKT 1 |  | CHECK |
| T_48251MOSCOWX-48247MOSCOWC1 | OPEN Branch MOSCOWX_115.0 (48251) TO MOSCOW_115.0 (48247) CKT 1 |  | CHECK |
| T_48255NLEWIST-48253NLEWISTC1 | OPEN Branch N LEWIST_230.0 (48255) TO N LEWIST_115.0 (48253) CKT 1 |  | CHECK |
| T_48263NINEFLSE-48265NINEMI12C1 | OPEN Branch NINEFLSE_ 30.0 (48263) TO NINEMI12_ 2.3 (48265) CKT 1 |  | CHECK |
| T_48263NINEFLSE-48269NINEMILEC1 | OPEN Branch NINEFLSE_ 30.0 (48263) TO NINEMILE_115.0 (48269) CKT 1 |  | CHECK |
| T_48267NINEMI34-48269NINEMILEC1 | OPEN Branch NINEMI34_ 13.8 (48267) TO NINEMILE_115.0 (48269) CKT 1 |  | CHECK |
| T_48275NORTHEAS-48277NORTHEASC1 | OPEN Branch NORTHEAS_ 13.8 (48275) TO NORTHEAS_115.0 (48277) CKT 1 |  | CHECK |
| T_48281NOXON-48283NOXON5C1 | OPEN Branch NOXON_230.0 (48281) TO NOXON 5_ 14.4 (48283) CKT 1 |  | CHECK |
| T_48281NOXON-48285NOXON12C1 | OPEN Branch NOXON_230.0 (48281) TO NOXON12_ 14.4 (48285) CKT 1 |  | CHECK |
| T_48287NOXON34-40787NOXONBPAC1 | OPEN Branch NOXON34_ 14.4 (48287) TO NOXONBPA_230.0 (40787) CKT 1 |  | CHECK |
| T_48317PINECRK-48315PINECRKC1 | OPEN Branch PINE CRK_230.0 (48317) TO PINE CRK_115.0 (48315) CKT 1 |  | CHECK |
| T_48317PINECRK-48315PINECRKC2 | OPEN Branch PINE CRK_230.0 (48317) TO PINE CRK_115.0 (48315) CKT 2 |  | CHECK |
| T_48321PLUMMER-48325PLUMMERGC1 | OPEN Branch PLUMMER_ 4.2 (48321) TO PLUMMERG_ 13.8 (48325) CKT 1 |  | CHECK |
| T_48323PLUMMER-48327PLUMMWEAC1 | OPEN Branch PLUMMER_115.0 (48323) TO PLUMMWEA_ 13.8 (48327) CKT 1 |  | CHECK |
| T_48329POSTFLS-48331POSTFL15C1 | OPEN Branch POST FLS_115.0 (48329) TO POSTFL15_ 2.4 (48331) CKT 1 |  | CHECK |
| T_48329POSTFLS-48333POSTFLS6C1 | OPEN Branch POST FLS_115.0 (48329) TO POSTFLS6_ 2.4 (48333) CKT 1 |  | CHECK |
| T_48335POSTSTRT-48337POSTSTRTC4 | OPEN Branch POSTSTRT_ 4.2 (48335) TO POSTSTRT_ 13.8 (48337) CKT 4 |  | CHECK |
| T_48337POSTSTRT-48339POSTSTRTC1 | OPEN Branch POSTSTRT_ 13.8 (48337) TO POSTSTRT_115.0 (48339) CKT 1 |  | CHECK |
| T_48337POSTSTRT-48339POSTSTRTC2 | OPEN Branch POSTSTRT_ 13.8 (48337) TO POSTSTRT_115.0 (48339) CKT 2 |  | CHECK |
| T_48351RATHBUS1-48359RATHGEN1C1 | OPEN Branch RATHBUS1_115.0 (48351) TO RATHGEN1_ 13.8 (48359) CKT 1 |  | CHECK |
| T_48353RATHBUS2-48361RATHGEN2C1 | OPEN Branch RATHBUS2_115.0 (48353) TO RATHGEN2_ 13.8 (48361) CKT 1 |  | CHECK |
| T_48357RATHDRUM-48355RATHDRUMC1 | OPEN Branch RATHDRUM_230.0 (48357) TO RATHDRUM_115.0 (48355) CKT 1 |  | CHECK |
| T_48357RATHDRUM-48356RATHDRMEC1 | OPEN Branch RATHDRUM_230.0 (48357) TO RATHDRME_115.0 (48356) CKT 1 |  | CHECK |
| T_48385SHAWNEE-48383SHAWNEEC1 | OPEN Branch SHAWNEE_230.0 (48385) TO SHAWNEE_115.0 (48383) CKT 1 |  | CHECK |
| T_48407SPKWASTE-48409SPKWASTEC1 | OPEN Branch SPKWASTE_ 13.8 (48407) TO SPKWASTE_115.0 (48409) CKT 1 |  | CHECK |
| T_48433UPRIVER-48437UPRIVERC1 | OPEN Branch UPRIVER_ 2.4 (48433) TO UPRIVER_ 13.8 (48437) CKT 1 |  | CHECK |
| T_48435UPRIVER-48437UPRIVERC1 | OPEN Branch UPRIVER_ 4.2 (48435) TO UPRIVER_ 13.8 (48437) CKT 1 |  | CHECK |
| T_48463WEST-48461WESTC1 | OPEN Branch WEST_230.0 (48463) TO WEST_115.0 (48461) CKT 1 |  | CHECK |
| T_48463WEST-48461WESTC2 | OPEN Branch WEST_230.0 (48463) TO WEST_115.0 (48461) CKT 2 |  | CHECK |
| T_48475CLWTR1-48484CWTW1C1 | OPEN Branch CLWTR1_ 34.5 (48475) TO CWTW1_ 12.0 (48484) CKT 1 |  | CHECK |
| T_48475CLWTR1-48487CWTW4C1 | OPEN Branch CLWTR1_ 34.5 (48475) TO CWTW4_ 12.0 (48487) CKT 1 |  | CHECK |
| T_48477CLWTR3-48485CWTW2C1 | OPEN Branch CLWTR3_ 34.5 (48477) TO CWTW2_ 12.0 (48485) CKT 1 |  | CHECK |
| T_48478CLWTR4-48482CWGEN3C1 | OPEN Branch CLWTR4_ 34.5 (48478) TO CWGEN3_ 12.0 (48482) CKT 1 |  | CHECK |
| T_48479CLWTR5-48486CWTW3C1 | OPEN Branch CLWTR5_ 34.5 (48479) TO CWTW3_ 12.0 (48486) CKT 1 |  | CHECK |
| T_48479CLWTR5-48488CWTW5C1 | OPEN Branch CLWTR5_ 34.5 (48479) TO CWTW5_ 12.0 (48488) CKT 1 |  | CHECK |
| T_48480CLWTR6-48483CWGEN4C1 | OPEN Branch CLWTR6_ 34.5 (48480) TO CWGEN4_ 12.0 (48483) CKT 1 |  | CHECK |
| T_48481CLWTR7-48489CWTW6C1 | OPEN Branch CLWTR7_ 34.5 (48481) TO CWTW6_ 12.0 (48489) CKT 1 |  | CHECK |
| T_48484CWTW1-48490CWBUS1C1 | OPEN Branch CWTW1_ 12.0 (48484) TO CWBUS1_ 12.0 (48490) CKT 1 |  | CHECK |
| T_48484CWTW1-48493CWBUS4C1 | OPEN Branch CWTW1_ 12.0 (48484) TO CWBUS4_ 12.0 (48493) CKT 1 |  | CHECK |
| T_48485CWTW2-48492CWBUS3C1 | OPEN Branch CWTW2_ 12.0 (48485) TO CWBUS3_ 12.0 (48492) CKT 1 |  | CHECK |
| T_48485CWTW2-48493CWBUS4C1 | OPEN Branch CWTW2_ 12.0 (48485) TO CWBUS4_ 12.0 (48493) CKT 1 |  | CHECK |
| T_48486CWTW3-48491CWBUS2C1 | OPEN Branch CWTW3_ 12.0 (48486) TO CWBUS2_ 12.0 (48491) CKT 1 |  | CHECK |
| T_48486CWTW3-48492CWBUS3C1 | OPEN Branch CWTW3_ 12.0 (48486) TO CWBUS3_ 12.0 (48492) CKT 1 |  | CHECK |
| T_48487CWTW4-48495CWBUS6C1 | OPEN Branch CWTW4_ 12.0 (48487) TO CWBUS6_ 12.0 (48495) CKT 1 |  | CHECK |
| T_48487CWTW4-48496CWBUS7C1 | OPEN Branch CWTW4_ 12.0 (48487) TO CWBUS7_ 12.0 (48496) CKT 1 |  | CHECK |
| T_48488CWTW5-48495CWBUS6C1 | OPEN Branch CWTW5_ 12.0 (48488) TO CWBUS6_ 12.0 (48495) CKT 1 |  | CHECK |
| T_48488CWTW5-48496CWBUS7C1 | OPEN Branch CWTW5_ 12.0 (48488) TO CWBUS7_ 12.0 (48496) CKT 1 |  | CHECK |
| T_48489CWTW6-48494CWBUS5C1 | OPEN Branch CWTW6_ 12.0 (48489) TO CWBUS5_ 12.0 (48494) CKT 1 |  | CHECK |
| T_48489CWTW6-48497CWBUS8C1 | OPEN Branch CWTW6_ 12.0 (48489) TO CWBUS8_ 12.0 (48497) CKT 1 |  | CHECK |
| T_48510DRYCREEK-48512DRYCREEKC1 | OPEN Branch DRYCREEK_230.0 (48512) TO DRYCREEK_115.0 (48510) CKT 1 |  | CHECK |
| T_48524BOULDER-48520BOULDERWC1 | OPEN Branch BOULDER_230.0 (48524) TO BOULDERW_115.0 (48520) CKT 1 |  | CHECK |
| T_48524BOULDER-48522BOULDEREC2 | OPEN Branch BOULDER_230.0 (48524) TO BOULDERE_115.0 (48522) CKT 2 |  | CHECK |
| T_48526BOULDERG-48522BOULDEREC1 | OPEN Branch BOULDERG_ 13.8 (48526) TO BOULDERE_115.0 (48522) CKT 1 |  | CHECK |
| T_Hatwai 500/230 Xfmr (BPA) | OPEN Branch HATWAI_500.0 (40521) TO HATWAI_230.0 (40519) CKT 1 |  | CHECK |
| Contingency Name | Actions | Model Criteria | Status | Comment |
| B_40017ADDY | OPEN Bus ADDY_115.0 (40017) |  | CHECK |  |
| B_40019ADDY | OPEN Bus ADDY_230.0 (40019) |  | CHECK |  |
| B_40021ADDY 2&1 | OPEN Bus ADDY 2_230.0 (40021) |  | CHECK |  |
| B_40021ADDY2 | OPEN Bus ADDY 2_230.0 (40021) |  | CHECK |  |
| B_40021ADDY2 | OPEN Gen BOUNDG55_ 14.4 (46472) #55 | South of Boundary > 650 | CHECK |  |
| B_40021ADDY2 | OPEN Gen BOUNDG56_ 14.4 (46474) #56 | South of Boundary > 650 | CHECK |  |
| B_40023AHSAHKA | OPEN Bus AHSAHKA_115.0 (40023) |  | CHECK |  |
| B_40029ALBENIF | OPEN Bus ALBENI F_115.0 (40029) |  | CHECK |  |
| B_40067ATHOL | OPEN Bus ATHOL_115.0 (40067) |  | CHECK |  |
| B_40086BELLS1 | OPEN Bus BELL S1_230.0 (40086) |  | CHECK |  |
| B_40086BELLS1 | OPEN Gen BOUNDG55_ 14.4 (46472) #55 | South of Boundary > 650 | CHECK |  |
| B_40086BELLS1 | OPEN Gen BOUNDG56_ 14.4 (46474) #56 | South of Boundary > 650 | CHECK |  |
| B_40087BELLBPA | OPEN Bus BELL BPA_115.0 (40087) |  | CHECK |  |
| B_40088BELLS2 | OPEN Bus BELL S2_230.0 (40088) |  | CHECK |  |
| B_40088BELLS2 | OPEN Gen BOUNDG55_ 14.4 (46472) #55 | South of Boundary > 650 | CHECK |  |
| B_40088BELLS2 | OPEN Gen BOUNDG56_ 14.4 (46474) #56 | South of Boundary > 650 | CHECK |  |
| B_40090BELLS3 | OPEN Bus BELL S3_230.0 (40090) |  | CHECK |  |
| B_40090BELLS3 | OPEN Gen LANCAS G_ 18.0 (47568) #1 |  | ALWAYS |  |
| B_40090BELLS3 | OPEN Gen LANCAS S_ 13.8 (47569) #1 |  | ALWAYS |  |
| B_40090BELLS3 | OPEN Gen BOUNDG55_ 14.4 (46472) #55 | South of Boundary > 650 | CHECK |  |
| B_40090BELLS3 | OPEN Gen BOUNDG56_ 14.4 (46474) #56 | South of Boundary > 650 | CHECK |  |
| B_40091BELLBPA | OPEN Shunt GARRISON_500.0 (40459) #r |  | ALWAYS |  |
| B_40091BELLBPA | OPEN Bus BELL BPA_500.0 (40091) |  | ALWAYS |  |
| B_40091BELLBPA | OPEN Load MILCTYDC_230.0 (63010) #D1 |  | ALWAYS |  |
| B_40091BELLBPA | OPEN Bus LIB PH1_230.0 (44200) | West MT Hydro > 1000 | CHECK |  |
| B_40091BELLBPA | OPEN Bus LIB PH2_230.0 (44201) | West MT Hydro > 1000 | CHECK |  |
| B_40091BELLBPA | OPEN Gen LANCAS S_ 13.8 (47569) #1 | WEST OF HATWAI > 3500 | CHECK |  |
| B_40091BELLBPA | OPEN Gen LANCAS G_ 18.0 (47568) #1 | WEST OF HATWAI > 3500 | CHECK |  |
| B_40092BELLS4 | OPEN Bus BELL S4_230.0 (40092) |  | CHECK |  |
| B_40094ADDBEL11 | OPEN Bus ADDBEL11_230.0 (40094) |  | CHECK |  |
| B_40094ADDBEL11 | OPEN Gen BOUNDG55_ 14.4 (46472) #55 | South of Boundary > 650 | CHECK |  |
| B_40094ADDBEL11 | OPEN Gen BOUNDG56_ 14.4 (46474) #56 | South of Boundary > 650 | CHECK |  |
| B_40096BELLSC | OPEN Bus BELL SC_500.0 (40096) |  | CHECK |  |
| B_40096BELLSC | OPEN Shunt GARRISON_500.0 (40459) #r |  | ALWAYS |  |
| B_40096BELLSC | OPEN Load MILCTYDC_230.0 (63010) #D1 |  | ALWAYS |  |
| B_40096BELLSC | OPEN Bus LIB PH1_230.0 (44200) | West MT Hydro > 1000 | CHECK |  |
| B_40096BELLSC | OPEN Bus LIB PH2_230.0 (44201) | West MT Hydro > 1000 | CHECK |  |
| B_40113BIGELOW | OPEN Bus BIGELOW_115.0 (40113) |  | CHECK |  |
| B_40133BONNERS | OPEN Bus BONNERS_115.0 (40133) |  | CHECK |  |
| B_40145BOUNDARY | OPEN Bus BOUNDARY_230.0 (40145) |  | CHECK |  |
| B_40145BOUNDARY | OPEN Gen BOUNDG55_ 14.4 (46472) #55 | SoB>650 | CHECK |  |
| B_40145BOUNDARY | OPEN Gen BOUNDG56_ 14.4 (46474) #56 | SoB>650 | CHECK |  |
| B_40145BOUNDARY | OPEN Gen BOUNDG54_ 14.4 (46470) #54 | SoB>650 | CHECK |  |
| B_40145BOUNDARY | OPEN Gen BOUNDG53_ 14.4 (46468) #53 | SoB>650 | CHECK |  |
| B_40145BOUNDARY | SET GENERATION AT BUS BOUNDG52_ 14.4 (46466) TO 100 MW | SoB>650 | CHECK |  |
| B_40149BRINKENS | OPEN Bus BRINKENS_115.0 (40149) |  | CHECK |  |
| B_40215CHENEY | OPEN Bus CHENEY_115.0 (40215) |  | CHECK |  |
| B_40239CLARKSTN | OPEN Bus CLARKSTN_115.0 (40239) |  | CHECK |  |
| B_40245CLAYTON | OPEN Bus CLAYTON_115.0 (40245) |  | CHECK |  |
| B_40255COLBERTT | OPEN Bus COLBERTT_115.0 (40255) |  | CHECK |  |
| B_40263COLVBPA | OPEN Bus COLV BPA_115.0 (40263) |  | CHECK |  |
| B_40275COOKMT | OPEN Bus COOK M T_115.0 (40275) |  | CHECK |  |
| B_40311CRESTN | OPEN Bus CRESTN_115.0 (40311) |  | CHECK |  |
| B_40317CUSICK | OPEN Bus CUSICK_115.0 (40317) |  | CHECK |  |
| B_40319CUSICK | OPEN Bus CUSICK_230.0 (40319) |  | CHECK |  |
| B_40337DEERPRK | OPEN Bus DEER PRK_115.0 (40337) |  | CHECK |  |
| B_40383EGRANVIL | OPEN Bus EGRANVIL_115.0 (40383) |  | CHECK |  |
| B_40384EGYPTTP | OPEN Bus EGYPT TP_115.0 (40384) |  | CHECK |  |
| B_40397FAIRCHLD | OPEN Bus FAIRCHLD_115.0 (40397) |  | CHECK |  |
| B_40439FOURLKS | OPEN Bus FOURLKS_115.0 (40439) |  | CHECK |  |
| B_40449GAFFNEY | OPEN Bus GAFFNEY_115.0 (40449) |  | CHECK |  |
| B_40483GREENBL | OPEN Bus GREEN BL_115.0 (40483) |  | CHECK |  |
| B_40495HALFMOON | OPEN Bus HALFMOON_115.0 (40495) |  | CHECK |  |
| B_40525HAYFORD | OPEN Bus HAYFORD_115.0 (40525) |  | CHECK |  |
| B_40577IRBY | OPEN Bus IRBY_115.0 (40577) |  | CHECK |  |
| B_40607KETTLET | OPEN Bus KETTLE T_115.0 (40607) |  | CHECK |  |
| B_40617LACLEDE | OPEN Bus LACLEDE_115.0 (40617) |  | CHECK |  |
| B_40624LANCASTR | OPEN Bus LANCASTR_230.0 (40624) |  | CHECK |  |
| B_40624LANCASTR | OPEN Gen LANCAS G_ 18.0 (47568) #1 |  | CHECK |  |
| B_40624LANCASTR | OPEN Gen LANCAS S_ 13.8 (47569) #1 |  | CHECK |  |
| B_40624LANCASTR | OPEN Bus LIB PH2_230.0 (44201) |  | CHECK |  |
| B_40730MEADTAP | OPEN Bus MEAD TAP_115.0 (40730) |  | CHECK |  |
| B_40731METALINE | OPEN Bus METALINE_115.0 (40731) |  | CHECK |  |
| B_40732METLNTAP | OPEN Bus METLNTAP_115.0 (40732) |  | CHECK |  |
| B_40779NEWPORTB | OPEN Bus NEWPORTB_115.0 (40779) |  | CHECK |  |
| B_40787NOXONBPA | OPEN Bus NOXONBPA_230.0 (40787) |  | CHECK |  |
| B_40787NOXONBPA | OPEN Bus LIB PH2_230.0 (44201) |  | CHECK |  |
| B_40855PRAIRIEB | OPEN Bus PRAIRIEB_115.0 (40855) |  | CHECK |  |
| B_40857PRIEST | OPEN Bus PRIEST_115.0 (40857) |  | CHECK |  |
| B_40879REPUBLIC | OPEN Bus REPUBLIC_115.0 (40879) |  | CHECK |  |
| B_40907SACHEEN | OPEN Bus SACHEEN_115.0 (40907) |  | CHECK |  |
| B_40909SACHEEN | OPEN Bus SACHEEN_230.0 (40909) |  | CHECK |  |
| B_40927SAMUEL &1 | OPEN Bus SAMUELS_115.0 (40927) |  | CHECK |  |
| B_40927SAMUELS | OPEN Bus SAMUELS_115.0 (40927) |  | CHECK |  |
| B_40928BONSAM11 | OPEN Bus BONSAM11_115.0 (40928) |  | CHECK |  |
| B_40929SANDCRK | OPEN Bus SAND CRK_115.0 (40929) |  | CHECK |  |
| B_40930BONSAM12 | OPEN Bus BONSAM12_115.0 (40930) |  | CHECK |  |
| B_40930SAMUEL &2 | OPEN Bus BONSAM12_115.0 (40930) |  | CHECK |  |
| B_40931SANDTP | OPEN Bus SAND TP_115.0 (40931) |  | CHECK |  |
| B_40933SANDPONT | OPEN Bus SANDPONT_115.0 (40933) |  | CHECK |  |
| B_40934SAND C&1 | OPEN Bus SANSAN11_115.0 (40934) |  | CHECK |  |
| B_40934SANSAN11 | OPEN Bus SANSAN11_115.0 (40934) |  | CHECK |  |
| B_40953SCARCELO | OPEN Bus SCARCELO_115.0 (40953) |  | CHECK |  |
| B_40965SELLE | OPEN Bus SELLE_115.0 (40965) |  | CHECK |  |
| B_41015SPRNGHIL | OPEN Bus SPRNGHIL_115.0 (41015) |  | CHECK |  |
| B_41089TRENTWOD | OPEN Bus TRENTWOD_115.0 (41089) |  | CHECK |  |
| B_41091TROUTCR | OPEN Bus TROUT CR_230.0 (41091) |  | CHECK |  |
| B_41097TROY | OPEN Bus TROY_115.0 (41097) |  | CHECK |  |
| B_41099TUMTUM | OPEN Bus TUM TUM_115.0 (41099) |  | CHECK |  |
| B_41107VALYWAY | OPEN Bus VALY WAY_115.0 (41107) |  | CHECK |  |
| B_41115VERA | OPEN Bus VERA_115.0 (41115) |  | CHECK |  |
| B_41117VERATAP | OPEN Bus VERA TAP_115.0 (41117) |  | CHECK |  |
| B_41125WAGNERLK | OPEN Bus WAGNERLK_115.0 (41125) |  | CHECK |  |
| B_41127WAGNERLT | OPEN Bus WAGNERLT_115.0 (41127) |  | CHECK |  |
| B_41169YAAK | OPEN Bus YAAK_115.0 (41169) |  | CHECK |  |
| B_41190BOXTAP | OPEN Bus BOX TAP_115.0 (41190) |  | CHECK |  |
| B_41239MOYIET | OPEN Bus MOYIE T_115.0 (41239) |  | CHECK |  |
| B_41240MOYIETX | OPEN Bus MOYIE TX_115.0 (41240) |  | CHECK |  |
| B_41241NBENCH | OPEN Bus N BENCH_115.0 (41241) |  | CHECK |  |
| B_41260SULLIVNB | OPEN Bus SULLIVNB_115.0 (41260) |  | CHECK |  |
| B_41275WESTBPA1 | OPEN Bus WESTBPA1_230.0 (41275) |  | CHECK |  |
| B_41276WESTBPA2 | OPEN Bus WESTBPA2_230.0 (41276) |  | CHECK |  |
| B_41298SMITHFLS | OPEN Bus SMITHFLS_ 13.8 (41298) |  | CHECK |  |
| B_41299SMITHFLS | OPEN Bus SMITHFLS_115.0 (41299) |  | CHECK |  |
| B_46151LARSON 230 | OPEN Bus LARSON_230.0 (46151) |  | CHECK |  |
| B_46156ROCKYFD 230 | OPEN Bus ROCKYFD_230.0 (46156) |  | CHECK |  |
| B_46619HEADWORK | OPEN Bus HEADWORK_ 13.8 (46619) |  | CHECK |  |
| B_46653SUMERFA1 | OPEN Bus SUMERFA1_ 13.8 (46653) |  | CHECK |  |
| B_46655SUMERFA2 | OPEN Bus SUMERFA2_ 13.8 (46655) |  | CHECK |  |
| B_47009BOXCANY | OPEN Bus BOX CANY_115.0 (47009) |  | CHECK |  |
| B_47010BOXCAN1 | OPEN Bus BOX CAN1_ 13.2 (47010) |  | CHECK |  |
| B_47012BOXCAN2 | OPEN Bus BOX CAN2_ 13.2 (47012) |  | CHECK |  |
| B_47014BOXCAN3 | OPEN Bus BOX CAN3_ 13.2 (47014) |  | CHECK |  |
| B_47016BOXCAN4 | OPEN Bus BOX CAN4_ 13.2 (47016) |  | CHECK |  |
| B_47025DELIGHT | OPEN Bus DELIGHT_115.0 (47025) |  | CHECK |  |
| B_47027DIAMLAK | OPEN Bus DIAM LAK_115.0 (47027) |  | CHECK |  |
| B_47033DOWERRD | OPEN Bus DOWER RD_115.0 (47033) |  | CHECK |  |
| B_47038EGYPT | OPEN Bus EGYPT_115.0 (47038) |  | CHECK |  |
| B_47073RALSTONB | OPEN Bus RALSTONB_115.0 (47073) |  | CHECK |  |
| B_47086PINEST | OPEN Bus PINE ST_115.0 (47086) |  | CHECK |  |
| B_47091USK | OPEN Bus USK_230.0 (47091) |  | CHECK |  |
| B_47126BOXPS | OPEN Bus BOX PS_115.0 (47126) |  | CHECK |  |
| B_47194MTHALL | OPEN Bus MT HALL_115.0 (47194) |  | CHECK |  |
| B_47254USK | OPEN Bus USK_115.0 (47254) |  | CHECK |  |
| B_47501ARMSTRNG | OPEN Bus ARMSTRNG_115.0 (47501) |  | CHECK |  |
| B_47503CHAMBERS | OPEN Bus CHAMBERS_115.0 (47503) |  | CHECK |  |
| B_47505HOODOO | OPEN Bus HOODOO_115.0 (47505) |  | CHECK |  |
| B_47507HOPKINSB | OPEN Bus HOPKINSB_115.0 (47507) |  | CHECK |  |
| B_47509MICA | OPEN Bus MICA_115.0 (47509) |  | CHECK |  |
| B_47511MOAB | OPEN Bus MOAB_115.0 (47511) |  | CHECK |  |
| B_47513W.PLAINS | OPEN Bus W.PLAINS_115.0 (47513) |  | CHECK |  |
| B_47568LANCASG | OPEN Bus LANCAS G_ 18.0 (47568) |  | CHECK |  |
| B_47569LANCASS | OPEN Bus LANCAS S_ 13.8 (47569) |  | CHECK |  |
| B_480014LAKETP | OPEN Bus 4LAKE TP_115.0 (48001) |  | CHECK |  |
| B_48003NELSONSB | OPEN Bus NELSONSB_115.0 (48003) |  | CHECK |  |
| B_48005NELSONTP | OPEN Bus NELSONT_115.0 (48005) |  | CHECK |  |
| B_48007ADDYAVA | OPEN Bus ADDY AVA_ 23.0 (48007) |  | CHECK |  |
| B_48009AIRWAYHT | OPEN Bus AIRWAYHT_115.0 (48009) |  | CHECK |  |
| B_48011APPLETAP | OPEN Bus APPLETAP_115.0 (48011) |  | CHECK |  |
| B_48013APPLEWAY | OPEN Bus APPLEWAY_115.0 (48013) |  | CHECK |  |
| B_48015ARDEN | OPEN Bus ARDEN_115.0 (48015) |  | CHECK |  |
| B_48017ATHOLTAP | OPEN Bus ATHOLTAP_115.0 (48017) |  | CHECK |  |
| B_48019AVONDALE | OPEN Bus AVONDALE_115.0 (48019) |  | CHECK |  |
| B_48021BARKER | OPEN Bus BARKER_115.0 (48021) |  | CHECK |  |
| B_48023BEACONN | OPEN Bus BEACON N_115.0 (48023) |  | CHECK |  |
| B_48025BEACONN | OPEN Bus BEACON N_230.0 (48025) |  | CHECK |  |
| B_48027BEACONS | OPEN Bus BEACON S_ 13.8 (48027) |  | CHECK |  |
| B_48029BEACONS | OPEN Bus BEACON S_115.0 (48029) |  | CHECK |  |
| B_48031BEACONS | OPEN Bus BEACON S_230.0 (48031) |  | CHECK |  |
| B_48033BELLTAP | OPEN Bus BELL TAP_115.0 (48033) |  | CHECK |  |
| B_48035BENEWAH | OPEN Bus BENEWAH_115.0 (48035) |  | CHECK |  |
| B_48037BENEWAH | OPEN Bus BENEWAH_230.0 (48037) |  | CHECK |  |
| B_48037BENEWAH | OPEN Gen NOXON34_ 14.4 (48287) #3 |  | CHECK |  |
| B_48037BENEWAH | OPEN Gen NOXON34_ 14.4 (48287) #4 |  | CHECK |  |
| B_48039BENTNAVA | OPEN Bus BENTNAVA_115.0 (48039) |  | CHECK |  |
| B_48041BIGCREEK | OPEN Bus BIGCREEK_115.0 (48041) |  | CHECK |  |
| B_48043BLANCHRD | OPEN Bus BLANCHRD_115.0 (48043) |  | CHECK |  |
| B_48045BLUECRK | OPEN Bus BLUECRK_115.0 (48045) |  | CHECK |  |
| B_48047BRONX | OPEN Bus BRONX_115.0 (48047) |  | CHECK |  |
| B_48049BUNKRHIL | OPEN Bus BUNKRHIL_115.0 (48049) |  | CHECK |  |
| B_48051BURKE | OPEN Bus BURKE_115.0 (48051) |  | CHECK |  |
| B_48053BURKAVAA | Unlinked Action: BUS 48053 OPEN |  | CHECK |  |
| B_48055BURKAVAB | Unlinked Action: BUS 48055 OPEN |  | CHECK |  |
| B_48057CABGORG | OPEN Bus CAB GORG_115.0 (48057) |  | CHECK |  |
| B_48059CABGORG | OPEN Bus CAB GORG_230.0 (48059) |  | CHECK |  |
| B_48059CABGORG | OPEN Gen NOXON12_ 14.4 (48285) #1 |  | CHECK |  |
| B_48059CABGORG | OPEN Gen NOXON12_ 14.4 (48285) #2 |  | CHECK |  |
| B_48059CABGORG | OPEN Gen NOXON34_ 14.4 (48287) #3 |  | CHECK |  |
| B_48059CABGORG | OPEN Gen NOXON34_ 14.4 (48287) #4 |  | CHECK |  |
| B_48061CABGOR12 | OPEN Bus CABGOR12_ 13.8 (48061) |  | CHECK |  |
| B_48063CABGOR34 | OPEN Bus CABGOR34_ 13.8 (48063) |  | CHECK |  |
| B_48065CABINETG | OPEN Bus CABINETG_115.0 (48065) |  | CHECK |  |
| B_48067CDA | OPEN Bus CDA_115.0 (48067) |  | CHECK |  |
| B_48069CHESTER | OPEN Bus CHESTER_115.0 (48069) |  | CHECK |  |
| B_48071CHEWELAH | OPEN Bus CHEWELAH_115.0 (48071) |  | CHECK |  |
| B_48073CHMBRSTP | OPEN Bus CHMBRSTP_115.0 (48073) |  | CHECK |  |
| B_48075CLEARWTR | OPEN Bus CLEARWTR_115.0 (48075) |  | CHECK |  |
| B_48077CLRKFORK | OPEN Bus CLRKFORK_115.0 (48077) |  | CHECK |  |
| B_48079COLBERT | OPEN Bus COLBERT_115.0 (48079) |  | CHECK |  |
| B_48081COLLWALN | OPEN Bus COLLWALN_115.0 (48081) |  | CHECK |  |
| B_48083COLVAVA | OPEN Bus COLV AVA_115.0 (48083) |  | CHECK |  |
| B_48085COLVILLE | OPEN Bus COLVILLE_ 13.8 (48085) |  | CHECK |  |
| B_48087COTTNWDT | OPEN Bus COTTNWDT_115.0 (48087) |  | CHECK |  |
| B_48089COTTNWOD | OPEN Bus COTTNWOD_115.0 (48089) |  | CHECK |  |
| B_48091CRAIGMNT | OPEN Bus CRAIGMNT_115.0 (48091) |  | CHECK |  |
| B_48093DALTONA | OPEN Bus DALTON A_115.0 (48093) |  | CHECK |  |
| B_48095DALTON2T | OPEN Bus DALTON2T_115.0 (48095) |  | CHECK |  |
| B_48097DALTONT | OPEN Bus DALTONT_115.0 (48097) |  | CHECK |  |
| B_48099DAVENPRT | OPEN Bus DAVENPRT_115.0 (48099) |  | CHECK |  |
| B_48101DEARY | OPEN Bus DEARY_115.0 (48101) |  | CHECK |  |
| B_48103DEVILGP | OPEN Bus DEVIL GP_115.0 (48103) |  | CHECK |  |
| B_48105DEVILGP2 | OPEN Bus DEVILGP2_115.0 (48105) |  | CHECK |  |
| B_48109DIAMOND | OPEN Bus DIAMOND_115.0 (48109) |  | CHECK |  |
| B_48111DOWERRDT | OPEN Bus DOWERRDT_115.0 (48111) |  | CHECK |  |
| B_48113DRYGULCH | OPEN Bus DRYGULCH_115.0 (48113) |  | CHECK |  |
| B_48115EASCOLFX | OPEN Bus EASCOLFX_115.0 (48115) |  | CHECK |  |
| B_48117EASTFARM | OPEN Bus EASTFARM_115.0 (48117) |  | CHECK |  |
| B_48119EGRANTAP | OPEN Bus EGRANTAP_115.0 (48119) |  | CHECK |  |
| B_48121EWAN | OPEN Bus EWAN_115.0 (48121) |  | CHECK |  |
| B_48122FAIRS | OPEN Bus FAIR S_115.0 (48122) |  | CHECK |  |
| B_48123FORD | OPEN Bus FORD_115.0 (48123) |  | CHECK |  |
| B_48125FOURLBPA | OPEN Bus FOURLBPA_115.0 (48125) |  | CHECK |  |
| B_48127FRANCEDR | OPEN Bus FRANCEDR_115.0 (48127) |  | CHECK |  |
| B_48129FTWRIGHT | OPEN Bus FTWRIGHT_115.0 (48129) |  | CHECK |  |
| B_48131GARDENSP | OPEN Bus GARDENSP_115.0 (48131) |  | CHECK |  |
| B_48132HAL&WHIT | OPEN Bus HAL&WHIT_115.0 (48132) |  | CHECK |  |
| B_48133GARFIELD | OPEN Bus GARFIELD_115.0 (48133) |  | CHECK |  |
| B_48135GIFFORD | OPEN Bus GIFFORD_115.0 (48135) |  | CHECK |  |
| B_48137GLENROSE | OPEN Bus GLENROSE_115.0 (48137) |  | CHECK |  |
| B_48139GLENTAP | OPEN Bus GLENTAP_115.0 (48139) |  | CHECK |  |
| B_48141GRANGVIL | OPEN Bus GRANGVIL_115.0 (48141) |  | CHECK |  |
| B_48143GREENWDA | OPEN Bus GREENWDA_115.0 (48143) |  | CHECK |  |
| B_48145HANGMAN | OPEN Bus HANGMAN_115.0 (48145) |  | CHECK |  |
| B_48147HARRNGTN | OPEN Bus HARRNGTN_115.0 (48147) |  | CHECK |  |
| B_48148HAYDEN | OPEN Bus HAYDEN_115.0 (48148) |  | CHECK |  |
| B_48149HEADWORK | OPEN Bus HEADWORK_115.0 (48149) |  | CHECK |  |
| B_48151HECLA | OPEN Bus HECLA_115.0 (48151) |  | CHECK |  |
| B_48153HECLAT | OPEN Bus HECLAT_115.0 (48153) |  | CHECK |  |
| B_48155HERN | OPEN Bus HERN_115.0 (48155) |  | CHECK |  |
| B_48157HOLBROOK | OPEN Bus HOLBROOK_115.0 (48157) |  | CHECK |  |
| B_48159HUETTER | OPEN Bus HUETTER_115.0 (48159) |  | CHECK |  |
| B_48163I.E.PAPR | OPEN Bus I.E.PAPR_115.0 (48163) |  | CHECK |  |
| B_48165IRVIN | OPEN Bus IRVIN_115.0 (48165) |  | CHECK |  |
| B_48167JAYPE | OPEN Bus JAYPE_115.0 (48167) |  | CHECK |  |
| B_48169JULIAETT | OPEN Bus JULIAETT_115.0 (48169) |  | CHECK |  |
| B_48171KAMIAH | OPEN Bus KAMIAH_115.0 (48171) |  | CHECK |  |
| B_48173KETTLEAV | OPEN Bus KETTLEAV_ 13.8 (48173) |  | CHECK |  |
| B_48175KETTLEAV | OPEN Bus KETTLEAV_115.0 (48175) |  | CHECK |  |
| B_48177KOOSKIA | OPEN Bus KOOSKIA_115.0 (48177) |  | CHECK |  |
| B_48179LAKEVIEW | OPEN Bus LAKEVIEW_230.0 (48179) |  | CHECK |  |
| B_48179LAKEVIEW | OPEN Gen NOXON12_ 14.4 (48285) #1 |  | CHECK |  |
| B_48179LAKEVIEW | OPEN Gen NOXON12_ 14.4 (48285) #2 |  | CHECK |  |
| B_48179LAKEVIEW | OPEN Gen NOXON34_ 14.4 (48287) #3 |  | CHECK |  |
| B_48179LAKEVIEW | OPEN Gen NOXON34_ 14.4 (48287) #4 |  | CHECK |  |
| B_48181LATAH | OPEN Bus LATAH_115.0 (48181) |  | CHECK |  |
| B_48183LEON | OPEN Bus LEON_115.0 (48183) |  | CHECK |  |
| B_48185LIBTYLK | OPEN Bus LIBTYLK_115.0 (48185) |  | CHECK |  |
| B_48187LIND | OPEN Bus LIND_115.0 (48187) |  | CHECK |  |
| B_48189LITFAL12 | OPEN Bus LITFAL12_ 4.0 (48189) |  | CHECK |  |
| B_48191LITFAL34 | OPEN Bus LITFAL34_ 4.0 (48191) |  | CHECK |  |
| B_48193LITTFALL | OPEN Bus LITTFALL_115.0 (48193) |  | CHECK |  |
| B_48194LOCUST | OPEN Bus LOCUST_115.0 (48194) |  | CHECK |  |
| B_48195LOLO | OPEN Bus LOLO_115.0 (48195) |  | CHECK |  |
| B_48197LOLO | OPEN Bus LOLO_230.0 (48197) |  | CHECK |  |
| B_48199LONGLAKA | OPEN Bus LONGLAKA_115.0 (48199) |  | CHECK |  |
| B_48201LONGLAKB | OPEN Bus LONGLAKB_115.0 (48201) |  | CHECK |  |
| B_48203LONGLAKT | OPEN Bus LONGLAKT_115.0 (48203) |  | CHECK |  |
| B_48205LONGLKG1 | OPEN Bus LONGLKG1_ 4.0 (48205) |  | CHECK |  |
| B_48207LONGLKG2 | OPEN Bus LONGLKG2_ 4.0 (48207) |  | CHECK |  |
| B_48209LONGLKG3 | OPEN Bus LONGLKG3_ 4.0 (48209) |  | CHECK |  |
| B_48211LONGLKG4 | OPEN Bus LONGLKG4_ 4.0 (48211) |  | CHECK |  |
| B_48213LOONLK | OPEN Bus LOON LK_115.0 (48213) |  | CHECK |  |
| B_48215LUCKYF | OPEN Bus LUCKY F_115.0 (48215) |  | CHECK |  |
| B_48217LUCKYFTP | OPEN Bus LUCKYFTP_115.0 (48217) |  | CHECK |  |
| B_48219LYONSTND | OPEN Bus LYONSTND_115.0 (48219) |  | CHECK |  |
| B_48221MARENGO | OPEN Bus MARENGO_115.0 (48221) |  | CHECK |  |
| B_48222MEADSUB | OPEN Bus MEAD SUB_115.0 (48222) |  | CHECK |  |
| B_48223METCHIP | OPEN Bus METCHIP_115.0 (48223) |  | CHECK |  |
| B_48225METRO | OPEN Bus METRO_115.0 (48225) |  | CHECK |  |
| B_48227MEYERSFL | OPEN Bus MEYERSFL_ 11.0 (48227) |  | CHECK |  |
| B_48229MEYERSFL | OPEN Bus MEYERSFL_ 13.0 (48229) |  | CHECK |  |
| B_48231MICATAP | OPEN Bus MICA TAP_115.0 (48231) |  | CHECK |  |
| B_48233MILAN | OPEN Bus MILAN_115.0 (48233) |  | CHECK |  |
| B_48235MILANTP | OPEN Bus MILAN TP_115.0 (48235) |  | CHECK |  |
| B_48237MILLWOOD | OPEN Bus MILLWOOD_115.0 (48237) |  | CHECK |  |
| B_48239MISSION | OPEN Bus MISSION_115.0 (48239) |  | CHECK |  |
| B_48241MONROEA | OPEN Bus MONROEA_ 13.8 (48241) |  | CHECK |  |
| B_48243MOSCCITY | OPEN Bus MOSCCITY_115.0 (48243) |  | CHECK |  |
| B_48245MOSCITYT | OPEN Bus MOSCITYT_115.0 (48245) |  | CHECK |  |
| B_48247MOSCOW | OPEN Bus MOSCOW_115.0 (48247) |  | CHECK |  |
| B_48249MOSCOW | OPEN Bus MOSCOW_230.0 (48249) |  | CHECK |  |
| B_48251MOSCOWX | OPEN Bus MOSCOWX_115.0 (48251) |  | CHECK |  |
| B_48253NLEWIST | OPEN Bus N LEWIST_115.0 (48253) |  | CHECK |  |
| B_48255NLEWIST | OPEN Bus N LEWIST_230.0 (48255) |  | CHECK |  |
| B_48258NEWPORTT | OPEN Bus NEWPORTT_115.0 (48258) |  | CHECK |  |
| B_48261NEZPERCE | OPEN Bus NEZPERCE_115.0 (48261) |  | CHECK |  |
| B_48263NINEFLSE | OPEN Bus NINEFLSE_ 30.0 (48263) |  | CHECK |  |
| B_48265NINEMI12 | OPEN Bus NINEMI12_ 2.3 (48265) |  | CHECK |  |
| B_48267NINEMI34 | OPEN Bus NINEMI34_ 13.8 (48267) |  | CHECK |  |
| B_48269NINEMILE | OPEN Bus NINEMILE_115.0 (48269) |  | CHECK |  |
| B_48271NINTHCNT | OPEN Bus NINTHCNT_115.0 (48271) |  | CHECK |  |
| B_48273NMOSCOW | OPEN Bus NMOSCOW_115.0 (48273) |  | CHECK |  |
| B_48275NORTHEAS | OPEN Bus NORTHEAS_ 13.8 (48275) |  | CHECK |  |
| B_48277NORTHEAS | OPEN Bus NORTHEAS_115.0 (48277) |  | CHECK |  |
| B_48279NORTHWES | OPEN Bus NORTHWES_115.0 (48279) |  | CHECK |  |
| B_48281NOXON | OPEN Bus NOXON_230.0 (48281) |  | CHECK |  |
| B_48281NOXON | OPEN Gen NOXON12_ 14.4 (48285) #1 |  | CHECK |  |
| B_48281NOXON | OPEN Gen NOXON12_ 14.4 (48285) #2 |  | CHECK |  |
| B_48281NOXON | OPEN Gen NOXON34_ 14.4 (48287) #3 |  | CHECK |  |
| B_48281NOXON | OPEN Gen NOXON34_ 14.4 (48287) #4 |  | CHECK |  |
| B_48283NOXON5 | OPEN Bus NOXON 5_ 14.4 (48283) |  | CHECK |  |
| B_48285NOXON12 | OPEN Bus NOXON12_ 14.4 (48285) |  | CHECK |  |
| B_48287NOXON34 | OPEN Bus NOXON34_ 14.4 (48287) |  | CHECK |  |
| B_48289NOXONCON | OPEN Bus NOXONCON_230.0 (48289) |  | CHECK |  |
| B_48291NPULLMAN | OPEN Bus NPULLMAN_115.0 (48291) |  | CHECK |  |
| B_48293ODEN | OPEN Bus ODEN_115.0 (48293) |  | CHECK |  |
| B_48295ODESSA | OPEN Bus ODESSA_115.0 (48295) |  | CHECK |  |
| B_48297OGARA | OPEN Bus OGARA_115.0 (48297) |  | CHECK |  |
| B_48298OLDTOWN | OPEN Bus OLDTOWN_115.0 (48298) |  | CHECK |  |
| B_48299OPPORTUN | OPEN Bus OPPORTUN_115.0 (48299) |  | CHECK |  |
| B_48300OLDTOWNA | OPEN Bus OLDTOWNA_115.0 (48300) |  | CHECK |  |
| B_48301ORIN | OPEN Bus ORIN_115.0 (48301) |  | CHECK |  |
| B_48303OROFINO | OPEN Bus OROFINO_115.0 (48303) |  | CHECK |  |
| B_48305OSBURN | OPEN Bus OSBURN_115.0 (48305) |  | CHECK |  |
| B_48307OTHELLO | OPEN Bus OTHELLO_115.0 (48307) |  | CHECK |  |
| B_48308LEE&REYN | OPEN Bus LEE&REYN_115.0 (48308) |  | CHECK |  |
| B_48309OTHELOSS | OPEN Bus OTHELOSS_115.0 (48309) |  | CHECK |  |
| B_48311OTIS | OPEN Bus OTIS_115.0 (48311) |  | CHECK |  |
| B_48313PALOUSE | OPEN Bus PALOUSE_115.0 (48313) |  | CHECK |  |
| B_48315PINECRK | OPEN Bus PINE CRK_115.0 (48315) |  | CHECK |  |
| B_48317PINECRK | OPEN Bus PINE CRK_230.0 (48317) |  | CHECK |  |
| B_48317PINECRK | OPEN Gen NOXON34_ 14.4 (48287) #3 |  | CHECK |  |
| B_48317PINECRK | OPEN Gen NOXON34_ 14.4 (48287) #4 |  | CHECK |  |
| B_48319PLEASANT | OPEN Bus PLEASANT_115.0 (48319) |  | CHECK |  |
| B_48321PLUMMER | OPEN Bus PLUMMER_ 4.2 (48321) |  | CHECK |  |
| B_48323PLUMMER | OPEN Bus PLUMMER_115.0 (48323) |  | CHECK |  |
| B_48325PLUMMERG | OPEN Bus PLUMMERG_ 13.8 (48325) |  | CHECK |  |
| B_48327PLUMMWEA | OPEN Bus PLUMMWEA_ 13.8 (48327) |  | CHECK |  |
| B_48329POSTFLS | OPEN Bus POST FLS_115.0 (48329) |  | CHECK |  |
| B_48331POSTFL15 | OPEN Bus POSTFL15_ 2.4 (48331) |  | CHECK |  |
| B_48333POSTFLS6 | OPEN Bus POSTFLS6_ 2.4 (48333) |  | CHECK |  |
| B_48335POSTSTRT | OPEN Bus POSTSTRT_ 4.2 (48335) |  | CHECK |  |
| B_48337POSTSTRT | OPEN Bus POSTSTRT_ 13.8 (48337) |  | CHECK |  |
| B_48339POSTSTRT | OPEN Bus POSTSTRT_115.0 (48339) |  | CHECK |  |
| B_48341POTLATA | OPEN Bus POTLAT A_115.0 (48341) |  | CHECK |  |
| B_48343POUNDLNE | OPEN Bus POUNDLNE_115.0 (48343) |  | CHECK |  |
| B_48345POUNDTAP | OPEN Bus POUNDTAP_115.0 (48345) |  | CHECK |  |
| B_48347PRIESTA | OPEN Bus PRIEST A_115.0 (48347) |  | CHECK |  |
| B_48349RAMSEY | OPEN Bus RAMSEY_115.0 (48349) |  | CHECK |  |
| B_48351RATHBUS1 | OPEN Bus RATHBUS1_115.0 (48351) |  | CHECK |  |
| B_48353RATHBUS2 | OPEN Bus RATHBUS2_115.0 (48353) |  | CHECK |  |
| B_48355RATHDRUM | OPEN Bus RATHDRUM_115.0 (48355) |  | CHECK |  |
| B_48356RATHDRME | OPEN Bus RATHDRME_115.0 (48356) |  | CHECK |  |
| B_48359RATHGEN1 | OPEN Bus RATHGEN1_ 13.8 (48359) |  | CHECK |  |
| B_48361RATHGEN2 | OPEN Bus RATHGEN2_ 13.8 (48361) |  | CHECK |  |
| B_48363REARDAN | OPEN Bus REARDAN_115.0 (48363) |  | CHECK |  |
| B_48365RITZVILL | OPEN Bus RITZVILL_115.0 (48365) |  | CHECK |  |
| B_48367ROCKFORD | OPEN Bus ROCKFORD_115.0 (48367) |  | CHECK |  |
| B_48369ROSALIA | OPEN Bus ROSALIA_115.0 (48369) |  | CHECK |  |
| B_48371ROSSPARK | OPEN Bus ROSSPARK_115.0 (48371) |  | CHECK |  |
| B_48373ROUNDLKT | OPEN Bus ROUNDLKT_115.0 (48373) |  | CHECK |  |
| B_48375ROXBORO | OPEN Bus ROXBORO_115.0 (48375) |  | CHECK |  |
| B_48376SAGLE | OPEN Bus SAGLE_115.0 (48376) |  | CHECK |  |
| B_48377SANDPTA | OPEN Bus SANDPT A_115.0 (48377) |  | CHECK |  |
| B_48379SCOTPAPR | OPEN Bus SCOTPAPR_115.0 (48379) |  | CHECK |  |
| B_48381SEVENTAP | OPEN Bus SEVENTAP_115.0 (48381) |  | CHECK |  |
| B_48383SHAWNEE | OPEN Bus SHAWNEE_115.0 (48383) |  | CHECK |  |
| B_48385SHAWNEE | OPEN Bus SHAWNEE_230.0 (48385) |  | CHECK |  |
| B_48387SILVRLAK | OPEN Bus SILVRLAK_115.0 (48387) |  | CHECK |  |
| B_48388SILVRLK2 | OPEN Bus SILVRLK2_115.0 (48388) |  | CHECK |  |
| B_48389SLEWIST | OPEN Bus SLEWIST_115.0 (48389) |  | CHECK |  |
| B_48391SOTHELLO | OPEN Bus SOTHELLO_115.0 (48391) |  | CHECK |  |
| B_48393SOTHELOT | OPEN Bus SOTHELOT_115.0 (48393) |  | CHECK |  |
| B_48395SOUTHEAS | OPEN Bus SOUTHEAS_115.0 (48395) |  | CHECK |  |
| B_48397SPANGLE | OPEN Bus SPANGLE_115.0 (48397) |  | CHECK |  |
| B_48399SPIRIT | OPEN Bus SPIRIT_115.0 (48399) |  | CHECK |  |
| B_48401SPIRITLK | OPEN Bus SPIRITLK_115.0 (48401) |  | CHECK |  |
| B_48403SPIRITLT | OPEN Bus SPIRITLT_115.0 (48403) |  | CHECK |  |
| B_48405SPKINDPK | OPEN Bus SPKINDPK_115.0 (48405) |  | CHECK |  |
| B_48407SPKWASTE | OPEN Bus SPKWASTE_ 13.8 (48407) |  | CHECK |  |
| B_48409SPKWASTE | OPEN Bus SPKWASTE_115.0 (48409) |  | CHECK |  |
| B_48411SPRAGUE | OPEN Bus SPRAGUE_115.0 (48411) |  | CHECK |  |
| B_48413SPULLMAN | OPEN Bus SPULLMAN_115.0 (48413) |  | CHECK |  |
| B_48417STMARIES | OPEN Bus STMARIES_115.0 (48417) |  | CHECK |  |
| B_48419STRATFRD | OPEN Bus STRATFRD_115.0 (48419) |  | CHECK |  |
| B_48421SUNSET | OPEN Bus SUNSET_115.0 (48421) |  | CHECK |  |
| B_48423SWEETWTR | OPEN Bus SWEETWTR_115.0 (48423) |  | CHECK |  |
| B_48425TAUNTON | OPEN Bus TAUNTON_115.0 (48425) |  | CHECK |  |
| B_48427TEKOA | OPEN Bus TEKOA_115.0 (48427) |  | CHECK |  |
| B_48429TENTHSTW | OPEN Bus TENTHSTW_115.0 (48429) |  | CHECK |  |
| B_48430TERRVIEW | OPEN Bus TERRVIEW_115.0 (48430) |  | CHECK |  |
| B_48431THIRHACH | OPEN Bus THIRHACH_115.0 (48431) |  | CHECK |  |
| B_48433UPRIVER | OPEN Bus UPRIVER_ 2.4 (48433) |  | CHECK |  |
| B_48435UPRIVER | OPEN Bus UPRIVER_ 4.2 (48435) |  | CHECK |  |
| B_48437UPRIVER | OPEN Bus UPRIVER_ 13.8 (48437) |  | CHECK |  |
| B_48439VAAGEN | OPEN Bus VAAGEN_ 4.2 (48439) |  | CHECK |  |
| B_48441VALLEYA | OPEN Bus VALLEY A_115.0 (48441) |  | CHECK |  |
| B_48443VANTAVA | OPEN Bus VANT AVA_230.0 (48443) |  | CHECK |  |
| B_48445VIOLA | OPEN Bus VIOLA_115.0 (48445) |  | CHECK |  |
| B_48447WAIKIKI | OPEN Bus WAIKIKI_115.0 (48447) |  | CHECK |  |
| B_48449WAIKIKIT | OPEN Bus WAIKIKIT_115.0 (48449) |  | CHECK |  |
| B_48451WALAAVA | OPEN Bus WALA AVA_230.0 (48451) |  | CHECK |  |
| B_48453WALLACE | OPEN Bus WALLACE_115.0 (48453) |  | CHECK |  |
| B_48455WARDENA | OPEN Bus WARDEN A_115.0 (48455) |  | CHECK |  |
| B_48457WASHTUNA | OPEN Bus WASHTUNA_115.0 (48457) |  | CHECK |  |
| B_48459WEIPPE | OPEN Bus WEIPPE_115.0 (48459) |  | CHECK |  |
| B_48461WEST | OPEN Bus WEST_115.0 (48461) |  | CHECK |  |
| B_48463WEST | OPEN Bus WEST_230.0 (48463) |  | CHECK |  |
| B_48465WICKES | OPEN Bus WICKES_115.0 (48465) |  | CHECK |  |
| B_48467WILBUR | OPEN Bus WILBUR_115.0 (48467) |  | CHECK |  |
| B_48469WILBURT | OPEN Bus WILBURT_115.0 (48469) |  | CHECK |  |
| B_48471WILSNCKT | OPEN Bus WILSNCKT_115.0 (48471) |  | CHECK |  |
| B_48475CLWTR1 | OPEN Bus CLWTR1_ 34.5 (48475) |  | CHECK |  |
| B_48476CLWTR2 | OPEN Bus CLWTR2_ 34.5 (48476) |  | CHECK |  |
| B_48477CLWTR3 | OPEN Bus CLWTR3_ 34.5 (48477) |  | CHECK |  |
| B_48478CLWTR4 | OPEN Bus CLWTR4_ 34.5 (48478) |  | CHECK |  |
| B_48479CLWTR5 | OPEN Bus CLWTR5_ 34.5 (48479) |  | CHECK |  |
| B_48480CLWTR6 | OPEN Bus CLWTR6_ 34.5 (48480) |  | CHECK |  |
| B_48481CLWTR7 | OPEN Bus CLWTR7_ 34.5 (48481) |  | CHECK |  |
| B_48482CWGEN3 | OPEN Bus CWGEN3_ 12.0 (48482) |  | CHECK |  |
| B_48483CWGEN4 | OPEN Bus CWGEN4_ 12.0 (48483) |  | CHECK |  |
| B_48484CWTW1 | OPEN Bus CWTW1_ 12.0 (48484) |  | CHECK |  |
| B_48485CWTW2 | OPEN Bus CWTW2_ 12.0 (48485) |  | CHECK |  |
| B_48486CWTW3 | OPEN Bus CWTW3_ 12.0 (48486) |  | CHECK |  |
| B_48487CWTW4 | OPEN Bus CWTW4_ 12.0 (48487) |  | CHECK |  |
| B_48488CWTW5 | OPEN Bus CWTW5_ 12.0 (48488) |  | CHECK |  |
| B_48489CWTW6 | OPEN Bus CWTW6_ 12.0 (48489) |  | CHECK |  |
| B_48490CWBUS1 | OPEN Bus CWBUS1_ 12.0 (48490) |  | CHECK |  |
| B_48491CWBUS2 | OPEN Bus CWBUS2_ 12.0 (48491) |  | CHECK |  |
| B_48492CWBUS3 | OPEN Bus CWBUS3_ 12.0 (48492) |  | CHECK |  |
| B_48493CWBUS4 | OPEN Bus CWBUS4_ 12.0 (48493) |  | CHECK |  |
| B_48494CWBUS5 | OPEN Bus CWBUS5_ 12.0 (48494) |  | CHECK |  |
| B_48495CWBUS6 | OPEN Bus CWBUS6_ 12.0 (48495) |  | CHECK |  |
| B_48496CWBUS7 | OPEN Bus CWBUS7_ 12.0 (48496) |  | CHECK |  |
| B_48497CWBUS8 | OPEN Bus CWBUS8_ 12.0 (48497) |  | CHECK |  |
| B_48510DRYCREEK | OPEN Bus DRYCREEK_115.0 (48510) |  | CHECK |  |
| B_48512DRYCREEK | OPEN Bus DRYCREEK_230.0 (48512) |  | CHECK |  |
| B_48514CRCHFELD | OPEN Bus CRCHFELD_115.0 (48514) |  | CHECK |  |
| B_48520BOULDERW | OPEN Bus BOULDERW_115.0 (48520) |  | CHECK |  |
| B_48522BOULDERE | OPEN Bus BOULDERE_115.0 (48522) |  | CHECK |  |
| B_48524BOULDER | OPEN Bus BOULDER_230.0 (48524) |  | CHECK |  |
| B_48526BOULDERG | OPEN Bus BOULDERG_ 13.8 (48526) |  | CHECK |  |
| B_Hatwai 230 Bus (BPA) | OPEN Bus HATWAI_230.0 (40519) |  | CHECK |  |
| B_Hot Springs 230 Bus (BPA) | OPEN Bus HOT SPR_230.0 (40551) |  | CHECK |  |
| B_Hot Springs 230 Bus (BPA) | OPEN Gen HUNGHR34_ 13.8 (40556) #3 |  | ALWAYS |  |
| B_Hot Springs 230 Bus (BPA) | OPEN Gen HUNGHR34_ 13.8 (40556) #4 |  | ALWAYS |  |
| B_Hot Springs 230 Bus (BPA) | OPEN Bus LIB PH2_230.0 (44201) |  | CHECK |  |
| BKR_BEACON 115 BUS TIE BREAKER FAIL | OPEN Bus BEACON N_115.0 (48023) |  | CHECK |  |
| BKR_BEACON 115 BUS TIE BREAKER FAIL | OPEN Bus BEACON S_115.0 (48029) |  | CHECK |  |
| BKR_BEACON 230 BUS TIE BREAKER FAIL | OPEN Bus BEACON S_230.0 (48031) |  | CHECK |  |
| BKR_BEACON 230 BUS TIE BREAKER FAIL | OPEN Bus BEACON N_230.0 (48025) |  | CHECK |  |
| BKR_DWORSHAK 500 BREAKER FAIL (BPA) | OPEN Bus DWORSHAK_500.0 (40369) |  | CHECK |  |
| BKR_DWORSHAK 500 BREAKER FAIL (BPA) | OPEN Branch DWOR 1_ 13.8 (40361) TO DWOR 2_ 13.8 (40363) CKT 1 |  | CHECK |  |
| BKR_DWORSHAK 500 BREAKER FAIL (BPA) | OPEN Gen DWOR 2_ 13.8 (40363) #1 |  | CHECK |  |
| BKR_DWORSHAK 500 BREAKER FAIL (BPA) | OPEN Gen DWOR 3_ 13.8 (40365) #1 |  | CHECK |  |
| BKR_DWORSHAK 500 BREAKER FAIL (BPA) | OPEN Load MILCTYDC_230.0 (63010) #D1 |  | CHECK |  |
| BKR_DWORSHAK 500 BREAKER FAIL (BPA) | OPEN Shunt GARRISON_500.0 (40459) #r |  | CHECK |  |
| BKR_DWORSHAK 500 BREAKER FAIL (BPA) | OPEN Bus LIB PH1_230.0 (44200) | West MT Hydro > 1000 | CHECK |  |
| BKR_DWORSHAK 500 BREAKER FAIL (BPA) | OPEN Bus LIB PH2_230.0 (44201) | West MT Hydro > 1000 | CHECK |  |
| BKR_HATWAI 500 BREAKER FAIL (BPA) | OPEN Shunt GARRISON_500.0 (40459) #r |  | CHECK |  |
| BKR_HATWAI 500 BREAKER FAIL (BPA) | OPEN Branch DWOR 1_ 13.8 (40361) TO DWOR 2_ 13.8 (40363) CKT 1 |  | CHECK |  |
| BKR_HATWAI 500 BREAKER FAIL (BPA) | OPEN Bus HATWAI_500.0 (40521) |  | CHECK |  |
| BKR_HATWAI 500 BREAKER FAIL (BPA) | OPEN Gen DWOR 3_ 13.8 (40365) #1 |  | CHECK |  |
| BKR_HATWAI 500 BREAKER FAIL (BPA) | OPEN Gen DWOR 2_ 13.8 (40363) #1 |  | CHECK |  |
| BKR_HATWAI 500 BREAKER FAIL (BPA) | OPEN Load MILCTYDC_230.0 (63010) #D1 |  | CHECK |  |
| BKR_HATWAI 500 BREAKER FAIL (BPA) | OPEN Bus LIB PH2_230.0 (44201) | West MT Hydro > 1000 | CHECK |  |
| BKR_HATWAI 500 BREAKER FAIL (BPA) | OPEN Bus LIB PH1_230.0 (44200) | West MT Hydro > 1000 | CHECK |  |
| BKR_HATWAI 500 BREAKER FAIL (BPA) | OPEN Gen LANCAS S_ 13.8 (47569) #1 | WEST OF HATWAI > 3500 | CHECK |  |
| BKR_HATWAI 500 BREAKER FAIL (BPA) | OPEN Gen LANCAS G_ 18.0 (47568) #1 | WEST OF HATWAI > 3500 | CHECK |  |
| BKR_NOXON 230 BUS TIE BREAKER FAIL | OPEN Bus NOXON_230.0 (48281) |  | CHECK |  |
| BKR_NOXON 230 BUS TIE BREAKER FAIL | OPEN Bus NOXONBPA_230.0 (40787) |  | CHECK |  |
| BKR_NOXON 230 BUS TIE BREAKER FAIL | OPEN Gen NOXON12_ 14.4 (48285) #1 |  | CHECK |  |
| BKR_NOXON 230 BUS TIE BREAKER FAIL | OPEN Gen NOXON12_ 14.4 (48285) #2 |  | CHECK |  |
| BKR_NOXON 230 BUS TIE BREAKER FAIL | OPEN Gen NOXON34_ 14.4 (48287) #3 |  | CHECK |  |
| BKR_NOXON 230 BUS TIE BREAKER FAIL | OPEN Gen NOXON34_ 14.4 (48287) #4 |  | CHECK |  |
| BKR_NOXON 230 BUS TIE BREAKER FAIL | OPEN Bus LIB PH2_230.0 (44201) |  | CHECK |  |
| L_40017ADDY-40263COLVBPAC1 | OPEN Branch ADDY_115.0 (40017) TO COLV BPA_115.0 (40263) CKT 1 |  | CHECK |  |
| L_40017ADDY-48071CHEWELAHC1 | OPEN Branch ADDY_115.0 (40017) TO CHEWELAH_115.0 (48071) CKT 1 |  | CHECK |  |
| L_40017ADDY-48135GIFFORDC1 | OPEN Branch ADDY_115.0 (40017) TO GIFFORD_115.0 (48135) CKT 1 |  | CHECK |  |
| L_40017ADDY-48213LOONLKC1 | OPEN Branch ADDY_115.0 (40017) TO LOON LK_115.0 (48213) CKT 1 |  | CHECK |  |
| L_40017ADDY-48223METCHIPC1 | OPEN Branch ADDY_115.0 (40017) TO METCHIP_115.0 (48223) CKT 1 |  | CHECK |  |
| L_40019ADDY-40021ADDY2C1 | OPEN Branch ADDY_230.0 (40019) TO ADDY 2_230.0 (40021) CKT 1 |  | CHECK |  |
| L_40019ADDY-40319CUSICKC1 | OPEN Branch ADDY_230.0 (40019) TO CUSICK_230.0 (40319) CKT 1 |  | CHECK |  |
| L_40021ADDY2-40090BELLS3C1_MS | OPEN MultiSectionLine ADDY 2_230.0 (40021) TO BELL S3_230.0 (40090) CKT 1 |  | CHECK |  |
| L_40021ADDY2-40090BELLS3C1_MS | OPEN Gen BOUNDG56_ 14.4 (46474) #56 | South of Boundary > 650 | CHECK |  |
| L_40021ADDY2-40090BELLS3C1_MS | OPEN Gen BOUNDG55_ 14.4 (46472) #55 | South of Boundary > 650 | CHECK |  |
| L_40021ADDY2-40145BOUNDARYC1_MS | OPEN MultiSectionLine ADDY 2_230.0 (40021) TO BOUNDARY_230.0 (40145) CKT 1 |  | CHECK |  |
| L_40021ADDY2-40145BOUNDARYC1_MS | OPEN Gen BOUNDG56_ 14.4 (46474) #56 | South of Boundary > 650 | CHECK |  |
| L_40021ADDY2-40145BOUNDARYC1_MS | OPEN Gen BOUNDG55_ 14.4 (46472) #55 | South of Boundary > 650 | CHECK |  |
| L_40023AHSAHKA-40367DWORSHAKC1 | OPEN Branch AHSAHKA_115.0 (40023) TO DWORSHAK_115.0 (40367) CKT 1 |  | CHECK |  |
| L_40023AHSAHKA-48303OROFINOC1 | OPEN Branch AHSAHKA_115.0 (40023) TO OROFINO_115.0 (48303) CKT 1 |  | CHECK |  |
| L_40029ALBENIF-40779NEWPORTBC1 | OPEN Branch ALBENI F_115.0 (40029) TO NEWPORTB_115.0 (40779) CKT 1 |  | CHECK |  |
| L_40029ALBENIF-47027DIAMLAKC1 | OPEN Branch ALBENI F_115.0 (40029) TO DIAM LAK_115.0 (47027) CKT 1 |  | CHECK |  |
| L_40029ALBENIF-48347PRIESTAC1 | OPEN Branch ALBENI F_115.0 (40029) TO PRIEST A_115.0 (48347) CKT 1 |  | CHECK |  |
| L_40067ATHOL-48017ATHOLTAPC1 | OPEN Branch ATHOL_115.0 (40067) TO ATHOLTAP_115.0 (48017) CKT 1 |  | CHECK |  |
| L_40086BELLS1-40088BELLS2C1 | OPEN Branch BELL S1_230.0 (40086) TO BELL S2_230.0 (40088) CKT 1 |  | CHECK |  |
| L_40086BELLS1-40092BELLS4C1 | OPEN Branch BELL S1_230.0 (40086) TO BELL S4_230.0 (40092) CKT 1 |  | CHECK |  |
| L_40086BELLS1-40909SACHEENC1 | OPEN Branch BELL S1_230.0 (40086) TO SACHEEN_230.0 (40909) CKT 1 |  | CHECK |  |
| L_40086BELLS1-40909SACHEENC1 | OPEN Gen BOUNDG55_ 14.4 (46472) #55 | South of Boundary > 650 | CHECK |  |
| L_40086BELLS1-40909SACHEENC1 | OPEN Gen BOUNDG56_ 14.4 (46474) #56 | South of Boundary > 650 | CHECK |  |
| L_40086BELLS1-41275WESTBPA1C1 | OPEN Branch BELL S1_230.0 (40086) TO WESTBPA1_230.0 (41275) CKT 1 |  | CHECK |  |
| L_40087BELLBPA-40113BIGELOWC1 | OPEN Branch BELL BPA_115.0 (40087) TO BIGELOW_115.0 (40113) CKT 1 |  | CHECK |  |
| L_40087BELLBPA-40730MEADTAPC1 | OPEN Branch BELL BPA_115.0 (40087) TO MEAD TAP_115.0 (40730) CKT 1 |  | CHECK |  |
| L_40087BELLBPA-41015SPRNGHILC1 | OPEN Branch BELL BPA_115.0 (40087) TO SPRNGHIL_115.0 (41015) CKT 1 |  | CHECK |  |
| L_40087BELLBPA-41089TRENTWODC1 | OPEN Branch BELL BPA_115.0 (40087) TO TRENTWOD_115.0 (41089) CKT 1 |  | CHECK |  |
| L_40087BELLBPA-48029BEACONSC1 | OPEN Branch BEACON S_115.0 (48029) TO BELL BPA_115.0 (40087) CKT 1 |  | CHECK |  |
| L_40087BELLBPA-48033BELLTAPC1 | OPEN Branch BELL BPA_115.0 (40087) TO BELL TAP_115.0 (48033) CKT 1 |  | CHECK |  |
| L_40087BELLBPA-48449WAIKIKITC1 | OPEN Branch BELL BPA_115.0 (40087) TO WAIKIKIT_115.0 (48449) CKT 1 |  | CHECK |  |
| L_40088BELLS2-40090BELLS3C1 | OPEN Branch BELL S2_230.0 (40088) TO BELL S3_230.0 (40090) CKT 1 |  | CHECK |  |
| L_40088BELLS2-41358COULEES3C5_MS | OPEN MultiSectionLine BELL S2_230.0 (40088) TO COULEES3_230.0 (41358) CKT 5 |  | CHECK |  |
| L_40088BELLS2-47091USK | OPEN Branch BELL S2_230.0 (40088) TO USK_230.0 (47091) CKT 1 |  | CHECK |  |
| L_40090BELLS3-40092BELLS4C1 | OPEN Branch BELL S3_230.0 (40090) TO BELL S4_230.0 (40092) CKT 1 |  | CHECK |  |
| L_40090BELLS3-40624LANCASTRC1_MS | OPEN Gen LANCAS G_ 18.0 (47568) #1 |  | ALWAYS |  |
| L_40090BELLS3-40624LANCASTRC1_MS | OPEN Gen LANCAS S_ 13.8 (47569) #1 |  | ALWAYS |  |
| L_40090BELLS3-40624LANCASTRC1_MS | OPEN MultiSectionLine BELL S3_230.0 (40090) TO LANCASTR_230.0 (40624) CKT 1 |  | ALWAYS |  |
| L_40090BELLS3-40624LANCASTRC1_MS | OPEN Bus LIB PH2_230.0 (44201) |  | CHECK |  |
| L_40090BELLS3-41356COULEES1C3_MS | OPEN MultiSectionLine BELL S3_230.0 (40090) TO COULEES1_230.0 (41356) CKT 3 |  | CHECK |  |
| L_40090BELLS3-48025BEACONNC5 | OPEN Branch BEACON N_230.0 (48025) TO BELL S3_230.0 (40090) CKT 5 |  | CHECK |  |
| L_40091BELLBPA-40096BELLSCC1 | OPEN Branch BELL BPA_500.0 (40091) TO BELL SC_500.0 (40096) CKT 1 |  | CHECK |  |
| L_40091BELLBPA-40096BELLSCC1 | OPEN Load MILCTYDC_230.0 (63010) #D1 |  | CHECK |  |
| L_40091BELLBPA-40096BELLSCC1 | OPEN Shunt GARRISON_500.0 (40459) #r |  | CHECK |  |
| L_40091BELLBPA-40096BELLSCC1 | OPEN Bus LIB PH1_230.0 (44200) | West MT Hydro > 1000 | CHECK |  |
| L_40091BELLBPA-40096BELLSCC1 | OPEN Bus LIB PH2_230.0 (44201) | West MT Hydro > 1000 | CHECK |  |
| L_40091BELLBPA-40288COULER1C6 | OPEN Branch BELL BPA_500.0 (40091) TO COULE R1_500.0 (40288) CKT 6 |  | ALWAYS |  |
| L_40091BELLBPA-40288COULER1C6 | OPEN Load MILCTYDC_230.0 (63010) #D1 |  | ALWAYS |  |
| L_40091BELLBPA-40288COULER1C6 | OPEN Bus LIB PH2_230.0 (44201) | West MT Hydro > 1000 | CHECK |  |
| L_40091BELLBPA-40288COULER1C6 | OPEN Bus LIB PH1_230.0 (44200) | West MT Hydro > 1000 | CHECK |  |
| L_40091BELLBPA-40288COULER1C6 | OPEN Gen LANCAS G_ 18.0 (47568) #1 | WEST OF HATWAI > 3500 | CHECK |  |
| L_40091BELLBPA-40288COULER1C6 | OPEN Gen LANCAS S_ 13.8 (47569) #1 | WEST OF HATWAI > 3500 | CHECK |  |
| L_40092BELLS4-48031BEACONSC4 | OPEN Branch BEACON S_230.0 (48031) TO BELL S4_230.0 (40092) CKT 4 |  | CHECK |  |
| L_40096BELLSC-41057TAFTC1_MS | OPEN MultiSectionLine BELL SC_500.0 (40096) TO TAFT_500.0 (41057) CKT 1 |  | CHECK |  |
| L_40096BELLSC-41057TAFTC1_MS | OPEN Load MILCTYDC_230.0 (63010) #D1 |  | CHECK |  |
| L_40096BELLSC-41057TAFTC1_MS | OPEN Shunt GARRISON_500.0 (40459) #r |  | CHECK |  |
| L_40096BELLSC-41057TAFTC1_MS | OPEN Bus LIB PH1_230.0 (44200) | West MT Hydro > 1000 | CHECK |  |
| L_40096BELLSC-41057TAFTC1_MS | OPEN Bus LIB PH2_230.0 (44201) | West MT Hydro > 1000 | CHECK |  |
| L_40113BIGELOW-40483GREENBLC1 | OPEN Branch BIGELOW_115.0 (40113) TO GREEN BL_115.0 (40483) CKT 1 |  | CHECK |  |
| L_40113BIGELOW-41089TRENTWODC1 | OPEN Branch BIGELOW_115.0 (40113) TO TRENTWOD_115.0 (41089) CKT 1 |  | CHECK |  |
| L_40133BONNERS-40927SAMUELSC1_MS | OPEN MultiSectionLine BONNERS_115.0 (40133) TO SAMUELS_115.0 (40927) CKT 1 |  | CHECK |  |
| L_40133BONNERS-41239MOYIETC1 | OPEN Branch BONNERS_115.0 (40133) TO MOYIE T_115.0 (41239) CKT 1 |  | CHECK |  |
| L_40133BONNERS-47194MTHALLC1 | OPEN Branch BONNERS_115.0 (40133) TO MT HALL_115.0 (47194) CKT 1 |  | CHECK |  |
| L_40145BOUNDARY-40319CUSICKC1 | OPEN Branch BOUNDARY_230.0 (40145) TO CUSICK_230.0 (40319) CKT 1 |  | CHECK |  |
| L_40145BOUNDARY-40909SACHEENC1 | OPEN Branch BOUNDARY_230.0 (40145) TO SACHEEN_230.0 (40909) CKT 1 |  | CHECK |  |
| L_40145BOUNDARY-46476BOUNDPH1C1 | OPEN Branch BOUNDARY_230.0 (40145) TO BOUNDPH1_230.0 (46476) CKT 1 |  | CHECK |  |
| L_40145BOUNDARY-46478BOUNDPH2C1 | OPEN Branch BOUNDARY_230.0 (40145) TO BOUNDPH2_230.0 (46478) CKT 1 |  | CHECK |  |
| L_40145BOUNDARY-46480BOUNDPH3C1 | OPEN Branch BOUNDARY_230.0 (40145) TO BOUNDPH3_230.0 (46480) CKT 1 |  | CHECK |  |
| L_40145BOUNDARY-46482BOUNDPH4C1 | OPEN Branch BOUNDARY_230.0 (40145) TO BOUNDPH4_230.0 (46482) CKT 1 |  | CHECK |  |
| L_40145BOUNDARY-46484BOUNDPH5C1 | OPEN Branch BOUNDARY_230.0 (40145) TO BOUNDPH5_230.0 (46484) CKT 1 |  | CHECK |  |
| L_40145BOUNDARY-46486BOUNDPH6C1 | OPEN Branch BOUNDARY_230.0 (40145) TO BOUNDPH6_230.0 (46486) CKT 1 |  | CHECK |  |
| L_40149BRINKENS-48341POTLATAC1 | OPEN Branch BRINKENS_115.0 (40149) TO POTLAT A_115.0 (48341) CKT 1 |  | CHECK |  |
| L_40149BRINKENS-48445VIOLAC1 | OPEN Branch BRINKENS_115.0 (40149) TO VIOLA_115.0 (48445) CKT 1 |  | CHECK |  |
| L_40215CHENEY-40439FOURLKSC1 | OPEN Branch CHENEY_115.0 (40215) TO FOURLKS_115.0 (40439) CKT 1 |  | CHECK |  |
| L_40239CLARKSTN-40835POMEROYC1 | OPEN Branch CLARKSTN_115.0 (40239) TO POMEROY_115.0 (40835) CKT 1 |  | CHECK |  |
| L_40239CLARKSTN-48253NLEWISTC1 | OPEN Branch CLARKSTN_115.0 (40239) TO N LEWIST_115.0 (48253) CKT 1 |  | CHECK |  |
| L_40239CLARKSTN-48253NLEWISTC1 | SET INJECTION GROUP HOPKINS RIDGE TO 50 MW |  | CHECK |  |
| L_40245CLAYTON-40337DEERPRKC1 | OPEN Branch CLAYTON_115.0 (40245) TO DEER PRK_115.0 (40337) CKT 1 |  | CHECK |  |
| L_40245CLAYTON-48213LOONLKC1 | OPEN Branch CLAYTON_115.0 (40245) TO LOON LK_115.0 (48213) CKT 1 |  | CHECK |  |
| L_40255COLBERTT-40495HALFMOONC1 | OPEN Branch COLBERTT_115.0 (40255) TO HALFMOON_115.0 (40495) CKT 1 |  | CHECK |  |
| L_40255COLBERTT-40730MEADTAPC1 | OPEN Branch COLBERTT_115.0 (40255) TO MEAD TAP_115.0 (40730) CKT 1 |  | CHECK |  |
| L_40263COLVBPA-40607KETTLETC1 | OPEN Branch COLV BPA_115.0 (40263) TO KETTLE T_115.0 (40607) CKT 1 |  | CHECK |  |
| L_40263COLVBPA-48399SPIRITC1 | OPEN Branch COLV BPA_115.0 (40263) TO SPIRIT_115.0 (48399) CKT 1 |  | CHECK |  |
| L_40275COOKMT-40607KETTLETC1 | OPEN Branch COOK M T_115.0 (40275) TO KETTLE T_115.0 (40607) CKT 1 |  | CHECK |  |
| L_40275COOKMT-40879REPUBLICC1 | OPEN Branch COOK M T_115.0 (40275) TO REPUBLIC_115.0 (40879) CKT 1 |  | CHECK |  |
| L_40288COULER1-40287COULEEC6 | OPEN Branch COULE R1_500.0 (40288) TO COULEE_500.0 (40287) CKT 6 |  | ALWAYS |  |
| L_40288COULER1-40287COULEEC6 | OPEN Load MILCTYDC_230.0 (63010) #D1 |  | ALWAYS |  |
| L_40288COULER1-40287COULEEC6 | OPEN Bus LIB PH2_230.0 (44201) | West MT Hydro > 1000 | CHECK |  |
| L_40288COULER1-40287COULEEC6 | OPEN Bus LIB PH1_230.0 (44200) | West MT Hydro > 1000 | CHECK |  |
| L_40288COULER1-40287COULEEC6 | OPEN Gen LANCAS G_ 18.0 (47568) #1 | WEST OF HATWAI > 3500 | CHECK |  |
| L_40288COULER1-40287COULEEC6 | OPEN Gen LANCAS S_ 13.8 (47569) #1 | WEST OF HATWAI > 3500 | CHECK |  |
| L_40311CRESTN-40384EGYPTTPC1 | OPEN Branch CRESTN_115.0 (40311) TO EGYPT TP_115.0 (40384) CKT 1 |  | CHECK |  |
| L_40311CRESTN-41127WAGNERLTC1 | OPEN Branch CRESTN_115.0 (40311) TO WAGNERLT_115.0 (41127) CKT 1 |  | CHECK |  |
| L_40317CUSICK-47254USKC1 | OPEN Branch CUSICK_115.0 (40317) TO USK_115.0 (47254) CKT 1 |  | CHECK |  |
| L_40319CUSICK-47091USKC1_MS | OPEN MultiSectionLine CUSICK_230.0 (40319) TO USK_230.0 (47091) CKT 1 |  | CHECK |  |
| L_40337DEERPRK-48235MILANTPC1 | OPEN Branch DEER PRK_115.0 (40337) TO MILAN TP_115.0 (48235) CKT 1 |  | CHECK |  |
| L_40383EGRANVIL-48119EGRANTAPC1 | OPEN Branch EGRANTAP_115.0 (48119) TO EGRANVIL_115.0 (40383) CKT 1 |  | CHECK |  |
| L_40384EGYPTTP-40637LARENEC1 | OPEN Branch EGYPT TP_115.0 (40384) TO LARENE_115.0 (40637) CKT 1 |  | CHECK |  |
| L_40397FAIRCHLD-48009AIRWAYHTC1 | OPEN Branch AIRWAYHT_115.0 (48009) TO FAIRCHLD_115.0 (40397) CKT 1 |  | CHECK |  |
| L_40397FAIRCHLD-48388SILVRLK2C1 | OPEN Branch FAIRCHLD_115.0 (40397) TO SILVRLK2_115.0 (48388) CKT 1 |  | CHECK |  |
| L_40449GAFFNEY-48363REARDANC1 | OPEN Branch GAFFNEY_115.0 (40449) TO REARDAN_115.0 (48363) CKT 1 |  | CHECK |  |
| L_40449GAFFNEY-48411SPRAGUEC1 | OPEN Branch GAFFNEY_115.0 (40449) TO SPRAGUE_115.0 (48411) CKT 1 |  | CHECK |  |
| L_40495HALFMOON-41099TUMTUMC1 | OPEN Branch HALFMOON_115.0 (40495) TO TUM TUM_115.0 (41099) CKT 1 |  | CHECK |  |
| L_40519HATWAI-48197LOLOC1 | OPEN Branch HATWAI_230.0 (40519) TO LOLO_230.0 (48197) CKT 1 |  | CHECK |  |
| L_40519HATWAI-48249MOSCOWC1 | OPEN Branch HATWAI_230.0 (40519) TO MOSCOW_230.0 (48249) CKT 1 |  | CHECK |  |
| L_40519HATWAI-48255NLEWISTC1 | OPEN Branch HATWAI_230.0 (40519) TO N LEWIST_230.0 (48255) CKT 1 |  | CHECK |  |
| L_40525HAYFORD-48125FOURLBPAC1 | OPEN Branch FOURLBPA_115.0 (48125) TO HAYFORD_115.0 (40525) CKT 1 |  | CHECK |  |
| L_40551HOTSPR-41091TROUTCRC1 | OPEN Branch HOT SPR_230.0 (40551) TO TROUT CR_230.0 (41091) CKT 1 |  | CHECK |  |
| L_40551HOTSPR-48281NOXONC2 | OPEN Branch HOT SPR_230.0 (40551) TO NOXON_230.0 (48281) CKT 2 |  | CHECK |  |
| L_40577IRBY-48295ODESSAC1 | OPEN Branch IRBY_115.0 (40577) TO ODESSA_115.0 (48295) CKT 1 |  | CHECK |  |
| L_40577IRBY-48471WILSNCKTC1 | OPEN Branch IRBY_115.0 (40577) TO WILSNCKT_115.0 (48471) CKT 1 |  | CHECK |  |
| L_40607KETTLET-48175KETTLEAVC1 | OPEN Branch KETTLE T_115.0 (40607) TO KETTLEAV_115.0 (48175) CKT 1 |  | CHECK |  |
| L_40617LACLEDE-40857PRIESTC1 | OPEN Branch LACLEDE_115.0 (40617) TO PRIEST_115.0 (40857) CKT 1 |  | CHECK |  |
| L_40617LACLEDE-40933SANDPONTC1 | OPEN Branch LACLEDE_115.0 (40617) TO SANDPONT_115.0 (40933) CKT 1 |  | CHECK |  |
| L_40624LANCASTR-40787NOXONBPAC1_MS | OPEN MultiSectionLine LANCASTR_230.0 (40624) TO NOXONBPA_230.0 (40787) CKT 1 |  | CHECK |  |
| L_40624LANCASTR-40787NOXONBPAC1_MS | OPEN Bus LIB PH2_230.0 (44201) |  | CHECK |  |
| L_40637LARENE-41015SPRNGHILC1 | OPEN Branch LARENE_115.0 (40637) TO SPRNGHIL_115.0 (41015) CKT 1 |  | CHECK |  |
| L_40657LIBBY-40787NOXONBPAC1_MS | OPEN MultiSectionLine LIBBY_230.0 (40657) TO NOXONBPA_230.0 (40787) CKT 1 |  | CHECK |  |
| L_40657LIBBY-40787NOXONBPAC1_MS | OPEN Bus LIB PH2_230.0 (44201) |  | CHECK |  |
| L_40730MEADTAP-48222MEADSUBC1 | OPEN Branch MEAD SUB_115.0 (48222) TO MEAD TAP_115.0 (40730) CKT 1 |  | CHECK |  |
| L_40731METALINE-40732METLNTAPC1 | OPEN Branch METALINE_115.0 (40731) TO METLNTAP_115.0 (40732) CKT 1 |  | CHECK |  |
| L_40779NEWPORTB-47086PINESTC1 | OPEN Branch NEWPORTB_115.0 (40779) TO PINE ST_115.0 (47086) CKT 1 |  | CHECK |  |
| L_40787NOXONBPA-48289NOXONCONC1 | OPEN Branch NOXONBPA_230.0 (40787) TO NOXONCON_230.0 (48289) CKT 1 |  | CHECK |  |
| L_40855PRAIRIEB-48329POSTFLSC1 | OPEN Branch POST FLS_115.0 (48329) TO PRAIRIEB_115.0 (40855) CKT 1 |  | CHECK |  |
| L_40855PRAIRIEB-48349RAMSEYC1 | OPEN Branch PRAIRIEB_115.0 (40855) TO RAMSEY_115.0 (48349) CKT 1 |  | CHECK |  |
| L_40857PRIEST-48347PRIESTAC1 | OPEN Branch PRIEST_115.0 (40857) TO PRIEST A_115.0 (48347) CKT 1 |  | CHECK |  |
| L_40927SAMUELS-40965SELLEC1_MS | OPEN MultiSectionLine SAMUELS_115.0 (40927) TO SELLE_115.0 (40965) CKT 1 |  | CHECK |  |
| L_40929SANDCRK-40931SANDTPC1 | OPEN Branch SAND CRK_115.0 (40929) TO SAND TP_115.0 (40931) CKT 1 |  | CHECK |  |
| L_40929SANDCRK-40965SELLEC1_MS | OPEN MultiSectionLine SAND CRK_115.0 (40929) TO SELLE_115.0 (40965) CKT 1 |  | CHECK |  |
| L_40929SANDCRK-48377SANDPTAC1_MS | OPEN MultiSectionLine SAND CRK_115.0 (40929) TO SANDPT A_115.0 (48377) CKT 1 |  | CHECK |  |
| L_40931SANDTP-40933SANDPONTC1_MS | OPEN MultiSectionLine SAND TP_115.0 (40931) TO SANDPONT_115.0 (40933) CKT 1 |  | CHECK |  |
| L_40933SANDPONT-48376SAGLEC1 | OPEN Branch SANDPONT_115.0 (40933) TO SAGLE_115.0 (48376) CKT 1 |  | CHECK |  |
| L_40953SCARCELO-48356RATHDRMEC1 | OPEN Branch RATHDRME_115.0 (48356) TO SCARCELO_115.0 (40953) CKT 1 |  | CHECK |  |
| L_41089TRENTWOD-41117VERATAPC1 | OPEN Branch TRENTWOD_115.0 (41089) TO VERA TAP_115.0 (41117) CKT 1 |  | CHECK |  |
| L_41097TROY-41169YAAKC1 | OPEN Branch TROY_115.0 (41097) TO YAAK_115.0 (41169) CKT 1 |  | CHECK |  |
| L_41107VALYWAY-41117VERATAPC1 | OPEN Branch VALY WAY_115.0 (41107) TO VERA TAP_115.0 (41117) CKT 1 |  | CHECK |  |
| L_41125WAGNERLK-48469WILBURTC1 | OPEN Branch WAGNERLK_115.0 (41125) TO WILBURT_115.0 (48469) CKT 1 |  | CHECK |  |
| L_41127WAGNERLT-48469WILBURTC1 | OPEN Branch WAGNERLT_115.0 (41127) TO WILBURT_115.0 (48469) CKT 1 |  | CHECK |  |
| L_41190BOXTAP-40732METLNTAPC1 | OPEN Branch BOX TAP_115.0 (41190) TO METLNTAP_115.0 (40732) CKT 1 |  | CHECK |  |
| L_41190BOXTAP-48399SPIRITC1 | OPEN Branch BOX TAP_115.0 (41190) TO SPIRIT_115.0 (48399) CKT 1 |  | CHECK |  |
| L_41239MOYIET-41169YAAKC1 | OPEN Branch MOYIE T_115.0 (41239) TO YAAK_115.0 (41169) CKT 1 |  | CHECK |  |
| L_41239MOYIET-41240MOYIETXC1 | OPEN Branch MOYIE T_115.0 (41239) TO MOYIE TX_115.0 (41240) CKT 1 |  | CHECK |  |
| L_41240MOYIETX-41241NBENCHC1 | OPEN Branch MOYIE TX_115.0 (41240) TO N BENCH_115.0 (41241) CKT 1 |  | CHECK |  |
| L_41260SULLIVNB-41115VERAC1 | OPEN Branch SULLIVNB_115.0 (41260) TO VERA_115.0 (41115) CKT 1 |  | CHECK |  |
| L_41260SULLIVNB-41117VERATAPC1 | OPEN Branch SULLIVNB_115.0 (41260) TO VERA TAP_115.0 (41117) CKT 1 |  | CHECK |  |
| L_41357COULEES2-41276WESTBPA2C1 | OPEN Branch COULEES2_230.0 (41357) TO WESTBPA2_230.0 (41276) CKT 1 |  | CHECK |  |
| L_46021COULECTY-48149HEADWORKC1 | OPEN Branch COULECTY_115.0 (46021) TO HEADWORK_115.0 (48149) CKT 1 |  | CHECK |  |
| L_46021COULECTY-48419STRATFRDC1 | OPEN Branch COULECTY_115.0 (46021) TO STRATFRD_115.0 (48419) CKT 1 |  | CHECK |  |
| L_46039LARSON-48373ROUNDLKTC1 | OPEN Branch LARSON_115.0 (46039) TO ROUNDLKT_115.0 (48373) CKT 1 |  | CHECK |  |
| L_46077ROUNDLK-48373ROUNDLKTC1 | OPEN Branch ROUND LK_115.0 (46077) TO ROUNDLKT_115.0 (48373) CKT 1 |  | CHECK |  |
| L_46087SANDUNES-48455WARDENAC1 | OPEN Branch SANDUNES_115.0 (46087) TO WARDEN A_115.0 (48455) CKT 1 |  | CHECK |  |
| L_46150COUL2GPD-41127WAGNERLTC1 | OPEN Branch COUL2GPD_115.0 (46150) TO WAGNERLT_115.0 (41127) CKT 1 |  | CHECK |  |
| L_46151Larson-46156Rockyfd 230 | OPEN Branch LARSON_230.0 (46151) TO ROCKYFD_230.0 (46156) CKT 1 |  | CHECK |  |
| L_46805CHELAN-48149HEADWORKC1 | OPEN Branch CHELAN_115.0 (46805) TO HEADWORK_115.0 (48149) CKT 1 |  | CHECK |  |
| L_47009BOXCANY-40317CUSICKC1 | OPEN Branch BOX CANY_115.0 (47009) TO CUSICK_115.0 (40317) CKT 1 |  | CHECK |  |
| L_47025DELIGHT-48187LINDC1 | OPEN Branch DELIGHT_115.0 (47025) TO LIND_115.0 (48187) CKT 1 |  | CHECK |  |
| L_47025DELIGHT-48457WASHTUNAC1 | OPEN Branch DELIGHT_115.0 (47025) TO WASHTUNA_115.0 (48457) CKT 1 |  | CHECK |  |
| L_47027DIAMLAK-40907SACHEENC1 | OPEN Branch DIAM LAK_115.0 (47027) TO SACHEEN_115.0 (40907) CKT 1 |  | CHECK |  |
| L_47033DOWERRD-48111DOWERRDTC1 | OPEN Branch DOWER RD_115.0 (47033) TO DOWERRDT_115.0 (48111) CKT 1 |  | CHECK |  |
| L_47038EGYPT-40384EGYPTTPC1 | OPEN Branch EGYPT_115.0 (47038) TO EGYPT TP_115.0 (40384) CKT 1 |  | CHECK |  |
| L_47086PINEST-47254USKC1 | OPEN Branch PINE ST_115.0 (47086) TO USK_115.0 (47254) CKT 1 |  | CHECK |  |
| L_47086PINEST-48258NEWPORTTC1 | OPEN Branch NEWPORTT_115.0 (48258) TO PINE ST_115.0 (47086) CKT 1 |  | CHECK |  |
| L_47126BOXPS-41190BOXTAPC1 | OPEN Branch BOX PS_115.0 (47126) TO BOX TAP_115.0 (41190) CKT 1 |  | CHECK |  |
| L_47194MTHALL-41299SMITHFLSC1 | OPEN Branch MT HALL_115.0 (47194) TO SMITHFLS_115.0 (41299) CKT 1 |  | CHECK |  |
| L_47278LIBBYFEC-41097TROYC1 | OPEN Branch LIBBYFEC_115.0 (47278) TO TROY_115.0 (41097) CKT 1 |  | CHECK |  |
| L_47501ARMSTRNG-48383SHAWNEEC1 | OPEN Branch ARMSTRNG_115.0 (47501) TO SHAWNEE_115.0 (48383) CKT 1 |  | CHECK |  |
| L_47501ARMSTRNG-48413SPULLMANC1 | OPEN Branch ARMSTRNG_115.0 (47501) TO SPULLMAN_115.0 (48413) CKT 1 |  | CHECK |  |
| L_47503CHAMBERS-48073CHMBRSTPC1 | OPEN Branch CHAMBERS_115.0 (47503) TO CHMBRSTP_115.0 (48073) CKT 1 |  | CHECK |  |
| L_47505HOODOO-48043BLANCHRDC1 | OPEN Branch BLANCHRD_115.0 (48043) TO HOODOO_115.0 (47505) CKT 1 |  | CHECK |  |
| L_47505HOODOO-48403SPIRITLTC1 | OPEN Branch HOODOO_115.0 (47505) TO SPIRITLT_115.0 (48403) CKT 1 |  | CHECK |  |
| L_47507HOPKINSB-48231MICATAPC1 | OPEN Branch HOPKINSB_115.0 (47507) TO MICA TAP_115.0 (48231) CKT 1 |  | CHECK |  |
| L_47507HOPKINSB-48271NINTHCNTC1 | OPEN Branch HOPKINSB_115.0 (47507) TO NINTHCNT_115.0 (48271) CKT 1 |  | CHECK |  |
| L_47509MICA-48231MICATAPC1 | OPEN Branch MICA_115.0 (47509) TO MICA TAP_115.0 (48231) CKT 1 |  | CHECK |  |
| L_47511MOAB-48319PLEASANTC1 | OPEN Branch MOAB_115.0 (47511) TO PLEASANT_115.0 (48319) CKT 1 |  | CHECK |  |
| L_47511MOAB-48522BOULDEREC1 | OPEN Branch BOULDERE_115.0 (48522) TO MOAB_115.0 (47511) CKT 1 |  | CHECK |  |
| L_480014LAKETP-40439FOURLKSC1 | OPEN Branch 4LAKE TP_115.0 (48001) TO FOURLKS_115.0 (40439) CKT 1 |  | CHECK |  |
| L_480014LAKETP-48145HANGMANC1 | OPEN Branch 4LAKE TP_115.0 (48001) TO HANGMAN_115.0 (48145) CKT 1 |  | CHECK |  |
| L_480014LAKETP-48397SPANGLEC1 | OPEN Branch 4LAKE TP_115.0 (48001) TO SPANGLE_115.0 (48397) CKT 1 |  | CHECK |  |
| L_48003NELSONSB-48005NELSONTPC1 | OPEN Branch NELSONSB_115.0 (48003) TO NELSONT_115.0 (48005) CKT 1 |  | CHECK |  |
| L_48005NELSONTP-48069CHESTERC1 | OPEN Branch NELSONT_115.0 (48005) TO CHESTER_115.0 (48069) CKT 1 |  | CHECK |  |
| L_48005NELSONTP-48271NINTHCNTC1 | OPEN Branch NELSONT_115.0 (48005) TO NINTHCNT_115.0 (48271) CKT 1 |  | CHECK |  |
| L_48009AIRWAYHT-47513W.PLAINSC1 | OPEN Branch AIRWAYHT_115.0 (48009) TO W.PLAINS_115.0 (47513) CKT 1 |  | CHECK |  |
| L_48009AIRWAYHT-48421SUNSETC1 | OPEN Branch AIRWAYHT_115.0 (48009) TO SUNSET_115.0 (48421) CKT 1 |  | CHECK |  |
| L_48011APPLETAP-48013APPLEWAYC1 | OPEN Branch APPLETAP_115.0 (48011) TO APPLEWAY_115.0 (48013) CKT 1 |  | CHECK |  |
| L_48011APPLETAP-48095DALTON2TC1 | OPEN Branch APPLETAP_115.0 (48011) TO DALTON2T_115.0 (48095) CKT 1 |  | CHECK |  |
| L_48011APPLETAP-48349RAMSEYC1 | OPEN Branch APPLETAP_115.0 (48011) TO RAMSEY_115.0 (48349) CKT 1 |  | CHECK |  |
| L_48015ARDEN-48223METCHIPC1 | OPEN Branch ARDEN_115.0 (48015) TO METCHIP_115.0 (48223) CKT 1 |  | CHECK |  |
| L_48015ARDEN-48301ORINC1 | OPEN Branch ARDEN_115.0 (48015) TO ORIN_115.0 (48301) CKT 1 |  | CHECK |  |
| L_48017ATHOLTAP-40953SCARCELOC1 | OPEN Branch ATHOLTAP_115.0 (48017) TO SCARCELO_115.0 (40953) CKT 1 |  | CHECK |  |
| L_48017ATHOLTAP-48403SPIRITLTC1 | OPEN Branch ATHOLTAP_115.0 (48017) TO SPIRITLT_115.0 (48403) CKT 1 |  | CHECK |  |
| L_48019AVONDALE-48095DALTON2TC1 | OPEN Branch AVONDALE_115.0 (48019) TO DALTON2T_115.0 (48095) CKT 1 |  | CHECK |  |
| L_48019AVONDALE-48356RATHDRMEC1 | OPEN Branch AVONDALE_115.0 (48019) TO RATHDRME_115.0 (48356) CKT 1 |  | CHECK |  |
| L_48021BARKER-48311OTISC1 | OPEN Branch BARKER_115.0 (48021) TO OTIS_115.0 (48311) CKT 1 |  | CHECK |  |
| L_48023BEACONN-48029BEACONSC1 | OPEN Branch BEACON N_115.0 (48023) TO BEACON S_115.0 (48029) CKT 1 |  | CHECK |  |
| L_48023BEACONN-48271NINTHCNTC1 | OPEN Branch BEACON N_115.0 (48023) TO NINTHCNT_115.0 (48271) CKT 1 |  | CHECK |  |
| L_48023BEACONN-48277NORTHEASC1 | OPEN Branch BEACON N_115.0 (48023) TO NORTHEAS_115.0 (48277) CKT 1 |  | CHECK |  |
| L_48023BEACONN-48371ROSSPARKC1 | OPEN Branch BEACON N_115.0 (48023) TO ROSSPARK_115.0 (48371) CKT 1 |  | CHECK |  |
| L_48023BEACONN-48405SPKINDPKC1 | OPEN Branch BEACON N_115.0 (48023) TO SPKINDPK_115.0 (48405) CKT 1 |  | CHECK |  |
| L_48025BEACONN-48031BEACONSC1 | OPEN Branch BEACON N_230.0 (48025) TO BEACON S_230.0 (48031) CKT 1 |  | CHECK |  |
| L_48025BEACONN-48357RATHDRUMC2 | OPEN Branch BEACON N_230.0 (48025) TO RATHDRUM_230.0 (48357) CKT 2 |  | CHECK |  |
| L_48027BEACONS-48437UPRIVERC1 | OPEN Branch BEACON S_ 13.8 (48027) TO UPRIVER_ 13.8 (48437) CKT 1 |  | CHECK |  |
| L_48029BEACONS-48033BELLTAPC1 | OPEN Branch BEACON S_115.0 (48029) TO BELL TAP_115.0 (48033) CKT 1 |  | CHECK |  |
| L_48029BEACONS-48194LOCUSTC1 | OPEN Branch BEACON S_115.0 (48029) TO LOCUST_115.0 (48194) CKT 1 |  | CHECK |  |
| L_48029BEACONS-48271NINTHCNTC2 | OPEN Branch BEACON S_115.0 (48029) TO NINTHCNT_115.0 (48271) CKT 2 |  | CHECK |  |
| L_48031BEACONS-48524BOULDERC1 | OPEN Branch BEACON S_230.0 (48031) TO BOULDER_230.0 (48524) CKT 1 |  | CHECK |  |
| L_48033BELLTAP-48381SEVENTAPC1 | OPEN Branch BELL TAP_115.0 (48033) TO SEVENTAP_115.0 (48381) CKT 1 |  | CHECK |  |
| L_48035BENEWAH-48181LATAHC1 | OPEN Branch BENEWAH_115.0 (48035) TO LATAH_115.0 (48181) CKT 1 |  | CHECK |  |
| L_48035BENEWAH-48323PLUMMERC1 | OPEN Branch BENEWAH_115.0 (48035) TO PLUMMER_115.0 (48323) CKT 1 |  | CHECK |  |
| L_48037BENEWAH-48249MOSCOWC1 | OPEN Branch BENEWAH_230.0 (48037) TO MOSCOW_230.0 (48249) CKT 1 |  | CHECK |  |
| L_48037BENEWAH-48317PINECRKC1 | OPEN Branch BENEWAH_230.0 (48037) TO PINE CRK_230.0 (48317) CKT 1 |  | CHECK |  |
| L_48037BENEWAH-48317PINECRKC1 | OPEN Gen NOXON34_ 14.4 (48287) #3 |  | CHECK |  |
| L_48037BENEWAH-48317PINECRKC1 | OPEN Gen NOXON34_ 14.4 (48287) #4 |  | CHECK |  |
| L_48037BENEWAH-48385SHAWNEEC1 | OPEN Branch BENEWAH_230.0 (48037) TO SHAWNEE_230.0 (48385) CKT 1 |  | CHECK |  |
| L_48037BENEWAH-48524BOULDERC1 | OPEN Branch BOULDER_230.0 (48524) TO BENEWAH_230.0 (48037) CKT 1 |  | CHECK |  |
| L_48039BENTNAVA-40097BENTONC1 | OPEN Branch BENTNAVA_115.0 (48039) TO BENTON_115.0 (40097) CKT 1 |  | CHECK |  |
| L_48039BENTNAVA-48425TAUNTONC1 | OPEN Branch BENTNAVA_115.0 (48039) TO TAUNTON_115.0 (48425) CKT 1 |  | CHECK |  |
| L_48041BIGCREEK-48049BUNKRHILC1 | OPEN Branch BIGCREEK_115.0 (48041) TO BUNKRHIL_115.0 (48049) CKT 1 |  | CHECK |  |
| L_48041BIGCREEK-48153HECLATC1 | OPEN Branch BIGCREEK_115.0 (48041) TO HECLAT_115.0 (48153) CKT 1 |  | CHECK |  |
| L_48043BLANCHRD-48258NEWPORTTC1 | OPEN Branch BLANCHRD_115.0 (48043) TO NEWPORTT_115.0 (48258) CKT 1 |  | CHECK |  |
| L_48045BLUECRK-48067CDAC1 | OPEN Branch BLUECRK_115.0 (48045) TO CDA_115.0 (48067) CKT 1 |  | CHECK |  |
| L_48045BLUECRK-48239MISSIONC1 | OPEN Branch BLUECRK_115.0 (48045) TO MISSION_115.0 (48239) CKT 1 |  | CHECK |  |
| L_48047BRONX-48293ODENC1 | OPEN Branch BRONX_115.0 (48047) TO ODEN_115.0 (48293) CKT 1 |  | CHECK |  |
| L_48047BRONX-48377SANDPTAC1 | OPEN Branch BRONX_115.0 (48047) TO SANDPT A_115.0 (48377) CKT 1 |  | CHECK |  |
| L_48049BUNKRHIL-48315PINECRKC1 | OPEN Branch BUNKRHIL_115.0 (48049) TO PINE CRK_115.0 (48315) CKT 1 |  | CHECK |  |
| L_48051BURKE-48053BURKAVAAC1 | Unlinked Action: BRANCH 48053 48051 1 OPEN |  | CHECK |  |
| L_48051BURKE-48055BURKAVABC1 | Unlinked Action: BRANCH 48055 48051 1 OPEN |  | CHECK |  |
| L_48051BURKE-48151HECLAC1 | OPEN Branch BURKE_115.0 (48051) TO HECLA_115.0 (48151) CKT 1 |  | CHECK |  |
| L_48051BURKE-48217LUCKYFTPC1 | OPEN Branch BURKE_115.0 (48051) TO LUCKYFTP_115.0 (48217) CKT 1 |  | CHECK |  |
| L_48057CABGORG-48065CABINETGC1 | OPEN Branch CAB GORG_115.0 (48057) TO CABINETG_115.0 (48065) CKT 1 |  | CHECK |  |
| L_48059CABGORG-48179LAKEVIEWC1 | OPEN Branch CAB GORG_230.0 (48059) TO LAKEVIEW_230.0 (48179) CKT 1 |  | CHECK |  |
| L_48059CABGORG-48179LAKEVIEWC1 | OPEN Gen NOXON12_ 14.4 (48285) #1 |  | CHECK |  |
| L_48059CABGORG-48179LAKEVIEWC1 | OPEN Gen NOXON12_ 14.4 (48285) #2 |  | CHECK |  |
| L_48059CABGORG-48179LAKEVIEWC1 | OPEN Gen NOXON34_ 14.4 (48287) #3 |  | CHECK |  |
| L_48059CABGORG-48179LAKEVIEWC1 | OPEN Gen NOXON34_ 14.4 (48287) #4 |  | CHECK |  |
| L_48059CABGORG-48281NOXONC1 | OPEN Branch CAB GORG_230.0 (48059) TO NOXON_230.0 (48281) CKT 1 |  | ALWAYS |  |
| L_48059CABGORG-48281NOXONC1 | OPEN Gen NOXON34_ 14.4 (48287) #3 | WMH > 1450 | CHECK |  |
| L_48059CABGORG-48281NOXONC1 | OPEN Gen NOXON34_ 14.4 (48287) #4 | WMH > 1450 | CHECK |  |
| L_48065CABINETG-48077CLRKFORKC1 | OPEN Branch CABINETG_115.0 (48065) TO CLRKFORK_115.0 (48077) CKT 1 |  | CHECK |  |
| L_48067CDA-48097DALTONTC1 | OPEN Branch CDA_115.0 (48067) TO DALTONT_115.0 (48097) CKT 1 |  | CHECK |  |
| L_48067CDA-48349RAMSEYC1 | OPEN Branch CDA_115.0 (48067) TO RAMSEY_115.0 (48349) CKT 1 |  | CHECK |  |
| L_48069CHESTER-48299OPPORTUNC1 | OPEN Branch CHESTER_115.0 (48069) TO OPPORTUN_115.0 (48299) CKT 1 |  | CHECK |  |
| L_48071CHEWELAH-48441VALLEYAC1 | OPEN Branch CHEWELAH_115.0 (48071) TO VALLEY A_115.0 (48441) CKT 1 |  | CHECK |  |
| L_48073CHMBRSTP-48115EASCOLFXC1 | OPEN Branch CHMBRSTP_115.0 (48073) TO EASCOLFX_115.0 (48115) CKT 1 |  | CHECK |  |
| L_48073CHMBRSTP-48383SHAWNEEC1 | OPEN Branch CHMBRSTP_115.0 (48073) TO SHAWNEE_115.0 (48383) CKT 1 |  | CHECK |  |
| L_48075CLEARWTR-48195LOLOC1 | OPEN Branch CLEARWTR_115.0 (48075) TO LOLO_115.0 (48195) CKT 1 |  | CHECK |  |
| L_48075CLEARWTR-48253NLEWISTC1 | OPEN Branch CLEARWTR_115.0 (48075) TO N LEWIST_115.0 (48253) CKT 1 |  | CHECK |  |
| L_48075CLEARWTR-48429TENTHSTWC1 | OPEN Branch CLEARWTR_115.0 (48075) TO TENTHSTW_115.0 (48429) CKT 1 |  | CHECK |  |
| L_48077CLRKFORK-48293ODENC1 | OPEN Branch CLRKFORK_115.0 (48077) TO ODEN_115.0 (48293) CKT 1 |  | CHECK |  |
| L_48079COLBERT-40255COLBERTTC1 | OPEN Branch COLBERT_115.0 (48079) TO COLBERTT_115.0 (40255) CKT 1 |  | CHECK |  |
| L_48081COLLWALN-48129FTWRIGHTC1 | OPEN Branch COLLWALN_115.0 (48081) TO FTWRIGHT_115.0 (48129) CKT 1 |  | CHECK |  |
| L_48081COLLWALN-48339POSTSTRTC1 | OPEN Branch COLLWALN_115.0 (48081) TO POSTSTRT_115.0 (48339) CKT 1 |  | CHECK |  |
| L_48083COLVAVA-48143GREENWDAC1 | OPEN Branch COLV AVA_115.0 (48083) TO GREENWDA_115.0 (48143) CKT 1 |  | CHECK |  |
| L_48083COLVAVA-48301ORINC1 | OPEN Branch COLV AVA_115.0 (48083) TO ORIN_115.0 (48301) CKT 1 |  | CHECK |  |
| L_48087COTTNWDT-48089COTTNWODC1 | OPEN Branch COTTNWDT_115.0 (48087) TO COTTNWOD_115.0 (48089) CKT 1 |  | CHECK |  |
| L_48087COTTNWDT-48261NEZPERCEC1 | OPEN Branch COTTNWDT_115.0 (48087) TO NEZPERCE_115.0 (48261) CKT 1 |  | CHECK |  |
| L_48087COTTNWDT-48465WICKESC1 | OPEN Branch COTTNWDT_115.0 (48087) TO WICKES_115.0 (48465) CKT 1 |  | CHECK |  |
| L_48091CRAIGMNT-48261NEZPERCEC1 | OPEN Branch CRAIGMNT_115.0 (48091) TO NEZPERCE_115.0 (48261) CKT 1 |  | CHECK |  |
| L_48091CRAIGMNT-48423SWEETWTRC1 | OPEN Branch CRAIGMNT_115.0 (48091) TO SWEETWTR_115.0 (48423) CKT 1 |  | CHECK |  |
| L_48093DALTONA-48097DALTONTC1 | OPEN Branch DALTON A_115.0 (48093) TO DALTONT_115.0 (48097) CKT 1 |  | CHECK |  |
| L_48097DALTONT-48148HAYDENC1 | OPEN Branch DALTONT_115.0 (48097) TO HAYDEN_115.0 (48148) CKT 1 |  | CHECK |  |
| L_48099DAVENPRT-48105DEVILGP2C1 | OPEN Branch DAVENPRT_115.0 (48099) TO DEVILGP2_115.0 (48105) CKT 1 |  | CHECK |  |
| L_48099DAVENPRT-48147HARRNGTNC1 | OPEN Branch DAVENPRT_115.0 (48099) TO HARRNGTN_115.0 (48147) CKT 1 |  | CHECK |  |
| L_48101DEARY-48169JULIAETTC1 | OPEN Branch DEARY_115.0 (48101) TO JULIAETT_115.0 (48169) CKT 1 |  | CHECK |  |
| L_48103DEVILGP-47513W.PLAINSC1 | OPEN Branch DEVIL GP_115.0 (48103) TO W.PLAINS_115.0 (47513) CKT 1 |  | CHECK |  |
| L_48103DEVILGP-48105DEVILGP2C1 | OPEN Branch DEVIL GP_115.0 (48103) TO DEVILGP2_115.0 (48105) CKT 1 |  | CHECK |  |
| L_48103DEVILGP-48199LONGLAKAC1 | OPEN Branch DEVIL GP_115.0 (48103) TO LONGLAKA_115.0 (48199) CKT 1 |  | CHECK |  |
| L_48103DEVILGP-48201LONGLAKBC1 | OPEN Branch DEVIL GP_115.0 (48103) TO LONGLAKB_115.0 (48201) CKT 1 |  | CHECK |  |
| L_48103DEVILGP-48203LONGLAKTC1 | OPEN Branch DEVIL GP_115.0 (48103) TO LONGLAKT_115.0 (48203) CKT 1 |  | CHECK |  |
| L_48103DEVILGP-48269NINEMILEC1 | OPEN Branch DEVIL GP_115.0 (48103) TO NINEMILE_115.0 (48269) CKT 1 |  | CHECK |  |
| L_48105DEVILGP2-48193LITTFALLC1 | OPEN Branch DEVILGP2_115.0 (48105) TO LITTFALL_115.0 (48193) CKT 1 |  | CHECK |  |
| L_48105DEVILGP2-48193LITTFALLC2 | OPEN Branch DEVILGP2_115.0 (48105) TO LITTFALL_115.0 (48193) CKT 2 |  | CHECK |  |
| L_48105DEVILGP2-48363REARDANC1 | OPEN Branch DEVILGP2_115.0 (48105) TO REARDAN_115.0 (48363) CKT 1 |  | CHECK |  |
| L_48109DIAMOND-48121EWANC1 | OPEN Branch DIAMOND_115.0 (48109) TO EWAN_115.0 (48121) CKT 1 |  | CHECK |  |
| L_48109DIAMOND-48383SHAWNEEC1 | OPEN Branch DIAMOND_115.0 (48109) TO SHAWNEE_115.0 (48383) CKT 1 |  | CHECK |  |
| L_48111DOWERRDT-48329POSTFLSC1 | OPEN Branch DOWERRDT_115.0 (48111) TO POST FLS_115.0 (48329) CKT 1 |  | CHECK |  |
| L_48113DRYGULCH-48253NLEWISTC1 | OPEN Branch DRYGULCH_115.0 (48113) TO N LEWIST_115.0 (48253) CKT 1 |  | CHECK |  |
| L_48115EASCOLFX-48369ROSALIAC1 | OPEN Branch EASCOLFX_115.0 (48115) TO ROSALIA_115.0 (48369) CKT 1 |  | CHECK |  |
| L_48117EASTFARM-48311OTISC1 | OPEN Branch EASTFARM_115.0 (48117) TO OTIS_115.0 (48311) CKT 1 |  | CHECK |  |
| L_48117EASTFARM-48329POSTFLSC1 | OPEN Branch EASTFARM_115.0 (48117) TO POST FLS_115.0 (48329) CKT 1 |  | CHECK |  |
| L_48119EGRANTAP-48141GRANGVILC1 | OPEN Branch EGRANTAP_115.0 (48119) TO GRANGVIL_115.0 (48141) CKT 1 |  | CHECK |  |
| L_48119EGRANTAP-48177KOOSKIAC1 | OPEN Branch EGRANTAP_115.0 (48119) TO KOOSKIA_115.0 (48177) CKT 1 |  | CHECK |  |
| L_48121EWAN-48221MARENGOC1 | OPEN Branch EWAN_115.0 (48121) TO MARENGO_115.0 (48221) CKT 1 |  | CHECK |  |
| L_48122FAIRS-48387SILVRLAKC1 | OPEN Branch FAIR S_115.0 (48122) TO SILVRLAK_115.0 (48387) CKT 1 |  | CHECK |  |
| L_48123FORD-48203LONGLAKTC1 | OPEN Branch FORD_115.0 (48123) TO LONGLAKT_115.0 (48203) CKT 1 |  | CHECK |  |
| L_48123FORD-48441VALLEYAC1 | OPEN Branch FORD_115.0 (48123) TO VALLEY A_115.0 (48441) CKT 1 |  | CHECK |  |
| L_48125FOURLBPA-40439FOURLKSC1 | OPEN Branch FOURLBPA_115.0 (48125) TO FOURLKS_115.0 (40439) CKT 1 |  | CHECK |  |
| L_48125FOURLBPA-40525HAYFORDC1 | OPEN Branch FOURLBPA_115.0 (48125) TO HAYFORD_115.0 (40525) CKT 1 |  | CHECK |  |
| L_48125FOURLBPA-48132HAL&WHITC1 | OPEN Branch FOURLBPA_115.0 (48125) TO HAL&WHIT_115.0 (48132) CKT 1 |  | CHECK |  |
| L_48127FRANCEDR-48219LYONSTNDC1 | OPEN Branch FRANCEDR_115.0 (48127) TO LYONSTND_115.0 (48219) CKT 1 |  | CHECK |  |
| L_48127FRANCEDR-48279NORTHWESC1 | OPEN Branch FRANCEDR_115.0 (48127) TO NORTHWES_115.0 (48279) CKT 1 |  | CHECK |  |
| L_48127FRANCEDR-48381SEVENTAPC1 | OPEN Branch FRANCEDR_115.0 (48127) TO SEVENTAP_115.0 (48381) CKT 1 |  | CHECK |  |
| L_48129FTWRIGHT-48461WESTC1 | OPEN Branch FTWRIGHT_115.0 (48129) TO WEST_115.0 (48461) CKT 1 |  | CHECK |  |
| L_48131GARDENSP-40525HAYFORDC1 | OPEN Branch GARDENSP_115.0 (48131) TO HAYFORD_115.0 (40525) CKT 1 |  | CHECK |  |
| L_48131GARDENSP-48409SPKWASTEC1 | OPEN Branch GARDENSP_115.0 (48131) TO SPKWASTE_115.0 (48409) CKT 1 |  | CHECK |  |
| L_48131GARDENSP-48421SUNSETC1 | OPEN Branch GARDENSP_115.0 (48131) TO SUNSET_115.0 (48421) CKT 1 |  | CHECK |  |
| L_48132HAL&WHIT-48387SILVRLAKC1 | OPEN Branch HAL&WHIT_115.0 (48132) TO SILVRLAK_115.0 (48387) CKT 1 |  | CHECK |  |
| L_48133GARFIELD-48313PALOUSEC1 | OPEN Branch GARFIELD_115.0 (48133) TO PALOUSE_115.0 (48313) CKT 1 |  | CHECK |  |
| L_48133GARFIELD-48427TEKOAC1 | OPEN Branch GARFIELD_115.0 (48133) TO TEKOA_115.0 (48427) CKT 1 |  | CHECK |  |
| L_48137GLENROSE-48139GLENTAPC1 | OPEN Branch GLENROSE_115.0 (48137) TO GLENTAP_115.0 (48139) CKT 1 |  | CHECK |  |
| L_48139GLENTAP-48271NINTHCNTC1 | OPEN Branch GLENTAP_115.0 (48139) TO NINTHCNT_115.0 (48271) CKT 1 |  | CHECK |  |
| L_48139GLENTAP-48395SOUTHEASC1 | OPEN Branch GLENTAP_115.0 (48139) TO SOUTHEAS_115.0 (48395) CKT 1 |  | CHECK |  |
| L_48141GRANGVIL-48465WICKESC1 | OPEN Branch GRANGVIL_115.0 (48141) TO WICKES_115.0 (48465) CKT 1 |  | CHECK |  |
| L_48143GREENWDA-48175KETTLEAVC1 | OPEN Branch GREENWDA_115.0 (48143) TO KETTLEAV_115.0 (48175) CKT 1 |  | CHECK |  |
| L_48145HANGMAN-48421SUNSETC1 | OPEN Branch HANGMAN_115.0 (48145) TO SUNSET_115.0 (48421) CKT 1 |  | CHECK |  |
| L_48147HARRNGTN-48295ODESSAC1 | OPEN Branch HARRNGTN_115.0 (48147) TO ODESSA_115.0 (48295) CKT 1 |  | CHECK |  |
| L_48148HAYDEN-48356RATHDRMEC1 | OPEN Branch HAYDEN_115.0 (48148) TO RATHDRME_115.0 (48356) CKT 1 |  | CHECK |  |
| L_48151HECLA-48453WALLACEC1 | OPEN Branch HECLA_115.0 (48151) TO WALLACE_115.0 (48453) CKT 1 |  | CHECK |  |
| L_48153HECLAT-48217LUCKYFTPC1 | OPEN Branch HECLAT_115.0 (48153) TO LUCKYFTP_115.0 (48217) CKT 1 |  | CHECK |  |
| L_48155HERN-48159HUETTERC1 | OPEN Branch HERN_115.0 (48155) TO HUETTER_115.0 (48159) CKT 1 |  | CHECK |  |
| L_48155HERN-48349RAMSEYC1 | OPEN Branch HERN_115.0 (48155) TO RAMSEY_115.0 (48349) CKT 1 |  | CHECK |  |
| L_48157HOLBROOK-48253NLEWISTC1 | OPEN Branch HOLBROOK_115.0 (48157) TO N LEWIST_115.0 (48253) CKT 1 |  | CHECK |  |
| L_48157HOLBROOK-48389SLEWISTC1 | OPEN Branch HOLBROOK_115.0 (48157) TO SLEWIST_115.0 (48389) CKT 1 |  | CHECK |  |
| L_48159HUETTER-48355RATHDRUMC1 | OPEN Branch HUETTER_115.0 (48159) TO RATHDRUM_115.0 (48355) CKT 1 |  | CHECK |  |
| L_48163I.E.PAPR-48237MILLWOODC1 | OPEN Branch I.E.PAPR_115.0 (48163) TO MILLWOOD_115.0 (48237) CKT 1 |  | CHECK |  |
| L_48165IRVIN-48237MILLWOODC1 | OPEN Branch IRVIN_115.0 (48165) TO MILLWOOD_115.0 (48237) CKT 1 |  | CHECK |  |
| L_48165IRVIN-48299OPPORTUNC1 | OPEN Branch IRVIN_115.0 (48165) TO OPPORTUN_115.0 (48299) CKT 1 |  | CHECK |  |
| L_48167JAYPE-48459WEIPPEC1 | OPEN Branch JAYPE_115.0 (48167) TO WEIPPE_115.0 (48459) CKT 1 |  | CHECK |  |
| L_48169JULIAETT-48247MOSCOWC1 | OPEN Branch JULIAETT_115.0 (48169) TO MOSCOW_115.0 (48247) CKT 1 |  | CHECK |  |
| L_48169JULIAETT-48303OROFINOC1 | OPEN Branch JULIAETT_115.0 (48169) TO OROFINO_115.0 (48303) CKT 1 |  | CHECK |  |
| L_48171KAMIAH-48261NEZPERCEC1 | OPEN Branch KAMIAH_115.0 (48171) TO NEZPERCE_115.0 (48261) CKT 1 |  | CHECK |  |
| L_48171KAMIAH-48379SCOTPAPRC1 | OPEN Branch KAMIAH_115.0 (48171) TO SCOTPAPR_115.0 (48379) CKT 1 |  | CHECK |  |
| L_48177KOOSKIA-48379SCOTPAPRC1 | OPEN Branch KOOSKIA_115.0 (48177) TO SCOTPAPR_115.0 (48379) CKT 1 |  | CHECK |  |
| L_48179LAKEVIEW-48357RATHDRUMC1 | OPEN Branch LAKEVIEW_230.0 (48179) TO RATHDRUM_230.0 (48357) CKT 1 |  | CHECK |  |
| L_48179LAKEVIEW-48357RATHDRUMC1 | OPEN Gen NOXON12_ 14.4 (48285) #1 |  | CHECK |  |
| L_48179LAKEVIEW-48357RATHDRUMC1 | OPEN Gen NOXON12_ 14.4 (48285) #2 |  | CHECK |  |
| L_48179LAKEVIEW-48357RATHDRUMC1 | OPEN Gen NOXON34_ 14.4 (48287) #3 |  | CHECK |  |
| L_48179LAKEVIEW-48357RATHDRUMC1 | OPEN Gen NOXON34_ 14.4 (48287) #4 |  | CHECK |  |
| L_48181LATAH-48367ROCKFORDC1 | OPEN Branch LATAH_115.0 (48181) TO ROCKFORD_115.0 (48367) CKT 1 |  | CHECK |  |
| L_48181LATAH-48427TEKOAC1 | OPEN Branch LATAH_115.0 (48181) TO TEKOA_115.0 (48427) CKT 1 |  | CHECK |  |
| L_48183LEON-48243MOSCCITYC1 | OPEN Branch LEON_115.0 (48183) TO MOSCCITY_115.0 (48243) CKT 1 |  | CHECK |  |
| L_48183LEON-48253NLEWISTC1 | OPEN Branch LEON_115.0 (48183) TO N LEWIST_115.0 (48253) CKT 1 |  | CHECK |  |
| L_48185LIBTYLK-48299OPPORTUNC1 | OPEN Branch LIBTYLK_115.0 (48185) TO OPPORTUN_115.0 (48299) CKT 1 |  | CHECK |  |
| L_48187LIND-47073RALSTONBC1 | OPEN Branch LIND_115.0 (48187) TO RALSTONB_115.0 (47073) CKT 1 |  | CHECK |  |
| L_48187LIND-48365RITZVILLC1 | OPEN Branch LIND_115.0 (48187) TO RITZVILL_115.0 (48365) CKT 1 |  | CHECK |  |
| L_48187LIND-48375ROXBOROC1 | OPEN Branch LIND_115.0 (48187) TO ROXBORO_115.0 (48375) CKT 1 |  | CHECK |  |
| L_48194LOCUST-48237MILLWOODC1 | OPEN Branch LOCUST_115.0 (48194) TO MILLWOOD_115.0 (48237) CKT 1 |  | CHECK |  |
| L_48195LOLO-48345POUNDTAPC1 | OPEN Branch LOLO_115.0 (48195) TO POUNDTAP_115.0 (48345) CKT 1 |  | CHECK |  |
| L_48195LOLO-48423SWEETWTRC1 | OPEN Branch LOLO_115.0 (48195) TO SWEETWTR_115.0 (48423) CKT 1 |  | CHECK |  |
| L_48195LOLO-48429TENTHSTWC1 | OPEN Branch LOLO_115.0 (48195) TO TENTHSTW_115.0 (48429) CKT 1 |  | CHECK |  |
| L_48197LOLO-48512DRYCREEKC1 | OPEN Branch DRYCREEK_230.0 (48512) TO LOLO_230.0 (48197) CKT 1 |  | CHECK |  |
| L_48197LOLO-60278IMNAHAC1 | OPEN Branch LOLO_230.0 (48197) TO IMNAHA_230.0 (60278) CKT 1 |  | CHECK |  |
| L_48199LONGLAKA-48201LONGLAKBC1 | OPEN Branch LONGLAKA_115.0 (48199) TO LONGLAKB_115.0 (48201) CKT 1 |  | CHECK |  |
| L_48215LUCKYF-48217LUCKYFTPC1 | OPEN Branch LUCKY F_115.0 (48215) TO LUCKYFTP_115.0 (48217) CKT 1 |  | CHECK |  |
| L_48219LYONSTND-48371ROSSPARKC1 | OPEN Branch LYONSTND_115.0 (48219) TO ROSSPARK_115.0 (48371) CKT 1 |  | CHECK |  |
| L_48221MARENGO-47073RALSTONBC1 | OPEN Branch MARENGO_115.0 (48221) TO RALSTONB_115.0 (47073) CKT 1 |  | CHECK |  |
| L_48225METRO-48339POSTSTRTC1 | OPEN Branch METRO_115.0 (48225) TO POSTSTRT_115.0 (48339) CKT 1 |  | CHECK |  |
| L_48225METRO-48421SUNSETC1 | OPEN Branch METRO_115.0 (48225) TO SUNSET_115.0 (48421) CKT 1 |  | CHECK |  |
| L_48231MICATAP-48367ROCKFORDC1 | OPEN Branch MICA TAP_115.0 (48231) TO ROCKFORD_115.0 (48367) CKT 1 |  | CHECK |  |
| L_48233MILAN-48235MILANTPC1 | OPEN Branch MILAN_115.0 (48233) TO MILAN TP_115.0 (48235) CKT 1 |  | CHECK |  |
| L_48235MILANTP-41099TUMTUMC1 | OPEN Branch MILAN TP_115.0 (48235) TO TUM TUM_115.0 (41099) CKT 1 |  | CHECK |  |
| L_48239MISSION-48315PINECRKC1 | OPEN Branch MISSION_115.0 (48239) TO PINE CRK_115.0 (48315) CKT 1 |  | CHECK |  |
| L_48243MOSCCITY-48245MOSCITYTC1 | OPEN Branch MOSCCITY_115.0 (48243) TO MOSCITYT_115.0 (48245) CKT 1 |  | CHECK |  |
| L_48245MOSCITYT-48247MOSCOWC1 | OPEN Branch MOSCITYT_115.0 (48245) TO MOSCOW_115.0 (48247) CKT 1 |  | CHECK |  |
| L_48245MOSCITYT-48413SPULLMANC1 | OPEN Branch MOSCITYT_115.0 (48245) TO SPULLMAN_115.0 (48413) CKT 1 |  | CHECK |  |
| L_48247MOSCOW-48273NMOSCOWC1 | OPEN Branch MOSCOW_115.0 (48247) TO NMOSCOW_115.0 (48273) CKT 1 |  | CHECK |  |
| L_48247MOSCOW-48445VIOLAC1 | OPEN Branch MOSCOW_115.0 (48247) TO VIOLA_115.0 (48445) CKT 1 |  | CHECK |  |
| L_48255NLEWIST-48385SHAWNEEC1 | OPEN Branch N LEWIST_230.0 (48255) TO SHAWNEE_230.0 (48385) CKT 1 |  | CHECK |  |
| L_48255NLEWIST-48512DRYCREEKC1 | OPEN Branch DRYCREEK_230.0 (48512) TO N LEWIST_230.0 (48255) CKT 1 |  | CHECK |  |
| L_48258NEWPORTT-48298OLDTOWNC1 | OPEN Branch NEWPORTT_115.0 (48258) TO OLDTOWN_115.0 (48298) CKT 1 |  | CHECK |  |
| L_48261NEZPERCE-48303OROFINOC1 | OPEN Branch NEZPERCE_115.0 (48261) TO OROFINO_115.0 (48303) CKT 1 |  | CHECK |  |
| L_48271NINTHCNT-48431THIRHACHC1 | OPEN Branch NINTHCNT_115.0 (48271) TO THIRHACH_115.0 (48431) CKT 1 |  | CHECK |  |
| L_48277NORTHEAS-48449WAIKIKITC1 | OPEN Branch NORTHEAS_115.0 (48277) TO WAIKIKIT_115.0 (48449) CKT 1 |  | CHECK |  |
| L_48279NORTHWES-48461WESTC1 | OPEN Branch NORTHWES_115.0 (48279) TO WEST_115.0 (48461) CKT 1 |  | CHECK |  |
| L_48281NOXON-40787NOXONBPAC1 | OPEN Branch NOXON_230.0 (48281) TO NOXONBPA_230.0 (40787) CKT 1 |  | CHECK |  |
| L_48281NOXON-48317PINECRKC1 | OPEN Branch NOXON_230.0 (48281) TO PINE CRK_230.0 (48317) CKT 1 |  | CHECK |  |
| L_48281NOXON-48317PINECRKC1 | OPEN Gen NOXON34_ 14.4 (48287) #3 |  | CHECK |  |
| L_48281NOXON-48317PINECRKC1 | OPEN Gen NOXON34_ 14.4 (48287) #4 |  | CHECK |  |
| L_48289NOXONCON-41091TROUTCRC1 | OPEN Branch NOXONCON_230.0 (48289) TO TROUT CR_230.0 (41091) CKT 1 |  | CHECK |  |
| L_48291NPULLMAN-48383SHAWNEEC1 | OPEN Branch NPULLMAN_115.0 (48291) TO SHAWNEE_115.0 (48383) CKT 1 |  | CHECK |  |
| L_48297OGARA-48315PINECRKC1 | OPEN Branch OGARA_115.0 (48297) TO PINE CRK_115.0 (48315) CKT 1 |  | CHECK |  |
| L_48297OGARA-48323PLUMMERC1 | OPEN Branch OGARA_115.0 (48297) TO PLUMMER_115.0 (48323) CKT 1 |  | CHECK |  |
| L_48297OGARA-48417STMARIESC1 | OPEN Branch OGARA_115.0 (48297) TO STMARIES_115.0 (48417) CKT 1 |  | CHECK |  |
| L_48298OLDTOWN-48300OLDTOWNAC1 | OPEN Branch OLDTOWN_115.0 (48298) TO OLDTOWNA_115.0 (48300) CKT 1 |  | CHECK |  |
| L_48299OPPORTUN-41107VALYWAYC1 | OPEN Branch OPPORTUN_115.0 (48299) TO VALY WAY_115.0 (41107) CKT 1 |  | CHECK |  |
| L_48303OROFINO-48459WEIPPEC1 | OPEN Branch OROFINO_115.0 (48303) TO WEIPPE_115.0 (48459) CKT 1 |  | CHECK |  |
| L_48305OSBURN-48315PINECRKC1 | OPEN Branch OSBURN_115.0 (48305) TO PINE CRK_115.0 (48315) CKT 1 |  | CHECK |  |
| L_48305OSBURN-48453WALLACEC1 | OPEN Branch OSBURN_115.0 (48305) TO WALLACE_115.0 (48453) CKT 1 |  | CHECK |  |
| L_48307OTHELLO-48308LEE&REYNC1 | OPEN Branch LEE&REYN_115.0 (48308) TO OTHELLO_115.0 (48307) CKT 1 |  | CHECK |  |
| L_48307OTHELLO-48309OTHELOSSC1 | OPEN Branch OTHELLO_115.0 (48307) TO OTHELOSS_115.0 (48309) CKT 1 |  | CHECK |  |
| L_48308LEE&REYN-48455WARDENAC1 | OPEN Branch LEE&REYN_115.0 (48308) TO WARDEN A_115.0 (48455) CKT 1 |  | CHECK |  |
| L_48309OTHELOSS-48393SOTHELOTC1 | OPEN Branch OTHELOSS_115.0 (48309) TO SOTHELOT_115.0 (48393) CKT 1 |  | CHECK |  |
| L_48309OTHELOSS-48455WARDENAC1 | OPEN Branch OTHELOSS_115.0 (48309) TO WARDEN A_115.0 (48455) CKT 1 |  | CHECK |  |
| L_48311OTIS-48185LIBTYLKC1 | OPEN Branch OTIS_115.0 (48311) TO LIBTYLK_115.0 (48185) CKT 1 |  | CHECK |  |
| L_48313PALOUSE-48445VIOLAC1 | OPEN Branch PALOUSE_115.0 (48313) TO VIOLA_115.0 (48445) CKT 1 |  | CHECK |  |
| L_48319PLEASANT-48355RATHDRUMC1 | OPEN Branch PLEASANT_115.0 (48319) TO RATHDRUM_115.0 (48355) CKT 1 |  | CHECK |  |
| L_48325PLUMMERG-48327PLUMMWEAC1 | OPEN Branch PLUMMERG_ 13.8 (48325) TO PLUMMWEA_ 13.8 (48327) CKT 1 |  | CHECK |  |
| L_48339POSTSTRT-48431THIRHACHC1 | OPEN Branch POSTSTRT_115.0 (48339) TO THIRHACH_115.0 (48431) CKT 1 |  | CHECK |  |
| L_48343POUNDLNE-48345POUNDTAPC1 | OPEN Branch POUNDLNE_115.0 (48343) TO POUNDTAP_115.0 (48345) CKT 1 |  | CHECK |  |
| L_48343POUNDLNE-48510DRYCREEKC1 | OPEN Branch DRYCREEK_115.0 (48510) TO POUNDLNE_115.0 (48343) CKT 1 |  | CHECK |  |
| L_48345POUNDTAP-48389SLEWISTC1 | OPEN Branch POUNDTAP_115.0 (48345) TO SLEWIST_115.0 (48389) CKT 1 |  | CHECK |  |
| L_48351RATHBUS1-48355RATHDRUMC1 | OPEN Branch RATHBUS1_115.0 (48351) TO RATHDRUM_115.0 (48355) CKT 1 |  | CHECK |  |
| L_48353RATHBUS2-48356RATHDRMEC1 | OPEN Branch RATHBUS2_115.0 (48353) TO RATHDRME_115.0 (48356) CKT 1 |  | CHECK |  |
| L_48356RATHDRME-48355RATHDRUMC1 | OPEN Branch RATHDRME_115.0 (48356) TO RATHDRUM_115.0 (48355) CKT 1 |  | CHECK |  |
| L_48357RATHDRUM-48524BOULDERC1 | OPEN Branch BOULDER_230.0 (48524) TO RATHDRUM_230.0 (48357) CKT 1 |  | CHECK |  |
| L_48365RITZVILL-48411SPRAGUEC1 | OPEN Branch RITZVILL_115.0 (48365) TO SPRAGUE_115.0 (48411) CKT 1 |  | CHECK |  |
| L_48369ROSALIA-48397SPANGLEC1 | OPEN Branch ROSALIA_115.0 (48369) TO SPANGLE_115.0 (48397) CKT 1 |  | CHECK |  |
| L_48371ROSSPARK-48431THIRHACHC1 | OPEN Branch ROSSPARK_115.0 (48371) TO THIRHACH_115.0 (48431) CKT 1 |  | CHECK |  |
| L_48373ROUNDLKT-48419STRATFRDC1 | OPEN Branch ROUNDLKT_115.0 (48373) TO STRATFRD_115.0 (48419) CKT 1 |  | CHECK |  |
| L_48375ROXBORO-48455WARDENAC1 | OPEN Branch ROXBORO_115.0 (48375) TO WARDEN A_115.0 (48455) CKT 1 |  | CHECK |  |
| L_48381SEVENTAP-48447WAIKIKIC1 | OPEN Branch SEVENTAP_115.0 (48381) TO WAIKIKI_115.0 (48447) CKT 1 |  | CHECK |  |
| L_48388SILVRLK2-48387SILVRLAKC1 | OPEN Branch SILVRLAK_115.0 (48387) TO SILVRLK2_115.0 (48388) CKT 1 |  | CHECK |  |
| L_48391SOTHELLO-48393SOTHELOTC1 | OPEN Branch SOTHELLO_115.0 (48391) TO SOTHELOT_115.0 (48393) CKT 1 |  | CHECK |  |
| L_48393SOTHELOT-48425TAUNTONC1 | OPEN Branch SOTHELOT_115.0 (48393) TO TAUNTON_115.0 (48425) CKT 1 |  | CHECK |  |
| L_48395SOUTHEAS-48421SUNSETC1 | OPEN Branch SOUTHEAS_115.0 (48395) TO SUNSET_115.0 (48421) CKT 1 |  | CHECK |  |
| L_48401SPIRITLK-48403SPIRITLTC1 | OPEN Branch SPIRITLK_115.0 (48401) TO SPIRITLT_115.0 (48403) CKT 1 |  | CHECK |  |
| L_48405SPKINDPK-48520BOULDERWC1 | OPEN Branch BOULDERW_115.0 (48520) TO SPKINDPK_115.0 (48405) CKT 1 |  | CHECK |  |
| L_48409SPKWASTE-48461WESTC1 | OPEN Branch SPKWASTE_115.0 (48409) TO WEST_115.0 (48461) CKT 1 |  | CHECK |  |
| L_48419STRATFRD-46447SUMERFALC1 | OPEN Branch STRATFRD_115.0 (48419) TO SUMERFAL_115.0 (46447) CKT 1 |  | CHECK |  |
| L_48419STRATFRD-48471WILSNCKTC1 | OPEN Branch STRATFRD_115.0 (48419) TO WILSNCKT_115.0 (48471) CKT 1 |  | CHECK |  |
| L_48430TERRVIEW-48273NMOSCOWC1 | OPEN Branch NMOSCOW_115.0 (48273) TO TERRVIEW_115.0 (48430) CKT 1 |  | CHECK |  |
| L_48430TERRVIEW-48291NPULLMANC1 | OPEN Branch TERRVIEW_115.0 (48430) TO NPULLMAN_115.0 (48291) CKT 1 |  | CHECK |  |
| L_48443VANTAVA-45327WALAWALAC1 | OPEN Branch VANT AVA_230.0 (48443) TO WALAWALA_230.0 (45327) CKT 1 |  | CHECK |  |
| L_48443VANTAVA-46169WANAPUMC1 | OPEN Branch VANT AVA_230.0 (48443) TO WANAPUM_230.0 (46169) CKT 1 |  | CHECK |  |
| L_48447WAIKIKI-48449WAIKIKITC1 | OPEN Branch WAIKIKI_115.0 (48447) TO WAIKIKIT_115.0 (48449) CKT 1 |  | CHECK |  |
| L_48451WALAAVA-45327WALAWALAC1 | OPEN Branch WALA AVA_230.0 (48451) TO WALAWALA_230.0 (45327) CKT 1 |  | CHECK |  |
| L_48451WALAAVA-48512DRYCREEKC1 | OPEN Branch DRYCREEK_230.0 (48512) TO WALA AVA_230.0 (48451) CKT 1 |  | CHECK |  |
| L_48451WALAAVA-48512DRYCREEKC1 | SET INJECTION GROUP HOPKINS RIDGE TO 120 MW |  | CHECK |  |
| L_48451WALAAVA-48512DRYCREEKC1 | SET INJECTION GROUP NINE MILE WIND TO 80 MW |  | CHECK |  |
| L_48455WARDENA-46117WARDENTC1 | OPEN Branch WARDEN A_115.0 (48455) TO WARDEN T_115.0 (46117) CKT 1 |  | CHECK |  |
| L_48463WEST-41275WESTBPA1C1 | OPEN Branch WEST_230.0 (48463) TO WESTBPA1_230.0 (41275) CKT 1 |  | CHECK |  |
| L_48463WEST-41276WESTBPA2C1 | OPEN Branch WEST_230.0 (48463) TO WESTBPA2_230.0 (41276) CKT 1 |  | CHECK |  |
| L_48467WILBUR-48469WILBURTC1 | OPEN Branch WILBUR_115.0 (48467) TO WILBURT_115.0 (48469) CKT 1 |  | CHECK |  |
| L_48471WILSNCKT-46129WILSONCKC1 | OPEN Branch WILSNCKT_115.0 (48471) TO WILSONCK_115.0 (46129) CKT 1 |  | CHECK |  |
| L_48475CLWTR1-48476CLWTR2C1 | OPEN Branch CLWTR1_ 34.5 (48475) TO CLWTR2_ 34.5 (48476) CKT 1 |  | CHECK |  |
| L_48475CLWTR1-48481CLWTR7C1 | OPEN Branch CLWTR1_ 34.5 (48475) TO CLWTR7_ 34.5 (48481) CKT 1 |  | CHECK |  |
| L_48476CLWTR2-48477CLWTR3C1 | OPEN Branch CLWTR2_ 34.5 (48476) TO CLWTR3_ 34.5 (48477) CKT 1 |  | CHECK |  |
| L_48477CLWTR3-48478CLWTR4C1 | OPEN Branch CLWTR3_ 34.5 (48477) TO CLWTR4_ 34.5 (48478) CKT 1 |  | CHECK |  |
| L_48478CLWTR4-48479CLWTR5C1 | OPEN Branch CLWTR4_ 34.5 (48478) TO CLWTR5_ 34.5 (48479) CKT 1 |  | CHECK |  |
| L_48479CLWTR5-48480CLWTR6C1 | OPEN Branch CLWTR5_ 34.5 (48479) TO CLWTR6_ 34.5 (48480) CKT 1 |  | CHECK |  |
| L_48480CLWTR6-48481CLWTR7C1 | OPEN Branch CLWTR6_ 34.5 (48480) TO CLWTR7_ 34.5 (48481) CKT 1 |  | CHECK |  |
| L_48490CWBUS1-48492CWBUS3C1 | OPEN Branch CWBUS1_ 12.0 (48490) TO CWBUS3_ 12.0 (48492) CKT 1 |  | CHECK |  |
| L_48491CWBUS2-48493CWBUS4C1 | OPEN Branch CWBUS2_ 12.0 (48491) TO CWBUS4_ 12.0 (48493) CKT 1 |  | CHECK |  |
| L_48494CWBUS5-48496CWBUS7C1 | OPEN Branch CWBUS5_ 12.0 (48494) TO CWBUS7_ 12.0 (48496) CKT 1 |  | CHECK |  |
| L_48495CWBUS6-48497CWBUS8C1 | OPEN Branch CWBUS6_ 12.0 (48495) TO CWBUS8_ 12.0 (48497) CKT 1 |  | CHECK |  |
| L_48510DRYCREEK-48113DRYGULCHC1 | OPEN Branch DRYCREEK_115.0 (48510) TO DRYGULCH_115.0 (48113) CKT 1 |  | CHECK |  |
| L_48510DRYCREEK-48514CRCHFELDC1 | OPEN Branch DRYCREEK_115.0 (48510) TO CRCHFELD_115.0 (48514) CKT 1 |  | CHECK |  |
| L_48520BOULDERW-48021BARKERC1 | OPEN Branch BOULDERW_115.0 (48520) TO BARKER_115.0 (48021) CKT 1 |  | CHECK |  |
| L_48520BOULDERW-48311OTISC1 | OPEN Branch BOULDERW_115.0 (48520) TO OTIS_115.0 (48311) CKT 1 |  | CHECK |  |
| L_48522BOULDERE-48165IRVINC1 | OPEN Branch BOULDERE_115.0 (48522) TO IRVIN_115.0 (48165) CKT 1 |  | CHECK |  |
| L_48522BOULDERE-48520BOULDERWC1 | OPEN Branch BOULDERE_115.0 (48522) TO BOULDERW_115.0 (48520) CKT 1 |  | CHECK |  |
| L_50822NLYPHS-40145BOUNDARYC1 | OPEN Branch NLYPHS_230.0 (50822) TO BOUNDARY_230.0 (40145) CKT 1 |  | CHECK |  |
| L_52219WAN230-40145BOUNDARYC1 | Unlinked Action: BRANCH 52219 40145 1 OPEN |  | CHECK |  |
| L_62085CROWCRB-48055BURKAVABC1 | Unlinked Action: BRANCH 62085 48055 1 OPEN |  | CHECK |  |
| L_62086THOMSON-48053BURKAVAAC1 | Unlinked Action: BRANCH 62086 48053 1 OPEN |  | CHECK |  |
| L_Addy - Bell 230 & Addy - Bell 115 (BPA) | OPEN Bus LOON LK_115.0 (48213) |  | CHECK | Addy - Bell 115 |
| L_Addy - Bell 230 & Addy - Bell 115 (BPA) | OPEN Bus CLAYTON_115.0 (40245) |  | CHECK | Addy - Bell 115 |
| L_Addy - Bell 230 & Addy - Bell 115 (BPA) | OPEN Bus DEER PRK_115.0 (40337) |  | CHECK | Addy - Bell 115 |
| L_Addy - Bell 230 & Addy - Bell 115 (BPA) | OPEN Bus MILAN TP_115.0 (48235) |  | CHECK | Addy - Bell 115 |
| L_Addy - Bell 230 & Addy - Bell 115 (BPA) | OPEN Bus MILAN_115.0 (48233) |  | CHECK | Addy - Bell 115 |
| L_Addy - Bell 230 & Addy - Bell 115 (BPA) | OPEN Bus TUM TUM_115.0 (41099) |  | CHECK | Addy - Bell 115 |
| L_Addy - Bell 230 & Addy - Bell 115 (BPA) | OPEN Bus HALFMOON_115.0 (40495) |  | CHECK | Addy - Bell 115 |
| L_Addy - Bell 230 & Addy - Bell 115 (BPA) | OPEN Bus COLBERTT_115.0 (40255) |  | CHECK | Addy - Bell 115 |
| L_Addy - Bell 230 & Addy - Bell 115 (BPA) | OPEN Bus COLBERT_115.0 (48079) |  | CHECK | Addy - Bell 115 |
| L_Addy - Bell 230 & Addy - Bell 115 (BPA) | OPEN Bus MEAD TAP_115.0 (40730) |  | CHECK | Addy - Bell 115 |
| L_Addy - Bell 230 & Addy - Bell 115 (BPA) | OPEN Bus MEAD SUB_115.0 (48222) |  | CHECK | Addy - Bell 115 |
| L_Addy - Bell 230 & Addy - Bell 115 (BPA) | OPEN MultiSectionLine ADDY 2_230.0 (40021) TO BELL S3_230.0 (40090) CKT 1 |  | CHECK | Addy - Bell 230 |
| L_Addy - Bell 230 & Addy - Bell 115 (BPA) | OPEN Bus BOUNDPH6_230.0 (46486) | SoB>650 | CHECK |  |
| L_Addy - Bell 230 & Addy - Bell 115 (BPA) | OPEN Bus BOUNDPH5_230.0 (46484) | SoB>650 | CHECK |  |
| L_Beacon S - Boulder & Beacon N - Rathdrum 230 (AVA) | OPEN Branch BEACON S_230.0 (48031) TO BOULDER_230.0 (48524) CKT 1 |  | CHECK |  |
| L_Beacon S - Boulder & Beacon N - Rathdrum 230 (AVA) | OPEN Branch BEACON N_230.0 (48025) TO RATHDRUM_230.0 (48357) CKT 2 |  | CHECK |  |
| L_Beacon S - Boulder 230 & Beacon N - Boulder 115 (AVA) | OPEN Branch BEACON S_230.0 (48031) TO BOULDER_230.0 (48524) CKT 1 |  | CHECK |  |
| L_Beacon S - Boulder 230 & Beacon N - Boulder 115 (AVA) | OPEN Bus SPKINDPK_115.0 (48405) |  | CHECK | Beacon - Boulder #1 115 |
| L_Beacon S - Boulder 230 & Beacon S - Boulder 115 (AVA) | OPEN Branch BEACON S_230.0 (48031) TO BOULDER_230.0 (48524) CKT 1 |  | CHECK |  |
| L_Beacon S - Boulder 230 & Beacon S - Boulder 115 (AVA) | OPEN Bus LOCUST_115.0 (48194) |  | CHECK | Beacon - Boulder #2 115 |
| L_Beacon S - Boulder 230 & Beacon S - Boulder 115 (AVA) | OPEN Bus MILLWOOD_115.0 (48237) |  | CHECK | Beacon - Boulder #2 115 |
| L_Beacon S - Boulder 230 & Beacon S - Boulder 115 (AVA) | OPEN Bus I.E.PAPR_115.0 (48163) |  | CHECK | Beacon - Boulder #2 115 |
| L_Beacon S - Boulder 230 & Beacon S - Boulder 115 (AVA) | OPEN Bus IRVIN_115.0 (48165) |  | CHECK | Beacon - Boulder #2 115 |
| L_Bell - Coulee #3 & #5 230 (BPA) | OPEN MultiSectionLine BELL S2_230.0 (40088) TO COULEES3_230.0 (41358) CKT 5 |  | CHECK |  |
| L_Bell - Coulee #3 & #5 230 (BPA) | OPEN MultiSectionLine BELL S3_230.0 (40090) TO COULEES1_230.0 (41356) CKT 3 |  | CHECK |  |
| L_Bell - Coulee 500 & Bell - Westside 230 (BPA) | OPEN Bus WESTBPA1_230.0 (41275) |  | CHECK | Bell - Westside 230 |
| L_Bell - Coulee 500 & Bell - Westside 230 (BPA) | OPEN Branch BELL BPA_500.0 (40091) TO COULE R1_500.0 (40288) CKT 6 |  | CHECK | Bell - Coulee 500 Ckt6 |
| L_Bell - Coulee 500 & Bell - Westside 230 (BPA) | OPEN Load MILCTYDC_230.0 (63010) #D1 |  | CHECK |  |
| L_Bell - Coulee 500 & Bell - Westside 230 (BPA) | OPEN Bus LIB PH1_230.0 (44200) | WMH > 1000 | CHECK |  |
| L_Bell - Coulee 500 & Bell - Westside 230 (BPA) | OPEN Bus LIB PH2_230.0 (44201) | WMH > 1000 | CHECK |  |
| L_Bell - Coulee 500 & Westside - Coulee 230 (BPA) | OPEN Bus WESTBPA2_230.0 (41276) |  | CHECK | Westside - Coulee 230 |
| L_Bell - Coulee 500 & Westside - Coulee 230 (BPA) | OPEN Load MILCTYDC_230.0 (63010) #D1 |  | CHECK |  |
| L_Bell - Coulee 500 & Westside - Coulee 230 (BPA) | OPEN Branch BELL BPA_500.0 (40091) TO COULE R1_500.0 (40288) CKT 6 |  | CHECK | Bell - Coulee 500 Ckt 6 |
| L_Bell - Coulee 500 & Westside - Coulee 230 (BPA) | OPEN Bus LIB PH1_230.0 (44200) | WMH > 1000 | CHECK |  |
| L_Bell - Coulee 500 & Westside - Coulee 230 (BPA) | OPEN Bus LIB PH2_230.0 (44201) | WMH > 1000 | CHECK |  |
| L_Bell - Sacheen & Bell - Usk 230 (BPA) | OPEN Branch BELL S1_230.0 (40086) TO SACHEEN_230.0 (40909) CKT 1 |  | CHECK | Bell - Sacheen 230 Ckt 1 |
| L_Bell - Sacheen & Bell - Usk 230 (BPA) | OPEN Branch BELL S2_230.0 (40088) TO USK_230.0 (47091) CKT 1 |  | CHECK | Bell - USK 230 Ckt 1 |
| L_Bell - Sacheen & Bell - Usk 230 (BPA) | OPEN Bus BOUNDPH6_230.0 (46486) | SoB>650 | CHECK |  |
| L_Bell - Sacheen & Bell - Usk 230 (BPA) | OPEN Bus BOUNDPH5_230.0 (46484) | SoB>650 | CHECK |  |
| L_Bell - Westside & Bell - Coulee #3 230 (AVA/BPA) | OPEN Bus WESTBPA1_230.0 (41275) |  | CHECK | Bell - Westside |
| L_Bell - Westside & Bell - Coulee #3 230 (AVA/BPA) | OPEN MultiSectionLine BELL S3_230.0 (40090) TO COULEES1_230.0 (41356) CKT 3 |  | CHECK |  |
| L_Bell - Westside 230 kV (BPA) | OPEN Branch BELL S1_230.0 (40086) TO WESTBPA1_230.0 (41275) CKT 1 |  | CHECK |  |
| L_Bell S3 - Lancaster & Beacon N - Rathdrum 230 (AVA/BPA) | OPEN Branch BEACON N_230.0 (48025) TO RATHDRUM_230.0 (48357) CKT 2 |  | CHECK | Beacon - Rathdrum 230 |
| L_Bell S3 - Lancaster & Beacon N - Rathdrum 230 (AVA/BPA) | OPEN Gen LANCAS G_ 18.0 (47568) #1 |  | CHECK |  |
| L_Bell S3 - Lancaster & Beacon N - Rathdrum 230 (AVA/BPA) | OPEN Gen LANCAS S_ 13.8 (47569) #1 |  | CHECK |  |
| L_Bell S3 - Lancaster & Beacon N - Rathdrum 230 (AVA/BPA) | OPEN MultiSectionLine BELL S3_230.0 (40090) TO LANCASTR_230.0 (40624) CKT 1 |  | CHECK | Bell S3 - Lancaster 230 |
| L_Bell S3 - Lancaster 230 & Bell - Taft 500 (BPA) | OPEN Gen LANCAS G_ 18.0 (47568) #1 |  | CHECK |  |
| L_Bell S3 - Lancaster 230 & Bell - Taft 500 (BPA) | OPEN Gen LANCAS S_ 13.8 (47569) #1 |  | CHECK |  |
| L_Bell S3 - Lancaster 230 & Bell - Taft 500 (BPA) | OPEN Load MILCTYDC_230.0 (63010) #D1 |  | CHECK |  |
| L_Bell S3 - Lancaster 230 & Bell - Taft 500 (BPA) | OPEN Shunt GARRISON_500.0 (40459) #r |  | CHECK |  |
| L_Bell S3 - Lancaster 230 & Bell - Taft 500 (BPA) | OPEN MultiSectionLine BELL S3_230.0 (40090) TO LANCASTR_230.0 (40624) CKT 1 |  | CHECK | Bell S3 - Lancaster 230 |
| L_Bell S3 - Lancaster 230 & Bell - Taft 500 (BPA) | OPEN MultiSectionLine BELL SC_500.0 (40096) TO TAFT_500.0 (41057) CKT 1 |  | CHECK | BellBPA - Taft 500 |
| L_Bell S3 - Lancaster 230 & Bell - Taft 500 (BPA) | OPEN Bus LIB PH1_230.0 (44200) | WMH > 1000 | CHECK |  |
| L_Bell S3 - Lancaster 230 & Bell - Taft 500 (BPA) | OPEN Bus LIB PH2_230.0 (44201) | WMH > 1000 | CHECK |  |
| L_Boulder - Otis 115 1 & 2 (AVA) | OPEN Branch BOULDERW_115.0 (48520) TO OTIS_115.0 (48311) CKT 1 |  | CHECK |  |
| L_Boulder - Otis 115 1 & 2 (AVA) | OPEN Bus BARKER_115.0 (48021) |  | CHECK |  |
| L_Boulder - Rathdrum & Beacon N - Rathdrum 230 (AVA) | OPEN Branch BOULDER_230.0 (48524) TO RATHDRUM_230.0 (48357) CKT 1 |  | CHECK |  |
| L_Boulder - Rathdrum & Beacon N - Rathdrum 230 (AVA) | OPEN Branch BEACON N_230.0 (48025) TO RATHDRUM_230.0 (48357) CKT 2 |  | CHECK |  |
| L_Boulder - Rathdrum 230 & Boulder - Rathdrum 115 (AVA) | OPEN Branch BOULDER_230.0 (48524) TO RATHDRUM_230.0 (48357) CKT 1 |  | CHECK |  |
| L_Boulder - Rathdrum 230 & Boulder - Rathdrum 115 (AVA) | OPEN Bus MOAB_115.0 (47511) |  | CHECK | Boulder - Rathdrum 115 |
| L_Boulder - Rathdrum 230 & Boulder - Rathdrum 115 (AVA) | OPEN Bus PLEASANT_115.0 (48319) |  | CHECK | Boulder - Rathdrum 115 |
| L_Bridger - Goshen & Bridger - Kinport 345 | OPEN Gen BRIDGER1_ 22.0 (60086) #1 |  | CHECK |  |
| L_Bridger - Goshen & Bridger - Kinport 345 | OPEN Gen BRIDGER2_ 22.0 (60087) #1 |  | CHECK |  |
| L_Bridger - Goshen & Bridger - Kinport 345 | SET SWITCHED SHUNT AT BUS GOSHEN_161.0 (65670) TO 100 MVR |  | CHECK |  |
| L_Bridger - Goshen & Bridger - Kinport 345 | OPEN MultiSectionLine BRIDGER_345.0 (60085) TO KINPORT_345.0 (60190) CKT 1 |  | CHECK |  |
| L_Brownlee - Hells Canyon & Oxbow - Lolo 230 | OPEN Branch HELLSCYN_230.0 (60150) TO BROWNLEE_230.0 (60095) CKT 1 |  | CHECK |  |
| L_Brownlee - Hells Canyon & Oxbow - Lolo 230 | OPEN Gen HELSCYN1_ 14.4 (60151) #1 |  | CHECK |  |
| L_Brownlee - Hells Canyon & Oxbow - Lolo 230 | OPEN Branch LOLO_230.0 (48197) TO IMNAHA_230.0 (60278) CKT 1 |  | CHECK |  |
| L_Brownlee - Hells Canyon & Oxbow - Lolo 230 | OPEN MultiSectionLine OXBOW_230.0 (60275) TO IMNAHA_230.0 (60278) CKT 1 |  | CHECK |  |
| L_Brownlee - Oxbow #1 & Brownlee - Hells Canyon 230 | OPEN Branch OXBOW_230.0 (60275) TO BROWNLEE_230.0 (60095) CKT 1 |  | CHECK |  |
| L_Brownlee - Oxbow #1 & Brownlee - Hells Canyon 230 | OPEN Branch HELLSCYN_230.0 (60150) TO BROWNLEE_230.0 (60095) CKT 1 |  | CHECK |  |
| L_Brownlee - Oxbow #1 & Brownlee - Hells Canyon 230 | OPEN Gen HELSCYN1_ 14.4 (60151) #1 |  | CHECK |  |
| L_Brownlee - Quartz - LaGrande 230 (IDA) | OPEN Bus QUARTZTP_230.0 (60310) |  | CHECK |  |
| L_Cab Gorg - Rathdrum & Noxon - Lancaster 230 (AVA/BPA) | OPEN MultiSectionLine LANCASTR_230.0 (40624) TO NOXONBPA_230.0 (40787) CKT 1 |  | CHECK | NoxonBPA - Lancaster 230 |
| L_Cab Gorg - Rathdrum & Noxon - Lancaster 230 (AVA/BPA) | OPEN Bus LIB PH2_230.0 (44201) |  | CHECK |  |
| L_Cab Gorg - Rathdrum & Noxon - Lancaster 230 (AVA/BPA) | OPEN Bus LAKEVIEW_230.0 (48179) |  | CHECK | Cabinet - Rathdrum 230 |
| L_Cab Gorg - Rathdrum & Noxon - Lancaster 230 (AVA/BPA) | OPEN Gen NOXON12_ 14.4 (48285) #2 | WMH > 1450 | CHECK |  |
| L_Cab Gorg - Rathdrum & Noxon - Lancaster 230 (AVA/BPA) | OPEN Gen NOXON34_ 14.4 (48287) #4 | WMH > 1450 | CHECK |  |
| L_Cab Gorg - Rathdrum & Noxon - Lancaster 230 (AVA/BPA) | OPEN Gen NOXON34_ 14.4 (48287) #3 | WMH > 1450 | CHECK |  |
| L_Cab Gorg - Rathdrum & Noxon - Lancaster 230 (AVA/BPA) | OPEN Gen NOXON12_ 14.4 (48285) #1 | WMH > 1450 | CHECK |  |
| L_CDA - Ramsey & Ramsey - Rathdrum #2 115 (AVA) | OPEN Branch CDA_115.0 (48067) TO RAMSEY_115.0 (48349) CKT 1 |  | CHECK |  |
| L_CDA - Ramsey & Ramsey - Rathdrum #2 115 (AVA) | OPEN Bus HERN_115.0 (48155) |  | CHECK | Ramsey - Rathdrum #2 |
| L_CDA - Ramsey & Ramsey - Rathdrum #2 115 (AVA) | OPEN Bus HUETTER_115.0 (48159) |  | CHECK | Ramsey - Rathdrum #2 |
| L_CDA - Rathdrum & Pine St - Rathdrum 115 (AVA) | OPEN Bus HAYDEN_115.0 (48148) |  | CHECK | CDA - RAT |
| L_CDA - Rathdrum & Pine St - Rathdrum 115 (AVA) | OPEN Bus DALTONT_115.0 (48097) |  | CHECK | CDA - RAT |
| L_CDA - Rathdrum & Pine St - Rathdrum 115 (AVA) | OPEN Bus DALTON A_115.0 (48093) |  | CHECK | CDA - RAT |
| L_CDA - Rathdrum & Pine St - Rathdrum 115 (AVA) | OPEN Bus SCARCELO_115.0 (40953) |  | CHECK | Pine St - RAT |
| L_CDA - Rathdrum & Pine St - Rathdrum 115 (AVA) | OPEN Bus ATHOL_115.0 (40067) |  | CHECK | Pine St - RAT |
| L_CDA - Rathdrum & Pine St - Rathdrum 115 (AVA) | OPEN Bus SPIRITLT_115.0 (48403) |  | CHECK | Pine St - RAT |
| L_CDA - Rathdrum & Pine St - Rathdrum 115 (AVA) | OPEN Bus ATHOLTAP_115.0 (48017) |  | CHECK | Pine St - RAT |
| L_CDA - Rathdrum & Pine St - Rathdrum 115 (AVA) | OPEN Bus SPIRITLK_115.0 (48401) |  | CHECK | Pine St - RAT |
| L_CDA - Rathdrum & Pine St - Rathdrum 115 (AVA) | OPEN Bus HOODOO_115.0 (47505) |  | CHECK | Pine St - RAT |
| L_CDA - Rathdrum & Pine St - Rathdrum 115 (AVA) | OPEN Bus BLANCHRD_115.0 (48043) |  | CHECK | Pine St - RAT |
| L_CDA - Rathdrum & Pine St - Rathdrum 115 (AVA) | OPEN Bus NEWPORTT_115.0 (48258) |  | CHECK | Pine St - RAT |
| L_CDA - Rathdrum & Pine St - Rathdrum 115 (AVA) | OPEN Bus OLDTOWN_115.0 (48298) |  | CHECK | Pine St - RAT |
| L_CDA - Rathdrum & Pine St - Rathdrum 115 (AVA) | OPEN Bus OLDTOWNA_115.0 (48300) |  | CHECK | Pine St - RAT |
| L_Columbia Falls - Kalispel 115 (BPA) | OPEN Branch COL FALL_115.0 (40247) TO KALISPEL_115.0 (40589) CKT 1 |  | CHECK |  |
| L_Dworshak - Hatwai 500 kV (BPA) | OPEN Shunt GARRISON_500.0 (40459) #r |  | CHECK |  |
| L_Dworshak - Hatwai 500 kV (BPA) | OPEN Branch DWOR 1_ 13.8 (40361) TO DWOR 2_ 13.8 (40363) CKT 1 |  | CHECK |  |
| L_Dworshak - Hatwai 500 kV (BPA) | OPEN Branch DWORSHAK_500.0 (40369) TO HATWAI_500.0 (40521) CKT 1 |  | CHECK |  |
| L_Dworshak - Hatwai 500 kV (BPA) | OPEN Gen DWOR 3_ 13.8 (40365) #1 |  | ALWAYS |  |
| L_Dworshak - Hatwai 500 kV (BPA) | OPEN Gen DWOR 2_ 13.8 (40363) #1 |  | ALWAYS |  |
| L_Dworshak - Hatwai 500 kV (BPA) | OPEN Load MILCTYDC_230.0 (63010) #D1 |  | CHECK |  |
| L_Dworshak - Hatwai 500 kV (BPA) | OPEN Bus LIB PH2_230.0 (44201) | West MT Hydro > 1000 | CHECK |  |
| L_Dworshak - Hatwai 500 kV (BPA) | OPEN Bus LIB PH1_230.0 (44200) | West MT Hydro > 1000 | CHECK |  |
| L_Dworshak - Hatwai 500 kV (BPA) | OPEN Gen LANCAS S_ 13.8 (47569) #1 | WEST OF HATWAI > 3500 | CHECK |  |
| L_Dworshak - Hatwai 500 kV (BPA) | OPEN Gen LANCAS G_ 18.0 (47568) #1 | WEST OF HATWAI > 3500 | CHECK |  |
| L_Dworshak - Taft 500 kV (BPA) | OPEN MultiSectionLine DWORSHAK_500.0 (40369) TO TAFT_500.0 (41057) CKT 1 |  | CHECK |  |
| L_Dworshak - Taft 500 kV (BPA) | OPEN Shunt GARRISON_500.0 (40459) #r |  | CHECK |  |
| L_Dworshak - Taft 500 kV (BPA) | OPEN Load MILCTYDC_230.0 (63010) #D1 |  | CHECK |  |
| L_Dworshak - Taft 500 kV (BPA) | OPEN Bus LIB PH1_230.0 (44200) | West MT Hydro > 1000 | CHECK |  |
| L_Dworshak - Taft 500 kV (BPA) | OPEN Bus LIB PH2_230.0 (44201) | West MT Hydro > 1000 | CHECK |  |
| L_Dworshak - Taft 500 kV (BPA) | OPEN Gen LANCAS S_ 13.8 (47569) #1 | WEST OF HATWAI > 3500 | CHECK |  |
| L_Dworshak - Taft 500 kV (BPA) | OPEN Gen LANCAS G_ 18.0 (47568) #1 | WEST OF HATWAI > 3500 | CHECK |  |
| L_Flathead - Columbia Falls 230 (BPA) | OPEN Branch COL FALL_230.0 (40249) TO FLATHEAD_230.0 (40421) CKT 1 |  | CHECK |  |
| L_Flathead - Columbia Falls 230 (BPA) | OPEN Gen HUNGHR34_ 13.8 (40556) #3 |  | ALWAYS |  |
| L_Flathead - Columbia Falls 230 (BPA) | OPEN Gen HUNGHR34_ 13.8 (40556) #4 |  | ALWAYS |  |
| L_Flathead - Columbia Falls 230 (BPA) | OPEN Bus LIB PH2_230.0 (44201) |  | CHECK |  |
| L_Hatwai - Lower Granite 500 kV (BPA) | OPEN Gen DWOR 3_ 13.8 (40365) #1 |  | ALWAYS |  |
| L_Hatwai - Lower Granite 500 kV (BPA) | SET INJECTION GROUP NINE MILE WIND TO 85 MW |  | CHECK |  |
| L_Hatwai - Lower Granite 500 kV (BPA) | OPEN Gen DWOR 2_ 13.8 (40363) #1 |  | ALWAYS |  |
| L_Hatwai - Lower Granite 500 kV (BPA) | OPEN Branch HATWAI_500.0 (40521) TO LOW GRAN_500.0 (40679) CKT 1 |  | CHECK |  |
| L_Hatwai - Lower Granite 500 kV (BPA) | OPEN Branch DWOR 1_ 13.8 (40361) TO DWOR 2_ 13.8 (40363) CKT 1 |  | ALWAYS |  |
| L_Hatwai - Lower Granite 500 kV (BPA) | OPEN Load MILCTYDC_230.0 (63010) #D1 |  | CHECK |  |
| L_Hatwai - Lower Granite 500 kV (BPA) | OPEN Shunt GARRISON_500.0 (40459) #r |  | CHECK |  |
| L_Hatwai - Lower Granite 500 kV (BPA) | SET INJECTION GROUP HOPKINS RIDGE TO 135 MW |  | CHECK |  |
| L_Hatwai - Lower Granite 500 kV (BPA) | OPEN Bus LIB PH2_230.0 (44201) | West MT Hydro > 1000 | CHECK |  |
| L_Hatwai - Lower Granite 500 kV (BPA) | OPEN Bus LIB PH1_230.0 (44200) | West MT Hydro > 1000 | CHECK |  |
| L_Hatwai - Lower Granite 500 kV (BPA) | OPEN Gen LANCAS S_ 13.8 (47569) #1 | WEST OF HATWAI > 3500 | CHECK |  |
| L_Hatwai - Lower Granite 500 kV (BPA) | OPEN Gen LANCAS G_ 18.0 (47568) #1 | WEST OF HATWAI > 3500 | CHECK |  |
| L_Hatwai - N Lewiston 230 & Clearwater - Lolo #1 115 (AVA) | OPEN Branch HATWAI_230.0 (40519) TO N LEWIST_230.0 (48255) CKT 1 |  | CHECK |  |
| L_Hatwai - N Lewiston 230 & Clearwater - Lolo #1 115 (AVA) | OPEN Branch CLEARWTR_115.0 (48075) TO LOLO_115.0 (48195) CKT 1 |  | CHECK |  |
| L_Hatwai - N Lewiston 230 & Clearwater - N Lewiston 115 | OPEN Branch HATWAI_230.0 (40519) TO N LEWIST_230.0 (48255) CKT 1 |  | CHECK |  |
| L_Hatwai - N Lewiston 230 & Clearwater - N Lewiston 115 | OPEN Branch CLEARWTR_115.0 (48075) TO N LEWIST_115.0 (48253) CKT 1 |  | CHECK |  |
| L_Hells Canyon - Brownlee 230 (IDA) | OPEN Branch HELLSCYN_230.0 (60150) TO BROWNLEE_230.0 (60095) CKT 1 |  | CHECK |  |
| L_Hells Canyon - Brownlee 230 (IDA) | OPEN Gen HELSCYN1_ 14.4 (60151) #1 |  | CHECK |  |
| L_Hot Springs - Flathead 230 (BPA) | OPEN Bus LION MTN_230.0 (47359) |  | CHECK |  |
| L_Hot Springs - Flathead 230 (BPA) | OPEN Gen HUNGHR34_ 13.8 (40556) #3 |  | ALWAYS |  |
| L_Hot Springs - Flathead 230 (BPA) | OPEN Gen HUNGHR34_ 13.8 (40556) #4 |  | ALWAYS |  |
| L_Hot Springs - Flathead 230 (BPA) | OPEN Bus LIB PH2_230.0 (44201) |  | CHECK |  |
| L_Libby - Conkelly 230 (BPA) | OPEN Bus HASKILL_230.0 (40513) |  | CHECK |  |
| L_Libby - Conkelly 230 (BPA) | OPEN Bus LIB PH2_230.0 (44201) |  | CHECK |  |
| L_Libby - Noxon & Libby - Conkelly 230 (BPA) | OPEN Bus HASKILL_230.0 (40513) |  | CHECK | Libby - Conkelly |
| L_Libby - Noxon & Libby - Conkelly 230 (BPA) | OPEN Bus TRUMB CR_230.0 (47360) |  | CHECK | Libby - Conkelly |
| L_Libby - Noxon & Libby - Conkelly 230 (BPA) | OPEN MultiSectionLine LIBBY_230.0 (40657) TO NOXONBPA_230.0 (40787) CKT 1 |  | CHECK | Libby - Noxon |
| L_Libby - Noxon & Libby - Conkelly 230 (BPA) | OPEN Bus LIB PH1_230.0 (44200) |  | CHECK |  |
| L_Libby - Noxon & Libby - Conkelly 230 (BPA) | OPEN Bus LIB PH2_230.0 (44201) |  | CHECK |  |
| L_Libby - Troy 115 (BPA) | OPEN Branch LIBBY_115.0 (40655) TO LIBBYFEC_115.0 (47278) CKT 1 |  | CHECK |  |
| L_Lower Granite - Little Goose #1 & #2 500 (BPA) | OPEN Branch LIT GOOS_500.0 (40665) TO LOW GRAN_500.0 (40679) CKT 1 |  | CHECK |  |
| L_Lower Granite - Little Goose #1 & #2 500 (BPA) | OPEN Branch LIT GOOS_500.0 (40665) TO LOW GRAN_500.0 (40679) CKT 2 |  | CHECK |  |
| L_Lower Granite - Little Goose #1 & #2 500 (BPA) | OPEN Branch DWOR 1_ 13.8 (40361) TO DWOR 2_ 13.8 (40363) CKT 1 |  | CHECK |  |
| L_Lower Granite - Little Goose #1 & #2 500 (BPA) | OPEN Gen DWOR 2_ 13.8 (40363) #1 |  | CHECK |  |
| L_Lower Granite - Little Goose #1 & #2 500 (BPA) | OPEN Gen DWOR 3_ 13.8 (40365) #1 |  | CHECK |  |
| L_Lower Granite - Little Goose #1 & #2 500 (BPA) | OPEN Load MILCTYDC_230.0 (63010) #D1 |  | CHECK |  |
| L_Lower Granite - Little Goose #1 & #2 500 (BPA) | OPEN Shunt GARRISON_500.0 (40459) #r |  | CHECK |  |
| L_Lower Granite - Little Goose #1 & #2 500 (BPA) | OPEN Bus LIB PH1_230.0 (44200) | WMH > 1000 | CHECK |  |
| L_Lower Granite - Little Goose #1 & #2 500 (BPA) | OPEN Bus LIB PH2_230.0 (44201) | WMH > 1000 | CHECK |  |
| L_McNary - Roundup 230 (BPA) | OPEN Branch MCNRY S1_230.0 (41351) TO ROUNDUP_230.0 (40905) CKT 1 |  | CHECK |  |
| L_Midpoint - Summer Lake 500 (BPA) | OPEN Bus BURSUM11_500.0 (45030) |  | CHECK |  |
| L_Mill Creek - Amps 230 (NWE) | OPEN Bus PTRSNFLT_230.0 (62030) |  | CHECK |  |
| L_N Lewiston - Dry Creek 230 & N Lewiston - Pound Lane 115 (AVA) | OPEN Branch DRYCREEK_230.0 (48512) TO N LEWIST_230.0 (48255) CKT 1 |  | CHECK |  |
| L_N Lewiston - Dry Creek 230 & N Lewiston - Pound Lane 115 (AVA) | OPEN Bus SLEWIST_115.0 (48389) |  | CHECK |  |
| L_N Lewiston - Dry Creek 230 & N Lewiston - Pound Lane 115 (AVA) | OPEN Bus HOLBROOK_115.0 (48157) |  | CHECK |  |
| L_N Lewiston - Dry Creek 230 & N Lewiston - Pound Lane 115 (AVA) | OPEN Branch POUNDLNE_115.0 (48343) TO POUNDTAP_115.0 (48345) CKT 1 |  | CHECK |  |
| L_Noxon - Cab Gorg & Noxon - Lancaster 230 (AVA/BPA) | OPEN Branch CAB GORG_230.0 (48059) TO NOXON_230.0 (48281) CKT 1 |  | CHECK | Cabinet - Noxon 230 |
| L_Noxon - Cab Gorg & Noxon - Lancaster 230 (AVA/BPA) | OPEN Bus LIB PH2_230.0 (44201) |  | CHECK |  |
| L_Noxon - Cab Gorg & Noxon - Lancaster 230 (AVA/BPA) | OPEN MultiSectionLine LANCASTR_230.0 (40624) TO NOXONBPA_230.0 (40787) CKT 1 |  | CHECK | NoxonBPA - Lancaster 230 |
| L_Noxon - Cab Gorg & Noxon - Lancaster 230 (AVA/BPA) | OPEN Gen NOXON12_ 14.4 (48285) #2 | WMH > 1450 | CHECK |  |
| L_Noxon - Cab Gorg & Noxon - Lancaster 230 (AVA/BPA) | OPEN Gen NOXON12_ 14.4 (48285) #1 | WMH > 1450 | CHECK |  |
| L_Noxon - Hot Spr #1 & Noxon - Libby 230 (BPA) | OPEN Bus NOXONCON_230.0 (48289) |  | CHECK | Noxon - Hot Spr #1 230 |
| L_Noxon - Hot Spr #1 & Noxon - Libby 230 (BPA) | OPEN Bus TROUT CR_230.0 (41091) |  | CHECK | Noxon - Hot Spr #1 230 |
| L_Noxon - Hot Spr #1 & Noxon - Libby 230 (BPA) | OPEN MultiSectionLine LIBBY_230.0 (40657) TO NOXONBPA_230.0 (40787) CKT 1 |  | CHECK | Libby - Noxon 230 |
| L_Noxon - Hot Spr #1 & Noxon - Libby 230 (BPA) | OPEN Bus LIB PH1_230.0 (44200) | WMH > 700 | CHECK |  |
| L_Noxon - Hot Spr #1 & Noxon - Libby 230 (BPA) | OPEN Bus LIB PH2_230.0 (44201) | WMH > 700 | CHECK |  |
| L_Noxon - Hot Spr 230 1 & 2 (BPA/AVA) | OPEN Branch HOT SPR_230.0 (40551) TO NOXON_230.0 (48281) CKT 2 |  | CHECK |  |
| L_Noxon - Hot Spr 230 1 & 2 (BPA/AVA) | OPEN Bus NOXONCON_230.0 (48289) |  | CHECK | Noxon - Hot Spr #1 |
| L_Noxon - Hot Spr 230 1 & 2 (BPA/AVA) | OPEN Bus TROUT CR_230.0 (41091) |  | CHECK | Noxon - Hot Spr #1 |
| L_Noxon - Lancaster 230 & Taft - Bell 500 (BPA) | OPEN Load MILCTYDC_230.0 (63010) #D1 |  | CHECK |  |
| L_Noxon - Lancaster 230 & Taft - Bell 500 (BPA) | OPEN Shunt GARRISON_500.0 (40459) #r |  | CHECK |  |
| L_Noxon - Lancaster 230 & Taft - Bell 500 (BPA) | OPEN MultiSectionLine LANCASTR_230.0 (40624) TO NOXONBPA_230.0 (40787) CKT 1 |  | CHECK | Noxon - Lancaster 230 |
| L_Noxon - Lancaster 230 & Taft - Bell 500 (BPA) | OPEN MultiSectionLine BELL SC_500.0 (40096) TO TAFT_500.0 (41057) CKT 1 |  | CHECK | BellBPA - Taft 500 |
| L_Noxon - Lancaster 230 & Taft - Bell 500 (BPA) | OPEN Bus LIB PH1_230.0 (44200) | WMH > 1000 | CHECK |  |
| L_Noxon - Lancaster 230 & Taft - Bell 500 (BPA) | OPEN Bus LIB PH2_230.0 (44201) | WMH > 1000 | CHECK |  |
| L_Noxon - Pine Creek & Noxon - Hot Spr #2 230 (AVA) | OPEN Branch NOXON_230.0 (48281) TO PINE CRK_230.0 (48317) CKT 1 |  | CHECK |  |
| L_Noxon - Pine Creek & Noxon - Hot Spr #2 230 (AVA) | OPEN Branch HOT SPR_230.0 (40551) TO NOXON_230.0 (48281) CKT 2 |  | CHECK |  |
| L_Noxon - Pine Creek & Noxon - Hot Spr #2 230 (AVA) | OPEN Gen NOXON12_ 14.4 (48285) #1 | WMH > 1450 | CHECK |  |
| L_Noxon - Pine Creek & Noxon - Hot Spr #2 230 (AVA) | OPEN Gen NOXON12_ 14.4 (48285) #2 | WMH > 1450 | CHECK |  |
| L_Post Falls - Ramsey & Ramsey - Rathdrum #1 115 (AVA) | OPEN Bus PRAIRIE_115.0 (46245) |  | CHECK | Post Falls - Ramsey |
| L_Post Falls - Ramsey & Ramsey - Rathdrum #1 115 (AVA) | OPEN Bus APPLETAP_115.0 (48011) |  | CHECK | Ramsey - Rathdrum #1 |
| L_Post Falls - Ramsey & Ramsey - Rathdrum #1 115 (AVA) | OPEN Bus APPLEWAY_115.0 (48013) |  | CHECK | Ramsey - Rathdrum #1 |
| L_Post Falls - Ramsey & Ramsey - Rathdrum #1 115 (AVA) | OPEN Bus DALTON2T_115.0 (48095) |  | CHECK | Ramsey - Rathdrum #1 |
| L_Post Falls - Ramsey & Ramsey - Rathdrum #1 115 (AVA) | OPEN Bus AVONDALE_115.0 (48019) |  | CHECK | Ramsey - Rathdrum #1 |
| L_Ramsey - Rathdrum #1 & Boulder - Rathdrum 115 (AVA) | OPEN Bus APPLETAP_115.0 (48011) |  | CHECK | Ramsey - Rathdrum #1 |
| L_Ramsey - Rathdrum #1 & Boulder - Rathdrum 115 (AVA) | OPEN Bus APPLEWAY_115.0 (48013) |  | CHECK | Ramsey - Rathdrum #1 |
| L_Ramsey - Rathdrum #1 & Boulder - Rathdrum 115 (AVA) | OPEN Bus DALTON2T_115.0 (48095) |  | CHECK | Ramsey - Rathdrum #1 |
| L_Ramsey - Rathdrum #1 & Boulder - Rathdrum 115 (AVA) | OPEN Bus AVONDALE_115.0 (48019) |  | CHECK | Ramsey - Rathdrum #1 |
| L_Ramsey - Rathdrum #1 & Boulder - Rathdrum 115 (AVA) | OPEN Bus MOAB_115.0 (47511) |  | CHECK | Boulder - Rathdrum 115 |
| L_Ramsey - Rathdrum #1 & Boulder - Rathdrum 115 (AVA) | OPEN Bus PLEASANT_115.0 (48319) |  | CHECK | Boulder - Rathdrum 115 |
| L_Taft - Hot Springs 500 kV (BPA) | OPEN Branch HOT SPR_500.0 (40553) TO TAFT_500.0 (41057) CKT 1 |  | CHECK |  |
| L_Taft - Hot Springs 500 kV (BPA) | OPEN Shunt GARRISON_500.0 (40459) #r |  | CHECK |  |
| L_Taft - Hot Springs 500 kV (BPA) | OPEN Bus LIB PH1_230.0 (44200) | West MT Hydro > 1000 | CHECK |  |
| L_Taft - Hot Springs 500 kV (BPA) | OPEN Bus LIB PH2_230.0 (44201) | West MT Hydro > 1000 | CHECK |  |
| L_Westside - Bell & Westside - Coulee 230 (AVA/BPA) | OPEN Bus WESTBPA2_230.0 (41276) |  | CHECK |  |
| L_Westside - Bell & Westside - Coulee 230 (AVA/BPA) | OPEN Bus WESTBPA1_230.0 (41275) |  | CHECK |  |
| L_Westside - Coulee & Bell - Coulee #3 230 (AVA/BPA) | OPEN Bus WESTBPA2_230.0 (41276) |  | CHECK | Westside - Coulee |
| L_Westside - Coulee & Bell - Coulee #3 230 (AVA/BPA) | OPEN MultiSectionLine BELL S3_230.0 (40090) TO COULEES1_230.0 (41356) CKT 3 |  | CHECK |  |
| L_Westside - Waste to Energy & Westside - Ft Wright 115 (AVA) | OPEN Branch FTWRIGHT_115.0 (48129) TO WEST_115.0 (48461) CKT 1 |  | CHECK |  |
| L_Westside - Waste to Energy & Westside - Ft Wright 115 (AVA) | OPEN Branch SPKWASTE_115.0 (48409) TO WEST_115.0 (48461) CKT 1 |  | CHECK |  |
| T_40017ADDY-48007ADDYAVAC1 | OPEN Branch ADDY_115.0 (40017) TO ADDY AVA_ 23.0 (48007) CKT 1 |  | CHECK |  |
| T_40021ADDY2-40017ADDYC1 | OPEN Branch ADDY 2_230.0 (40021) TO ADDY_115.0 (40017) CKT 1 |  | CHECK |  |
| T_40088BELLS2-40087BELLBPAC1 | OPEN Branch BELL S2_230.0 (40088) TO BELL BPA_115.0 (40087) CKT 1 |  | CHECK |  |
| T_40091BELLBPA-40092BELLS4C1 | OPEN Branch BELL BPA_500.0 (40091) TO BELL S4_230.0 (40092) CKT 1 |  | CHECK |  |
| T_40909SACHEEN-40907SACHEENC1 | OPEN Branch SACHEEN_230.0 (40909) TO SACHEEN_115.0 (40907) CKT 1 |  | CHECK |  |
| T_41298SMITHFLS-41299SMITHFLSC1 | OPEN Branch SMITHFLS_ 13.8 (41298) TO SMITHFLS_115.0 (41299) CKT 1 |  | CHECK |  |
| T_45097DRYGULCH-48113DRYGULCHC1 | OPEN Branch DRYGULCH_ 69.0 (45097) TO DRYGULCH_115.0 (48113) CKT 1 |  | CHECK |  |
| T_46447SUMERFAL-46653SUMERFA1C1 | OPEN Branch SUMERFAL_115.0 (46447) TO SUMERFA1_ 13.8 (46653) CKT 1 |  | CHECK |  |
| T_46447SUMERFAL-46655SUMERFA2C1 | OPEN Branch SUMERFAL_115.0 (46447) TO SUMERFA2_ 13.8 (46655) CKT 1 |  | CHECK |  |
| T_46619HEADWORK-48149HEADWORKC1 | OPEN Branch HEADWORK_ 13.8 (46619) TO HEADWORK_115.0 (48149) CKT 1 |  | CHECK |  |
| T_47010BOXCAN1-47009BOXCANYC1 | OPEN Branch BOX CAN1_ 13.2 (47010) TO BOX CANY_115.0 (47009) CKT 1 |  | CHECK |  |
| T_47012BOXCAN2-47009BOXCANYC1 | OPEN Branch BOX CAN2_ 13.2 (47012) TO BOX CANY_115.0 (47009) CKT 1 |  | CHECK |  |
| T_47014BOXCAN3-47009BOXCANYC1 | OPEN Branch BOX CAN3_ 13.2 (47014) TO BOX CANY_115.0 (47009) CKT 1 |  | CHECK |  |
| T_47016BOXCAN4-47009BOXCANYC1 | OPEN Branch BOX CAN4_ 13.2 (47016) TO BOX CANY_115.0 (47009) CKT 1 |  | CHECK |  |
| T_47126BOXPS-47009BOXCANYC1 | OPEN Branch BOX PS_115.0 (47126) TO BOX CANY_115.0 (47009) CKT 1 |  | CHECK |  |
| T_47254USK-47091USKC1 | OPEN Branch USK_115.0 (47254) TO USK_230.0 (47091) CKT 1 |  | CHECK |  |
| T_47568LANCASG-40624LANCASTRC1 | OPEN Branch LANCAS G_ 18.0 (47568) TO LANCASTR_230.0 (40624) CKT 1 |  | CHECK |  |
| T_47569LANCASS-40624LANCASTRC1 | OPEN Branch LANCAS S_ 13.8 (47569) TO LANCASTR_230.0 (40624) CKT 1 |  | CHECK |  |
| T_48025BEACONN-48023BEACONNC1 | OPEN Branch BEACON N_230.0 (48025) TO BEACON N_115.0 (48023) CKT 1 |  | CHECK |  |
| T_48027BEACONS-48029BEACONSC1 | OPEN Branch BEACON S_ 13.8 (48027) TO BEACON S_115.0 (48029) CKT 1 |  | CHECK |  |
| T_48031BEACONS-48029BEACONSC1 | OPEN Branch BEACON S_230.0 (48031) TO BEACON S_115.0 (48029) CKT 1 |  | CHECK |  |
| T_48037BENEWAH-48035BENEWAHC1 | OPEN Branch BENEWAH_230.0 (48037) TO BENEWAH_115.0 (48035) CKT 1 |  | CHECK |  |
| T_48059CABGORG-48057CABGORGC1 | OPEN Branch CAB GORG_230.0 (48059) TO CAB GORG_115.0 (48057) CKT 1 |  | CHECK |  |
| T_48059CABGORG-48061CABGOR12C1 | OPEN Branch CAB GORG_230.0 (48059) TO CABGOR12_ 13.8 (48061) CKT 1 |  | CHECK |  |
| T_48059CABGORG-48063CABGOR34C1 | OPEN Branch CAB GORG_230.0 (48059) TO CABGOR34_ 13.8 (48063) CKT 1 |  | CHECK |  |
| T_48075CLEARWTR-48476CLWTR2C1 | OPEN Branch CLEARWTR_115.0 (48075) TO CLWTR2_ 34.5 (48476) CKT 1 |  | CHECK |  |
| T_48075CLEARWTR-48481CLWTR7C1 | OPEN Branch CLEARWTR_115.0 (48075) TO CLWTR7_ 34.5 (48481) CKT 1 |  | CHECK |  |
| T_48083COLVAVA-48085COLVILLEC1 | OPEN Branch COLV AVA_115.0 (48083) TO COLVILLE_ 13.8 (48085) CKT 1 |  | CHECK |  |
| T_48085COLVILLE-48439VAAGENC1 | OPEN Branch COLVILLE_ 13.8 (48085) TO VAAGEN_ 4.2 (48439) CKT 1 |  | CHECK |  |
| T_48143GREENWDA-48229MEYERSFLC1 | OPEN Branch GREENWDA_115.0 (48143) TO MEYERSFL_ 13.0 (48229) CKT 1 |  | CHECK |  |
| T_48173KETTLEAV-48175KETTLEAVC1 | OPEN Branch KETTLEAV_ 13.8 (48173) TO KETTLEAV_115.0 (48175) CKT 1 |  | CHECK |  |
| T_48189LITFAL12-48193LITTFALLC1 | OPEN Branch LITFAL12_ 4.0 (48189) TO LITTFALL_115.0 (48193) CKT 1 |  | CHECK |  |
| T_48191LITFAL34-48193LITTFALLC1 | OPEN Branch LITFAL34_ 4.0 (48191) TO LITTFALL_115.0 (48193) CKT 1 |  | CHECK |  |
| T_48197LOLO-48195LOLOC1 | OPEN Branch LOLO_230.0 (48197) TO LOLO_115.0 (48195) CKT 1 |  | CHECK |  |
| T_48197LOLO-48195LOLOC2 | OPEN Branch LOLO_230.0 (48197) TO LOLO_115.0 (48195) CKT 2 |  | CHECK |  |
| T_48199LONGLAKA-48205LONGLKG1C1 | OPEN Branch LONGLAKA_115.0 (48199) TO LONGLKG1_ 4.0 (48205) CKT 1 |  | CHECK |  |
| T_48199LONGLAKA-48207LONGLKG2C1 | OPEN Branch LONGLAKA_115.0 (48199) TO LONGLKG2_ 4.0 (48207) CKT 1 |  | CHECK |  |
| T_48201LONGLAKB-48209LONGLKG3C1 | OPEN Branch LONGLAKB_115.0 (48201) TO LONGLKG3_ 4.0 (48209) CKT 1 |  | CHECK |  |
| T_48201LONGLAKB-48211LONGLKG4C1 | OPEN Branch LONGLAKB_115.0 (48201) TO LONGLKG4_ 4.0 (48211) CKT 1 |  | CHECK |  |
| T_48227MEYERSFL-48229MEYERSFLC1 | OPEN Branch MEYERSFL_ 11.0 (48227) TO MEYERSFL_ 13.0 (48229) CKT 1 |  | CHECK |  |
| T_48241MONROEA-48337POSTSTRTC1 | OPEN Branch MONROEA_ 13.8 (48241) TO POSTSTRT_ 13.8 (48337) CKT 1 |  | CHECK |  |
| T_48249MOSCOW-48251MOSCOWXC1 | OPEN Branch MOSCOW_230.0 (48249) TO MOSCOWX_115.0 (48251) CKT 1 |  | CHECK |  |
| T_48251MOSCOWX-48247MOSCOWC1 | OPEN Branch MOSCOWX_115.0 (48251) TO MOSCOW_115.0 (48247) CKT 1 |  | CHECK |  |
| T_48255NLEWIST-48253NLEWISTC1 | OPEN Branch N LEWIST_230.0 (48255) TO N LEWIST_115.0 (48253) CKT 1 |  | CHECK |  |
| T_48263NINEFLSE-48265NINEMI12C1 | OPEN Branch NINEFLSE_ 30.0 (48263) TO NINEMI12_ 2.3 (48265) CKT 1 |  | CHECK |  |
| T_48263NINEFLSE-48269NINEMILEC1 | OPEN Branch NINEFLSE_ 30.0 (48263) TO NINEMILE_115.0 (48269) CKT 1 |  | CHECK |  |
| T_48267NINEMI34-48269NINEMILEC1 | OPEN Branch NINEMI34_ 13.8 (48267) TO NINEMILE_115.0 (48269) CKT 1 |  | CHECK |  |
| T_48275NORTHEAS-48277NORTHEASC1 | OPEN Branch NORTHEAS_ 13.8 (48275) TO NORTHEAS_115.0 (48277) CKT 1 |  | CHECK |  |
| T_48281NOXON-48283NOXON5C1 | OPEN Branch NOXON_230.0 (48281) TO NOXON 5_ 14.4 (48283) CKT 1 |  | CHECK |  |
| T_48281NOXON-48285NOXON12C1 | OPEN Branch NOXON_230.0 (48281) TO NOXON12_ 14.4 (48285) CKT 1 |  | CHECK |  |
| T_48287NOXON34-40787NOXONBPAC1 | OPEN Branch NOXON34_ 14.4 (48287) TO NOXONBPA_230.0 (40787) CKT 1 |  | CHECK |  |
| T_48317PINECRK-48315PINECRKC1 | OPEN Branch PINE CRK_230.0 (48317) TO PINE CRK_115.0 (48315) CKT 1 |  | CHECK |  |
| T_48317PINECRK-48315PINECRKC2 | OPEN Branch PINE CRK_230.0 (48317) TO PINE CRK_115.0 (48315) CKT 2 |  | CHECK |  |
| T_48321PLUMMER-48325PLUMMERGC1 | OPEN Branch PLUMMER_ 4.2 (48321) TO PLUMMERG_ 13.8 (48325) CKT 1 |  | CHECK |  |
| T_48323PLUMMER-48327PLUMMWEAC1 | OPEN Branch PLUMMER_115.0 (48323) TO PLUMMWEA_ 13.8 (48327) CKT 1 |  | CHECK |  |
| T_48329POSTFLS-48331POSTFL15C1 | OPEN Branch POST FLS_115.0 (48329) TO POSTFL15_ 2.4 (48331) CKT 1 |  | CHECK |  |
| T_48329POSTFLS-48333POSTFLS6C1 | OPEN Branch POST FLS_115.0 (48329) TO POSTFLS6_ 2.4 (48333) CKT 1 |  | CHECK |  |
| T_48335POSTSTRT-48337POSTSTRTC4 | OPEN Branch POSTSTRT_ 4.2 (48335) TO POSTSTRT_ 13.8 (48337) CKT 4 |  | CHECK |  |
| T_48337POSTSTRT-48339POSTSTRTC1 | OPEN Branch POSTSTRT_ 13.8 (48337) TO POSTSTRT_115.0 (48339) CKT 1 |  | CHECK |  |
| T_48337POSTSTRT-48339POSTSTRTC2 | OPEN Branch POSTSTRT_ 13.8 (48337) TO POSTSTRT_115.0 (48339) CKT 2 |  | CHECK |  |
| T_48351RATHBUS1-48359RATHGEN1C1 | OPEN Branch RATHBUS1_115.0 (48351) TO RATHGEN1_ 13.8 (48359) CKT 1 |  | CHECK |  |
| T_48353RATHBUS2-48361RATHGEN2C1 | OPEN Branch RATHBUS2_115.0 (48353) TO RATHGEN2_ 13.8 (48361) CKT 1 |  | CHECK |  |
| T_48357RATHDRUM-48355RATHDRUMC1 | OPEN Branch RATHDRUM_230.0 (48357) TO RATHDRUM_115.0 (48355) CKT 1 |  | CHECK |  |
| T_48357RATHDRUM-48356RATHDRMEC1 | OPEN Branch RATHDRUM_230.0 (48357) TO RATHDRME_115.0 (48356) CKT 1 |  | CHECK |  |
| T_48385SHAWNEE-48383SHAWNEEC1 | OPEN Branch SHAWNEE_230.0 (48385) TO SHAWNEE_115.0 (48383) CKT 1 |  | CHECK |  |
| T_48407SPKWASTE-48409SPKWASTEC1 | OPEN Branch SPKWASTE_ 13.8 (48407) TO SPKWASTE_115.0 (48409) CKT 1 |  | CHECK |  |
| T_48433UPRIVER-48437UPRIVERC1 | OPEN Branch UPRIVER_ 2.4 (48433) TO UPRIVER_ 13.8 (48437) CKT 1 |  | CHECK |  |
| T_48435UPRIVER-48437UPRIVERC1 | OPEN Branch UPRIVER_ 4.2 (48435) TO UPRIVER_ 13.8 (48437) CKT 1 |  | CHECK |  |
| T_48463WEST-48461WESTC1 | OPEN Branch WEST_230.0 (48463) TO WEST_115.0 (48461) CKT 1 |  | CHECK |  |
| T_48463WEST-48461WESTC2 | OPEN Branch WEST_230.0 (48463) TO WEST_115.0 (48461) CKT 2 |  | CHECK |  |
| T_48475CLWTR1-48484CWTW1C1 | OPEN Branch CLWTR1_ 34.5 (48475) TO CWTW1_ 12.0 (48484) CKT 1 |  | CHECK |  |
| T_48475CLWTR1-48487CWTW4C1 | OPEN Branch CLWTR1_ 34.5 (48475) TO CWTW4_ 12.0 (48487) CKT 1 |  | CHECK |  |
| T_48477CLWTR3-48485CWTW2C1 | OPEN Branch CLWTR3_ 34.5 (48477) TO CWTW2_ 12.0 (48485) CKT 1 |  | CHECK |  |
| T_48478CLWTR4-48482CWGEN3C1 | OPEN Branch CLWTR4_ 34.5 (48478) TO CWGEN3_ 12.0 (48482) CKT 1 |  | CHECK |  |
| T_48479CLWTR5-48486CWTW3C1 | OPEN Branch CLWTR5_ 34.5 (48479) TO CWTW3_ 12.0 (48486) CKT 1 |  | CHECK |  |
| T_48479CLWTR5-48488CWTW5C1 | OPEN Branch CLWTR5_ 34.5 (48479) TO CWTW5_ 12.0 (48488) CKT 1 |  | CHECK |  |
| T_48480CLWTR6-48483CWGEN4C1 | OPEN Branch CLWTR6_ 34.5 (48480) TO CWGEN4_ 12.0 (48483) CKT 1 |  | CHECK |  |
| T_48481CLWTR7-48489CWTW6C1 | OPEN Branch CLWTR7_ 34.5 (48481) TO CWTW6_ 12.0 (48489) CKT 1 |  | CHECK |  |
| T_48484CWTW1-48490CWBUS1C1 | OPEN Branch CWTW1_ 12.0 (48484) TO CWBUS1_ 12.0 (48490) CKT 1 |  | CHECK |  |
| T_48484CWTW1-48493CWBUS4C1 | OPEN Branch CWTW1_ 12.0 (48484) TO CWBUS4_ 12.0 (48493) CKT 1 |  | CHECK |  |
| T_48485CWTW2-48492CWBUS3C1 | OPEN Branch CWTW2_ 12.0 (48485) TO CWBUS3_ 12.0 (48492) CKT 1 |  | CHECK |  |
| T_48485CWTW2-48493CWBUS4C1 | OPEN Branch CWTW2_ 12.0 (48485) TO CWBUS4_ 12.0 (48493) CKT 1 |  | CHECK |  |
| T_48486CWTW3-48491CWBUS2C1 | OPEN Branch CWTW3_ 12.0 (48486) TO CWBUS2_ 12.0 (48491) CKT 1 |  | CHECK |  |
| T_48486CWTW3-48492CWBUS3C1 | OPEN Branch CWTW3_ 12.0 (48486) TO CWBUS3_ 12.0 (48492) CKT 1 |  | CHECK |  |
| T_48487CWTW4-48495CWBUS6C1 | OPEN Branch CWTW4_ 12.0 (48487) TO CWBUS6_ 12.0 (48495) CKT 1 |  | CHECK |  |
| T_48487CWTW4-48496CWBUS7C1 | OPEN Branch CWTW4_ 12.0 (48487) TO CWBUS7_ 12.0 (48496) CKT 1 |  | CHECK |  |
| T_48488CWTW5-48495CWBUS6C1 | OPEN Branch CWTW5_ 12.0 (48488) TO CWBUS6_ 12.0 (48495) CKT 1 |  | CHECK |  |
| T_48488CWTW5-48496CWBUS7C1 | OPEN Branch CWTW5_ 12.0 (48488) TO CWBUS7_ 12.0 (48496) CKT 1 |  | CHECK |  |
| T_48489CWTW6-48494CWBUS5C1 | OPEN Branch CWTW6_ 12.0 (48489) TO CWBUS5_ 12.0 (48494) CKT 1 |  | CHECK |  |
| T_48489CWTW6-48497CWBUS8C1 | OPEN Branch CWTW6_ 12.0 (48489) TO CWBUS8_ 12.0 (48497) CKT 1 |  | CHECK |  |
| T_48510DRYCREEK-48512DRYCREEKC1 | OPEN Branch DRYCREEK_230.0 (48512) TO DRYCREEK_115.0 (48510) CKT 1 |  | CHECK |  |
| T_48524BOULDER-48520BOULDERWC1 | OPEN Branch BOULDER_230.0 (48524) TO BOULDERW_115.0 (48520) CKT 1 |  | CHECK |  |
| T_48524BOULDER-48522BOULDEREC2 | OPEN Branch BOULDER_230.0 (48524) TO BOULDERE_115.0 (48522) CKT 2 |  | CHECK |  |
| T_48526BOULDERG-48522BOULDEREC1 | OPEN Branch BOULDERG_ 13.8 (48526) TO BOULDERE_115.0 (48522) CKT 1 |  | CHECK |  |
| T_Hatwai 500/230 Xfmr (BPA) | OPEN Branch HATWAI_500.0 (40521) TO HATWAI_230.0 (40519) CKT 1 |  | CHECK |  |