BHBE Common Use System

2011 Local Transmission Plan

Study Scope

- Background

The Transmission Provider will perform power flow and dynamic analysis to evaluate the transmission system performance with forecasted network and native loads as well as planned system additions and upgrades.  Any system performance criteria violations found during the study will be corrected through the use of Remedial Action Schemes, Operating Procedures, or transmission facility additions.  These identified solutions will then be summarized in the Common Use System (“CUS”) Local Transmission Plan (“LTP”).  Additional information on the LTP process can be found on the BHBE website (www.oatioasis.com/BHBE) within the “Transmission Planning” folder.

- Base Case Scenarios

The LTP will focus on 2016 for the near-term study period, including both peak and off-peak demand scenarios. 2018 and 2022 were chosen for the off-peak and peak far-term study periods, respectively.  The study years were selected based on several factors including base case availability, in-service dates of planned system upgrades, and previously completed planning studies.  All generation and transmission system upgrades currently under construction or submitted for regulatory review will be included in the base case scenarios.  Proposed projects may be included in the base case upon agreement of both the TP and TCPC.  Descriptions of any changes made to a starting case to create a base case scenario will be documented.

WECC-approved base cases will be used to develop the study cases, unless the TP and members of the TCPC agree to an alternate starting case.   Table 1 includes the proposed study cases and their respective starting case.

Table 1: TCPC Study Cases

| Near-Term Study Case | Starting Case | Far-Term Study Case | Starting Case |
| --- | --- | --- | --- |
| 2016 Heavy Summer | WECC 2016HS2 | 2022 Heavy Summer | WECC 2021HS1 |
| 2016 Light Winter | WECC 2016HW2 | 2018 Light Winter | WECC 2018HW1 |

- Uncertainty Scenarios

An uncertainty scenario will be created for each of the base case scenarios in Table 1 based on stakeholder input.  Uncertainty scenarios provide an opportunity to evaluate generation and transmission projects submitted for consideration but not included in the base case, as well as demand response resources.

- Power Flow Simulations

For each base case and uncertainty scenario identified above power flow simulations will be run to evaluate system performance under NERC TPL Standard Category A-C events and worst case Category D events within the CUS transmission system including tie lines.  The transmission system will be evaluated with the Rapid City DC Tie scheduled at 200 MW east-to-west, 0 MW and 200 MW west-to-east.  Rapid City and Wyodak area gas-fired generation will be dispatched as needed to mitigate performance criteria violations.  Current operating procedures and remedial action schemes will be employed unless certain circumstances require otherwise.

The study will monitor the performance of the transmission system in the Western Interconnection bounded by the Yellowtail, Casper, Difficulty, LRS and Sidney 230 kV substations.

- Dynamic Simulations

Dynamic simulations will be run on all study cases to evaluate system performance under NERC TPL Standard Category A and worst-case Category B, C and D events based upon the results of the power flow simulations.

- Study Timeline

  - Q1 2011 – Collect base case updates from neighbor utilities and load/resource data from transmission customers.

  - Q2/Q3 2011 – Perform simulations and develop solutions to mitigate performance violations.

  - Q4 2011 – Draft and finalize the CUS Local Transmission Plan.