Black Hills Power, Inc

Basin Electric Power Cooperative

Powder River Energy Corporation

Transmission System Planning

Methodology, Criteria and Process

September 14, 2007

Table of Contents: To be Published

# Introduction

Black Hills Power, Inc. (“BHP”), Basin Electric Power Cooperative (“BEPC”) and Powder River Energy Corporation (“PRECorp”) each own certain transmission facilities within a Common Use System. This System is shown in Figure 1 below will be defined as the Transmission Provider Transmission System. Transmission service is provided on the Transmission System pursuant to a single Joint Open Access Transmission Tariff (“JOATT”) with the aforementioned transmission owners being the Transmission Providers (“TP”). The methodology, process and criteria described herein are used to evaluate the TP transmission system, ensuring system reliability is maintained throughout the planning horizon.  Reliability, by definition, examines the adequacy and security of the electric transmission system.

The Federal Energy Regulatory Commission (FERC) Order No. 890 requires the TP to explain how they will treat retail native loads, in order to ensure that standards and processes are consistently applied to all customers. Consistent application of the TP planning process, standards, methodology and criteria for all customers (i.e., retail, network and point-to-point) is ensured through the coordination, openness and transparency of TP planning process. All customers are treated on an equal and comparable basis using the transmission system planning process, methodology and criteria described herein.  All customer data is included in the planning analysis without regard to their classification.  The TP transmission system planning process is designed to be transparent, open and understandable.  The information described herein reflects existing practice, with the addition of new processes that encompass Order 890 transmission system planning requirements.  For example, the TP planning process is being expanded to include input from stakeholders and other interested parties during the planning stage. As described in Attachment K to the JOATT, a Transmission Coordination and Planning Committee (“TCPC”) will be established to facilitate a coordinated, open and transparent planning process.

FERC Order 890 makes a distinction between the transmission system planning for load due to customers’ needs (i.e., system planning) and planning for new generation interconnection.  The TP adheres to the FERC Large Generation Interconnection Procedures (“LGIP”) and Small Generation Interconnection Procedures (“SGIP”) requirements to study generation interconnection.  In studying a request for transmission service, the TP follows its tariff requirements as provided on the BHBE OASIS Website at http://www.oatioasis.com/BHBE.

# Transmission Provider Electric Transmission System

The TP electric transmission system consists of approximately 570 miles of high voltage (230 kV) transmission lines located in three states.

The TP transmission system has interconnections to two major transmission systems located in the Western Electricity Coordinating Council (“WECC”) area and one back-to-back AC-DC interconnection to a system that connects with the Mid-Continent Area Power Pool (“MAPP”) region.

The following graphic displays the TP transmission system.

The dashed lines indicate future committed facilities.

# Transmission Provider Planning Process

The TP transmission system planning process is depicted in the following flowchart.

The TP will follow an annual planning cycle that follows the process shown in Figure 2 above.  This process will be used to develop a 15-year electric transmission system plan.  The planning process steps (i.e., Study plan and scenario development, technical study, decision and reporting) are fully integrated and produce the TP transmission plan. This process is fully described in the following sections.

### Timeline

The typical timeline for the TP one-year planning cycle is shown in the following table.  The Transmission Coordination and Planning Committee (“TCPC”) will meet annually in January to assess the need to initiate a planning study for that year.  Depending on the previous planning study results and recent system operations, the TCPC may deem a new planning study unnecessary for that year.  However, a planning study must be initiated at a minimum every two years.

This timeline displays the approximate time dedicated to each of the planning steps and time when forecast data will be collected.  Data that is collected will fall into one of three time periods for inclusion into the TP planning process - “Open”, “Optional” or “Closed”.  All data collected during the Open time period will be included in the study assuming the data is complete.  Data obtained during the Optional time period may or may not be included in the study if it is not complete or the Technical Study has progressed to a point where including this information is not practical.  The TP will consult with the TCPC in making this determination.  Data collected during the Closed time period of the annual cycle will be compared to the data used in the technical analysis and any notable changes will be discussed in the final TP Transmission Planning Report.

## Regional & Sub Regional Participation

The TP’s participation in regional and sub-regional planning activities will be broad, ranging from providing data to participating in studies and committees.  The TP transmission system data, assumptions and transmission plan will be shared with interconnected transmission systems, sub-regional and regional entities.  The TP base case data and transmission plan will be provided to other Transmission Providers when appropriate.

The TP will provide its transmission plan’s data and assumptions to sub-regional and regional committees that are responsible for building databases and then using this database for load and resource assessments and for operating and planning reliability studies.  This is an annual process that requires the TP to provide basic transmission data, load forecasts and generation dispatch information to be shared and included in the databases used by regional and sub-regional planning entities.  The TP will participate in these forums as appropriate.

The TP will provide its transmission plan to the WECC, Colorado Coordinated Planning Group (“CCPG”), and other sub-regional entities as appropriate.  In the sub-regional context, the TP is an active participant of CCPG.  The TP will submit its data, assumptions and transmission plan to CCPG as required for inclusion in all applicable sub-regional transmission plans.  The TP will actively participate in the CCPG planning process to ensure data and assumptions are properly represented in all applicable sub-regional plans.  When appropriate the TP will provide its transmission plan information to WECC or other regional entities.

The TP will participate in sub-regional and regional transmission planning studies as appropriate to ensure data and assumptions are coordinated.  These studies may be focused on integrating new transmission lines into the regional transmission network or a broad planning study of regional or sub-regional transmission needs.  The TP’s participation in these studies will be guided by the intent of the study and how the TP transmission system might be affected.

The TP will also participate in regional or sub-regional studies to identify enhancements that could relieve significant and recurring congestion.

# Transmission Planning Process and Basic Methodology

Below is a discussion of the TP’s planning process and basic methodology that is used to formally analyze its electric transmission system.  By application of this methodology, the TP ensures that a reliable transmission system exists to serve network customer load and firm point-to-point transmission service requests.  The TP’s methodology is intended to define operating conditions that fail to meet reliability criteria and then identify mitigations or solutions (e.g., transmission and non-transmission) that solve the criteria violations.  The operating conditions are for a specific instant in time, such as peak load conditions, and are not an integrated time period, such as an hour, day, month, etc.  The TP’s basic process and methodology described below is focused on transmission reliability and not economic congestion studies that can be requested by customers.

The TP’s goal is to design a reliable, least cost transmission system that will perform under expected operating conditions wherein customer load can be served reliably throughout the planning horizon. The TP process and methodology includes transmission system planning and the WECC Annual Study Plan.

## Transmission Provider Transmission System Planning Process

The TP planning process includes the four steps shown in the graph to the right.  These step are (1) Study Plan and Scenario Development, (2) Technical Study, (3) Decision, and (4) Reporting.  How these steps are integrated to formulate the transmission plan is shown in Figure 2 above and further described below. The transmission lines used in a system planning study may range in size from 69 kV to 230 kV and may be networked or radial.

The transmission system planning process involves forecasting customer demand, identifying area reliability problems, evaluating possible mitigation options and selecting a solution that solves the area’s transmission needs.  Transmission system planning evaluates the transmission system reliability up to 15 years in the future.  The planning effort considers transmission and non-transmission alternatives to resolve the reliability problem for a specified area.  The TP’s process is flexible, involves stakeholder input and is intended to develop a plan that:

- Responds to customers needs;

- Is low cost (e.g., Total Present Value Revenue Requirement, Rate Impact, etc.);

- Considers non-transmission and transmission alternatives;

- Assesses future uncertainty and risk;

- Promotes the TP commitment to protecting the environment;

- Includes input from the public and other interested parties;

- Provides adequate return to investors;

- Complements corporate goals and commitments;

- Meets FERC Standards and WECC Standards;

- Meets the applicable state regulatory expectations;

- Meets Regional and Sub-Regional planning requirements;

- Satisfies the requirements of the FERC Order 890; and

- Conforms to applicable state and national laws and regulations.

### Study Plan and Scenario Development

As can be seen in Figure 2 above, this portion of the planning process includes coordination and input from the TCPC. The TP will work with the TCPC to identify the study objectives, study plan and pertinent scenarios that should be studied in order to meet various stakeholder needs. The TCPC will provide input into the TP transmission planning process pursuant to FERC Order 890 Transparency requirements.  Information regarding the TCPC can be found in Attachment K to the JOATT located on the BHBE OASIS Website at http://www.oatioasis.com/BHBE/.

The TP uses scenario planning and not probabilistic planning for developing the electric transmission system plan.  The TP may, however, use probabilistic assessment methods within a defined scenario to evaluate uncertainty

A scenario represents a “snapshot” in time that depicts a specific condition such as peak and light summer load, maximum and minimum area generation, maximum export, etc. Each scenario should be realistic and be designed to provide maximum stress to the transmission system regardless if it causes inadequate transmission system performance as measured against established criteria. Since there are a large number of combinations of load, generation and export/import conditions, careful consideration must be given to design each scenario to depict a future load and generation dispatch pattern that stresses the transmission system. Experience has shown that the transmission system is stressed during heavy summer conditions with minimum exports and during light load conditions with maximum export conditions. A good study plan and realistic scenarios will help ensure the planning process identifies upgrades required to ensure the transmission system remains reliable under all operating conditions.

The TP basic methodology is to develop the base scenarios to study and then to develop uncertainty scenarios from these base scenarios.  This methodology is described in more detail below.

#### Base Scenarios

Base case scenarios will be used to examine the transmission system under a variety of future assumptions for a specific period of time. Varying the amount, type and location of generation, the load level and export/import conditions are all important in defining a scenario. These assumptions include, but are not limited to the following:

- Load Forecast (e.g., year to study)

- Load Condition to Study (e.g. season, peak load or light load, etc.)

- Generation Available (e.g., generation additions/changes)

- Generation Dispatch Conditions (e.g., how is the generation operated)

    - Different types of generation to determine how generation responds to outage conditions

    - Generation location and magnitude to determine transmission stress

    - Higher generation levels to cause more power to be exported out of the TP transmission system.  Lower generation levels with high imports

- Transmission System Elements Available (e.g., transmission element additions/changes)

- Transmission System Configuration (e.g., what elements are out-of-service)

Even though new interconnect projects follow FERC’s defined interconnection methods, the study results from the new interconnect projects cannot be ignored in transmission system planning.  The addition of new generation to the TP transmission system can affect the flows throughout the system.  Additional power flows from the new generation, and flow changes due to transmission system upgrades, may require transmission system upgrades.  The TP, with input from the TCPC, will consider scenarios including new generators with associated transmission or develop uncertainty scenarios that include this information.

#### Uncertainty Scenarios

The uncertainty scenarios are intended to recognize that the future, as assumed in the base scenarios, is not known.  This uncertain future creates risk, which may be quantifiable or non-quantifiable.  Risk may be expressed as a dollar cost or other impact.  The base scenarios must make assumptions about future conditions, but the uncertainty scenario helps with understanding the risk associated with those assumptions.  The purpose of the uncertainty scenarios is to develop information about the cost and electrical performance of base scenarios so that an informed decision about future transmission investments can be made.

### Technical Study

The technical study is the second step in electric transmission system planning process. Once the scenarios are defined as noted above, the technical study will begin by developing a base case that specifies the modeling information for the scenario condition.  Each scenario may include several base cases to span the 15-year study horizon.  For example, to study the summer peaks in 2010 and 2015 requires two distinct base cases that reflect the load, generation and transmission line and equipment changes and additions for the specific year.  Developing a base case depicting the scenario is critical and can take a significant amount of work and time to develop.  A 15-year study for a scenario may actually include only three base cases representing years 5, 10 and 15.  These base cases will differ by the load growth, generation and transmission assumptions.

Once a base case is built, the technical study is performed to examine the reliability of the TP electric transmission lines that move power between the bulk electric transmission system and the distribution system. The TP uses a sophisticated computer model (i.e., PSS/E) to simulate generator output, electrical flows over the transmission lines, electrical equipment action, customer loads and export (or import) path flows. The technical study is quantifies transmission system performance by measuring the bus voltage, equipment loading, reactive power requirement, system frequency and other electrical parameters against established reliability criteria. If inadequate performance is observed, a solution or mitigation (e.g., transmission or non-transmission) is proposed, and the base case is modified to include the proposed solution.  The simulation is repeated and system performance is again measured against established criteria.  This circular process is repeated until the system performance meets or exceeds reliability requirements. It should be noted, that at the conclusion of the study, only a single solution will be defined and implemented, so once a solution is defined for a scenario, it must be included in all scenarios to ensure that it works for all conditions.

A database is developed that includes technical data for generation, transmission lines, electrical system equipment and customer load levels and geographic distribution.  The TP will consult with the TCPC in developing forecast data for transmission, generation and demand response resources.  The basic methodologies for developing this forecast data are described below.

- Transmission:  The TP will use the existing transmission infrastructure as a starting point.  This data will be reviewed and any updates to the existing transmission data will be included in the basecase.  Future new additions to the transmission system may or may not be included.  If a new transmission project is under construction, then it will be included in the base case.  Future new transmission additions not under construction will not be included in the initial basecase unless both the TP and the TCPC agree that is should be included.  These projects may be included in some of the base and/or uncertainty scenarios and not others.  Other future new transmission additions will be considered as one of the mitigation options should transmission system reliability problems arise during the study.  

New regional transmission projects that affect the TP transmission system will be included if the project is in Phase 2 of the WECC Three Phase Rating Process and both the TP and the TCPC agree to include it.  These projects may be included in some of the base and/or uncertainty scenarios and not others.

- Generation: The TP will use the existing generation infrastructure as a starting point.  This generation data will be reviewed and any updates or changes will be included in the basecase.  Future generation additions, including generation from the TP generation interconnect and transmission service request queue may be included.  Since the TP currently has area stability margin concerns, proposed new generation additions may significantly change the transmission system configuration because of the mitigation requirements (i.e., transmission fixes) to connect and move power across the TP transmission system.  The Transmission System Planning process cannot ignore this.  The TP will review these potential new generation additions and their transmission fixes with the TCPC and then consider including them into the base scenarios and/or uncertainty scenarios.  It is likely that these new proposed projects might be included in some of the base scenarios and not others or may be include in the uncertainty scenarios only.

- Demand Response Resources:  The TP will obtain demand response resource forecasts directly from the LSE’s and customers within the TP footprint.  The TP will review these forecasts with the TCPC and then consider including them in the basecase.  The uncertainty scenarios may adjust these forecasts.

Using this database information, the TP will develop the basecases that are used to model the transmission system.  These basecases will also include this data for the entire WECC region.  The time frame that the base case data represents is for a very specific condition that may occur over the course of the year.  Thus, defining the conditions for a base case involves defining the generation, transmission configuration and customer load levels that are the focus of the study.  In order to study each hour of a year, 8760 different base cases could be developed (8760 hours = 8760 basecases).  This is impractical.  Transmission planning’s purpose is to ensure transmission system reliability under all operating conditions, which means that the studies need focus only on the conditions that may stress the system.  The following two examples describe stressed system conditions:

Example 1:  TP load at peak load conditions, such as a summer peak day, and base load generation will stress the local area transmission system serving the local area load.

Example 2:  TP load at light load conditions, such as the middle of the night, with base load generation levels and high export levels will stress the transmission system stability.

The technical analyses will use different engineering studies to evaluate the system performance.  These studies are designed to use different engineering perspective to ensure system reliability is maintained.  These methods include, but are not limited to, the following:

- Steady-State Powerflow Analyses

- Post Transient Steady-State Powerflow Analyses (or Steady-State Post Fault Analysis)

- Transient Stability Analyses (or Dynamic Analyses)

- Fault Duty Analyses

- Reactive Margin Analyses

A study of the transmission system under static conditions is a steady-state powerflow study, and a study over time is called a transient stability study.  The steady state powerflow analysis is a static evaluation of a local area transmission system that examines the transmission system under normal operating conditions with all lines in-service and with single and multiple transmission lines or elements out-of-service (i.e., N-1, N-2, N-1-1, etc. conditions).  Note that the “-1” in N-1 represents the number of transmission elements that are out of service.  A transient stability study (i.e., a dynamic simulation study) evaluates the transmission system performance on a progressive time dependent basis.  These studies evaluate credible outage events to determine if the transmission system will recover to acceptable steady-state operation after the outage.  The studies include an assortment of outage events that are intended to provide a thorough test of the reliability of the transmission system.  After a powerflow simulation is completed, a search of the simulation results for unacceptable thermal overloads and voltage excursions is made.  Unacceptable transmission system performance must be corrected by including transmission and non-transmission (e.g., demand-side resource, generation, etc.) fixes into a second simulation.  Additional mitigation or fixes are included in the simulation until a valid solution is found.  A valid solution is one that meets the reliability criteria describe below.  Economic and system performance information for this scenario is identified and retained for comparative analysis between scenarios during the decision step.

The credible “worst case” single and multiple fault events must be simulated to determine if the transmission system will recover to acceptable steady-state operation.  A dynamic simulation includes an assortment of outage events that are intended to provide a thorough test of the reliability of the transmission system.

Each scenario study must evaluate the effectiveness of existing Remedial Action Schemes (“RAS”) within the TP transmission system.  A RAS is used to maintain system reliability for voltage performance problems.  These RAS include the Rapid City DC Tie RAS, the Wyodak Tripping Scheme, the Neil Simpson II Tripping Scheme, the future Wygen II Tripping Scheme and the future Reno Load Dropping Scheme.  The Rapid City DC Tie RAS either blocks or runs back the power flow across the DC tie based upon 230 kV outages, Rapid City load and on-line Rapid City generation.  This RAS is not a WECC certified RAS/SPS.  The generator and load tripping schemes are all used to correct first-swing voltage violations following a disturbance in the Wyodak area.  These generator or load tripping schemes are not WECC certified RAS/SPS’.  The TP may also consider an Overload Mitigation Scheme (“OMS”) to control for thermal overloading.  See the Criteria section for a more detailed discussion of the RAS and OMS use.

From these studies and analysis of the changes in system steady-state and transient voltage levels after the loss of a single line, multiple lines, or generating units; changes in the line and equipment thermal loading conditions; changes in Volt-Ampere reactive (“VAr”) requirements (voltage support); and unacceptable frequency excursions are scrutinized.  All relevant reliability criteria are applied in these evaluations. Reliability criteria are defined in the Reliability Criteria section of this document.

The TP will also conduct fault duty and reactive margin studies as needed.  A fault duty study is a study of electrical current interrupting devices (e.g., breakers) to ensure the device can open under maximum load conditions.  When a fault or short circuit occurs on a power line, the protective relay equipment detects the increased current (i.e., fault current) flowing in the line and signals the line’s circuit breakers to open.  When the circuit breakers open, they must be capable of interrupting the full fault current.  The worst-case fault current is commonly referred to as the “fault-duty”.  A reactive margin study is a study to ensure that the transmission system has sufficient voltage control to maintain adequate voltage levels.

### Decision

An objective of a system planning study is to evaluate the range of potential transmission and non-transmission (e.g., demand side management, generation, conservation, etc.) solutions within the technical study and determine the best solution. The primary purpose of the decision phase is to provide descriptive information about the system and the problem (risk, cost, etc.) and identify the best solution or mitigation to resolve the problem. The TP will use selection criteria and weighting to provide a ranking of the solution(s). The TP will seek input from the TCPC in identifying and weighting the criteria to use in selecting the appropriate solution. This information along with documented advantages and disadvantages of each solution will be used to aid in selecting best solution or mitigation that achieves the objectives of the transmission plan.  Selection criteria may include, but is not limited to, the following:

- Total present value of upgrade costs

- Time available to implement upgrade

- System performance with each solution

- Probability of scenario requiring a solution

- Environmental assessment and/or costs

- Non-quantifiable assessment

The primary purpose of the selection criteria is to provide descriptive information (e.g., costs, risks, etc.) about the system and solution(s) needed to resolve the problems.  This information can be ordered or weighted so that stakeholders can understand the differences between the scenarios and provide input to the TP.  The TP Coordination Committee and TP management can then use this information to make an informed decision regarding future transmission investment to serve future network load and point-to-point requests.  Once approved, the solution will be prioritized into the TP Business and Strategic Plans.

### Reporting

The TP, with input from the TCPC, will develop a report that describes the study plan, scenarios, technical studies, selection criteria and selected solutions. The final report will be published on the BHBE OASIS web page.  It is the TP’s intent to publish a formal report annually, with the first report due Q4 2009.

## Load Forecast Methodology

Pursuant to FERC MOD-016, the TP will obtain load forecasts from Load Serving Entities (“LSE”) within the TP.  A summer and winter peak load forecast will be collected from the LSE’s within the TP for use in the study.  The LSE’s peak load forecasts will be summed, assuming they are time coincident, to calculate the TP area load forecast.  The loads within the TP are metered and tracked.  That is, the loads are well defined and monitored.  If the LSE and TP load forecast, based on actual historical loads, results are significantly different, the TP will attempt to reconcile these differences.  If the TP cannot reconcile these differences, the TP will choose which forecast to use in the study.

The TP peak load forecast will be adjusted to reflect demand response resource reductions, conservation reductions and other appropriate peak load modifying sources.

Once the TP load forecast is developed, this forecast is disaggregated to the respective transmission system load buses.  There are two types of load buses – (1) a load bus where the load does not change over time (e.g., a single large industrial load bus); and (2) a load bus where the load changes over time (e.g., residential load).  The TP will use its knowledge of load characteristics along with historical loading observations to estimate the individual load bus data in time.  The load bus forecasts are summed and compared to the TP load forecast.  If the two forecasts do not match, the TP will adjust the variable bus load forecasts until the two forecasts are the same.

## WECC Annual Study Program

In addition to the TP’s own transmission system planning study, it participates in the WECC Annual Study Program.  This program examines the reliability of electric transmission lines that are instrumental in moving electricity across the TP system from sources of supply inside and outside the TP system to markets inside and outside the TP system.  A detailed simulation model is used for steady state and dynamic event analysis that assesses electric transmission stability before and after a loss of a critical electrical element (e.g., transmission line).

Two types of study assessments are conducted - Operating Transfer Capability (“OTC”) studies and Bulk System Planning Studies.  The distinction between these studies is that the OTC study establishes the next season’s maximum transfer capacity for selected electric transmission paths and the planning studies evaluate the bulk transmission system’s adequacy and security 2-10 years into the future.  The Annual Study Program requires that each year approximately ten detailed studies be conducted to assess bulk electric transmission reliability.  The mix of operating and planning studies varies each year.

When conducting a seasonal OTC study, the TP will follow the WECC policy outlining the process, procedures and assumptions to use for OTC studies.  OTC studies are only required on WECC Rated Paths. The TP transmission system currently has no WECC paths.

The Bulk System Planning Study originates through the WECC System Review Work Group (“SRWG”) annual planning program.  The WECC study follows the same process as the OTC studies, except the season can range from 2 to 10 years in the future and may include proposed new facilities.  The goal of the planning study is to examine the reliability of the future transmission system under prescribed seasonal loads, generation patterns, and various outage conditions and to identify appropriate upgrades and/or new facilities to maintain bulk system reliability into the future.

## Economic Planning Study

Pursuant to FERC Order 890, stakeholders may request an Economic Planning Study.  The purpose of FERC Order 890 Economic Planning Studies is to ensure that customers may request studies that evaluate potential upgrades or other investments that could reduce congestion or integrate new resources and loads on an aggregated or regional basis (e.g., wind developers), not to assign cost responsibility for those investments or otherwise determine whether they should be implemented.  This is different than a proposed new generation interconnect study in that an interconnect study is to interconnect a new Generating Facility, or to increase the capacity of, or make a Material Modification to the operating characteristics of, an existing Generating Facility that is interconnected with the Transmission Provider's Transmission System.

A request for an Economic Planning Study may be confined to the TP transmission system, in which case the TP would complete the study using the methodology, criteria and process described within this document.  A request for an Economic Planning Study may be included as a scenario in the TP annual Transmission System Planning cycle if it is received prior to the establishment of the Study Plan.  If the request is received after the Study Plan has been developed, then the TP will process the request using methodology and process as described in Attachment K of the JOATT.

# Criteria

The TP reliability criteria, NERC/WECC regional reliability criteria (hereafter called Reliability Standards), FERC Standards and industry standards (e.g., IEEE Standards) are the basis for the TP transmission planning criteria.  This section describes these criteria.

## Reliability Criteria

Electric transmission reliability is concerned with the adequacy and security of the electric transmission system.  Adequacy addresses whether or not there is enough transmission, and security is the ability of the transmission system to withstand contingencies (i.e., the loss of a single or multiple transmission elements).  The TP uses two types of reliability criteria as shown below:

- TP Internal Reliability Criteria. A set of technical transmission reliability measures that have been established for the safe and reliable operation of the TP transmission system.

- The FERC Standards and WECC Reliability Criteria. A set of minimum performance standards for voltage excursions and voltage recovery after a credible outage event on the transmission system.

The TP uses these criteria in evaluating a change or addition to its electric transmission equipment and/or a change or addition to load or generation.  The TP will use these reliability criteria as needed to fully evaluate the impacts of lines, generation or loads to its electrical system.  The TP augments these criteria with other standards such as, but not limited to, the ANSI and IEEE standards.

The TP planning process ensures that changes that either directly or indirectly affects its transmission system will not materially reduce the reliability to existing customers.  The TP transmission system must remain dependable at all times so that it may provide reliable high quality service to all customers.

### Internal Reliability Criteria

The TP Internal Reliability criteria are used for reliability performance evaluation of the electric transmission system.  Steady state implies the condition on the transmission system before an outage, or after an outage and after switching occurs, regulators adjust, reactors or capacitors switch, and the electrical system has settled down (typically three minutes or more).  This latter condition is also called post-fault reliability requirements.

The TP criteria includes a collection of ANSI standards as well as past and current practices, that when applied with experienced engineering judgment, lead to a reliable and economical electric transmission system.  These criteria support the FERC Standards and WECC Reliability Criteria that disallow a blackout, voltage collapse, or cascading outages unless the initiating disturbance and corresponding impacts are confined to either a local network or a radial system.  An individual project or customer load may require an enhanced reliability requirement.

The TP plans a transmission system that provides acceptable voltage levels during system normal and outage conditions.  Areas of the TP system that are served by radial transmission service are excluded from single contingency evaluation.

#### Steady State, Transient  and Post-Transient Voltage Criteria

The steady state voltage criteria listed below are based on the assumption that all switching has taken place, all generators and transformer Load Tap Changer’s (“LTC”) have regulated voltages to set values, and capacitors or reactors are switched.  The TP follows the voltage limits as outlined in the Colorado Coordinated Planning Group’s Voltage Coordination Guide (“VCG”).

- The VCG defines “Acceptable Voltages” as between the range of 0.95 to 1.05 per unit.  “Acceptable Voltages” are used by the TP as the steady state voltage criteria.

- Transient voltage criteria require that the first-swing voltage at all buses shall not exceed 0.70 per unit.

- The VCG defines “Emergency Voltages” as in the range 0.9 to 0.95 and 1.05 to 1.10 per unit.   “Emergency Voltages” are used by the TP as the post fault voltage criteria.

#### Transmission Equipment Rating and Loading

Transmission facility ratings are determined by the individual Transmission Owners in accordance with their respective Facility Ratings Methodologies.

##### New Facility (Generation, Transmission, Load, or Line):

The primary goal when interconnecting a new facility to the TP transmission system is to ensure that the configuration of the interconnection will not materially reduce the performance of the transmission system or the reliability of service to customers.  A material reduction in reliability occurs when operation associated with a new facility or the interconnection itself precludes complying with TP criteria, WECC criteria, FERC Standards or good utility practice.  System reliability cannot be jeopardized as a result of connecting a new or up-graded facility.  Steady state and transient electric transmission system performance must meet or exceed TP, FERC and WECC performance criteria, and changes in fault duty cannot exceed equipment capability.  Any unacceptable system performance (voltage, thermal, frequency, fault duty, PV/QV, power quality, etc.) must be mitigated prior to interconnection.

The addition of new generation to the TP transmission system, including induction machine generation, must not cause unacceptable voltage fluctuations (i.e., a flicker problem) or harmonics as the units operate or as the generators cycle on and off during marginal operating conditions.  New generation connected to the TP transmission system shall comply with the limits set by IEEE Standard 519.  A high-speed dynamic responsive reactive device (e.g., STATCOM, Static Compensator) must be provided to protect against flicker unless it can be demonstrated that the new generation does not cause a flicker problem.  Instead of a high-speed dynamic responsive device, it might be proven that a different solution, such as managing individual wind turbine generation starts through a master control system, solves the flicker problem.

At the Point of Interconnection, the TP requires an interconnection facility to be able to produce or absorb Reactive Power between 0.9 leading to 0.9 lagging power factor to meet voltage schedules set by the Transmission Operator within a range of 0.95 to 1.05 of nominal.

Induction generators are assumed to have operational characteristics either through internal or external capabilities to operate throughout a power factor range of 0.95 leading to 0.95 lagging at the Point of Interconnection.

#### Remedial Action Scheme (RAS) and Overload Mitigation Scheme (OMS) Application

The TP may consider a RAS or an OMS application to protect the electric transmission system against certain types of events, but each application will be evaluated on a case-by-case basis with no assurance that a RAS or an OMS application will be acceptable.

        An OMS may be used to mitigate a thermal overload that is less than the thermal rating of a system element by tripping or by generator run-back.  This may be an appropriate application for an overload that results from a single (or multiple) contingency outage event.  The OMS may be manual (with a response time not greater than 30 minutes) or automated (with a faster response time).  Typically, response time for an OMS application is measured in tenths of seconds to minutes.  Generally, an OMS can be thought of as a scheme that can be backed up by relay operation or operator intervention if necessary.  An OMS will not be considered as acceptable mitigation for system element overload if its failure to operate properly could lead to widespread outages on the Bulk Electric System.

        A RAS may be used for certain single and multiple contingency outage events that result in unacceptable electric system reliability performance that is not related to minor thermal overloading and that requires a more immediate response (e.g., unacceptable transient stability performance).  A RAS must be an automated response to the outage.  Typically, response time for a RAS application is measured in cycles or at most a few seconds.  While the ranges of expected response times may overlap, there is a distinctly different character to a RAS.  It may be expected to meet a higher reliability standard, depending on the application.  There is no expectation that a transmission system operator could intervene if the RAS were to fail to operate.  Any RAS application must meet WECC system planning criteria.  The TP will submit any RAS application that may be proposed to the WECC RASRS for their approval if the RAS failure could lead to widespread outages on the Bulk Electric System of the Western Interconnection.  If a RAS does not receive the approval of the RASRS, the TP will not use it.

The TP criterion for the use of a RAS or an OMS is consistent with the performance requirements of existing facilities connected to the TP transmission system.  The TP criterion is stated below:

- N-1 Outage: For single contingency (N-1) conditions with a new facility (i.e., generation, transmission, load, line, etc.) connected, unacceptable system performance must be mitigated.

    - N-1 RAS Application: Any RAS application to mitigate for an N-1 outage should be comparable to other RAS applications on the TP transmission system.  The TP may consider a RAS for an N-1 three-phase line fault, but this will be evaluated on a case-by-case basis with no assurance that the RAS application will be acceptable.  A RAS application will meet FERC/NERC/WECC system planning criteria.  The TP will require that any RAS application, where failure of the RAS may cause widespread outages, be redundant and be approved by the WECC Remedial Action Scheme Reliability Subcommittee (“RASRS”).

    - N-1 OMS application for line overloads: Using an OMS may be acceptable to mitigate (i.e., reduce overload) for a thermal overload condition caused by a single contingency.  Each overload situation will be evaluated on a case-by-case basis with no assurance that the TP will choose to apply an OMS instead of system changes or enhancement.  In all instances, an OMS must:

      - Limit loading to below 100% of rated capacity;

      - Allow no accelerated loss of life, or degradation of utility equipment per accepted industry standards and/or good utility practice;

      - Maintain a safe system;

      - Limit conductor loading to not exceed the conductor’s maximum design.

    - N-1 OMS application for transformer overloads:  Using an OMS may be acceptable to mitigate (i.e., reduce the overload) for a transformer thermal overload condition caused by the loss of a single system element (i.e., line, parallel transformer, etc.).  Using an OMS for transformer overloads may be applied if the overload does not exceed the one hour allowable overload per unit rating as specified in the Transmission Owners Facility Rating Methodology.  For transformer overloads greater than one hour allowable overload per unit rating, an OMS is unacceptable mitigation.  In all instances, an OMS must:

      - Limit the overload duration to less than 30 minutes;

      - Maintain a safe system;

      - Allow no accelerated loss of life, or degradation of utility equipment per accepted industry standards and/or good utility practice.

- N-2 (double or greater) Outage: The TP may accept an OMS for thermal overloads or a RAS as the primary mitigation for an N-2 (or greater) outage condition.  Each application would be evaluated on a case-by-case basis with no assurance that the TP will choose to utilize an OMS or RAS scheme instead of system changes or enhancement.  Any application may be required to be redundant and must meet FERC Standards and WECC criteria.

- Any RAS application will meet WECC system planning criteria.  The TP will require that any RAS application that may cause widespread outages if the RAS fails to perform as designed be redundant and be approved by the WECC RASRS.

The TP may consider an OMS for a creditable N-2 (or greater) outage condition.  Each OMS application will be evaluated on a case-by-case basis with no assurance that the OMS application will be acceptable.  Any N-2 OMS application may be required to be redundant.

- RAS Application for a Stuck Breaker:  The TP may consider a RAS application to mitigate for a stuck breaker contingency.  Each RAS application will be evaluated on a case-by-case basis with no assurance that the RAS application will be acceptable.  Any RAS will meet WECC system planning criteria.  The TP will require that any RAS application that may cause widespread outages if the RAS fails to perform as designed be redundant and be approved by the WECC RASRS.

- RAS Application for a Transformer Outage:  The TP may consider a RAS application to mitigate for a transformer outage.  However, it is recognized and may not be acceptable because application of a RAS for the catastrophic loss of a transformer could require the local system operations to be reduced until a suitable transformer is installed.  Each RAS application will be evaluated on a case-by-case basis with no assurance that the RAS application will be acceptable.  Any RAS application may be required to be redundant and meet WECC system planning criteria.  The TP will require that the WECC RASRS approve any RAS application.

#### Voltage Ride Through

The TP will follow FERC and WECC voltage ride through criteria as appropriate.  Under certain circumstances, the TP may require the generation to trip offline to maintain system reliability instead of riding through the event.

#### Harmonics

Because some generation facilities, such as wind generation, may include large capacitor banks to supply adequate voltage support, and power electronic installations to accommodate the induction generators that are used for such facilities, and because both such facilities may introduce harmonic currents either due to resonances at harmonic frequencies or through inverter circuitry that is capable of introducing harmonic currents, the TP may require a study be conducted to evaluate the potential for unacceptable levels of harmonic currents that may be introduced by the facility.   This study should be performed along with the Facilities Study for the project.  The TP will supply the system Thevenin Equivalent impedance of its power system at the Point of Interconnection for the purpose of completing this study.  This can be used to verify that no harmonic of the system frequency will be above acceptable levels [see IEEE standard 519-1992 and ANSI standard C84.1-1989].  The project will be required to mitigate any harmonics levels outside of acceptable limits.

#### Sub-synchronous Resonance

Currently none of the TP transmission lines are series compensated.   However, should series compensation be identified as a solution to mitigate criteria violations, A Sub-synchronous Resonance (“SSR”) study will be required to evaluate risk to area generators.  Furthermore, the addition of a new generation project may require additional study to evaluate the exposure of each generator connected directly to or near any future series compensation system.  The TP welcomes the opportunity to participate in any SSR studies.

### FERC Standard Requirements and WECC Reliability Criteria

The FERC Standards and the WECC Reliability Criteria are used to evaluate the system performance under steady state and transient stability and the recovery performance of the TP transmission system. These criteria apply to all of the TP electric transmission system.  The following table, copied from NERC Standards, shows the tabled values that the TP will follows.

Table I.  Transmission Systems Standards  — Normal and Contingency Conditions*

| Category | Contingencies |  | System Limits or Impacts |
| --- | --- | --- | --- |
|  | Initiating Event(s) and Contingency Element(s) | Elements Out of Service | Thermal Limits | Voltage Limits | System Stable | Loss of Demand or Curtailed Firm Transfers | Cascading c Outages |
| A - No Contingencies | All Facilities in Service | None | Applicable Rating a (A/R) | Applicable Rating a (A/R) | Yes | No | No |
| B - Event resulting in the loss of a single element. | Single Line Ground (SLG) or 3-Phase (3Ø) Fault, with Normal Clearing: 1. Generator 2. Transmission Circuit 3. Transformer Loss of an Element without a Fault. | Single Single Single Single | A/R A/R A/R A/R | A/R A/R A/R A/R | Yes Yes Yes Yes | No b No b No b No b | No No No No |
|  | Single Pole Block, Normal Clearingf: 4. Single Pole (dc) Line | Single | A/R | A/R | Yes | Nob | No |
| C - Event(s) resulting in the loss of two or more (multiple) elements. | SLG Fault, with Normal Clearingf: 1. Bus Section 2. Breaker (failure or internal fault) | Multiple Multiple | A/R A/R | A/R A/R | Yes Yes | Planned/Controlledd Planned/Controlledd | No No |
|  | SLG or 3Ø Fault, with Normal Clearingf, Manual System Adjustments, followed by another SLG or 3Ø Fault, with Normal Clearingf: 3. Category B (B1, B2, B3, or B4) contingency, manual system adjustments, followed by another Category B (B1, B2, B3, or B4) contingency | Multiple | A/R | A/R | Yes | Planned/Controlledd | No |
|  | Bipolar Block, with Normal Clearingf: 4. Bipolar (dc) Line Fault (non 3Ø), with Normal Clearingf: 5. Any two circuits of a multiple circuit towerlineg | Multiple Multiple | A/R A/R | A/R A/R | Yes Yes | Planned/Controlledd Planned/Controlledd | No No |
|  | SLG Fault, with Delayed Clearingf (stuck breaker or protection system failure): 6. Generator 8. Transformer 7. Transmission Circuit 9. Bus Section | Multiple Multiple | A/R A/R | A/R A/R | Yes Yes | Planned/Controlledd Planned/Controlledd | No No |
| D e - Extreme event resulting in two or more (multiple) elements removed or cascading out of service | 3Ø Fault, with Delayed Clearing f (stuck breaker or protection system failure): 1. Generator 3. Transformer 2. Transmission Circuit 4. Bus Section 3Ø Fault, with Normal Clearingf: Breaker (failure or internal fault) Other: 6. Loss of towerline with three or more circuits 7. All transmission lines on a common right-of way 8. Loss of a substation (one voltage level plus transformers) 9. Loss of a switching station (one voltage level plus transformers) 10. Loss of all generating units at a station 11. Loss of a large load or major load center 12. Failure of a fully redundant special protection system (or remedial action scheme) to operate when required 13. Operation, partial operation, or misoperation of a fully redundant special protection system (or remedial action scheme) in response to an event or abnormal system condition for which it was not intended to operate 14. Impact of severe power swings or oscillations from disturbances in another Regional Council. | Evaluate for risks and consequences. May involve substantial loss of customer demand and generation in a widespread area or areas. Portions or all of the interconnected systems may or may not achieve a new, stable operating point. Evaluation of these events may require joint studies with neighboring systems. |

# Footnotes

Western Area Power Administration and PacifiCorp.

TCPC is a stakeholder committee that meets regularly with the TP to provided input and comments throughout the TP planning study cycle.  Membership is open and communication is open and transparent.  For more information see Attachment K to the JOATT on the BHBE OASIS Website (http:/www.oatioasis.com/BHBE/).

For example: WECC System Review Work Group (SRWG), WECC LRS Subcommittee, WECC Transmission Studies Subcommittee, Colorado Coordinated Planning Group, etc.

Demand-side resource, generation, interruptible load, etc.

The PSS/E model automatically completes a transient stability study by running the computer model repeatedly over time and recording how the generation and transmission elements change over time as the result of an outage.  A sequence of results is produced that depict how the generation and transmission system equipment responds to this outage condition.  The time step must be very small to accurately capture transmission system changes because generation and load are matched instantaneously.  For example, a dynamic study runs a powerflow simulation of the system, with progressive “real” time adjustments, every ¼ cycle or 0.00417 seconds.  Thus to make a 5 second study, the program must be run 1200 times.

The TPs model the WECC transmission system using the PTI PSS/E software.  The TP base case data includes the 69 kV to 230 kV transmission system data.

WECC is in the process of removing standards that duplicate the FERC Standards; so only the more stringent WECC criteria will remain.

The FERC Standards are implemented by NERC.

* Any Region may implement standards that are more stringent, but not inconsistent with NERC’s industry-wide standards.

# Text boxes

2. Technical Study

1. Study Plan and

Scenario Development

3. Decision

4. Reporting

FIGURE 1: CUS Transmission System Planning Process

Reporting

Decision

Study Plan and Scenario Development

Technical Study

ID Study Objective,

Assumptions, Develop Study

Plan and Scenarios

Develop Base Cases

and Perform

Simulations, multi

-

year

Analyze Results and

Identify Reliability

Problems

Identify Mitigation or

Solutions to Reliability

Problems

Document Solutions,

ID

Advantages/disadvantages

to Each Solution

Publish  Report

CUS Coordination

Committee and

TP

Management Decision

Prioritize Into Company

Business and Strategic

Plan

Reliability

Criteria Met?

Another Scenario?

Identify Best Solution:

a. Selection Criteria

b. Advantages/Disadvantages

Re

-

Run Simulations

Y

N

Y

N

TCPC

Input

Timing Of Other Public input

determined by

TCPC

Construction and

Rate Base support

TCPC

= Transmission Coordination and Planning Committee

CCPG

and

WECC

As Requested/Needed

Analyze Results and

Identify Reliability

Problems

TCPC

Input

TCPC

Input

TCPC

Input

CCPG

Review,

WECC

Project

Review Process

CCPG

Review,

WECC

Project

Review Process

FIGURE 2: TP Transmission System Planning Process

Reporting

Decision

Study Plan and Scenario Development

Technical Study

ID Study Objective,

Assumptions, Develop Study

Plan and Scenarios

Develop Base Cases

and Perform

Simulations, multi

-

year

Analyze Results and

Identify Reliability

Problems

Identify Mitigation or

Solutions to Reliability

Problems

Document Solutions,

ID

Advantages/disadvantages

to Each Solution

Publish  Report

CUS Coordination

Committee and

TP

Management Decision

Prioritize Into Company

Business and Strategic

Plan

Reliability

Criteria Met?

Another Scenario?

Identify Best Solution:

a. Selection Criteria

b. Advantages/Disadvantages

Re

-

Run Simulations

Y

N

Y

N

TCPC

Input

Timing Of Other Public input

determined by

TCPC

Construction and

Rate Base support

TCPC

= Transmission Coordination and Planning Committee

CCPG

and

WECC

As Requested/Needed

Analyze Results and

Identify Reliability

Problems

TCPC

Input

TCPC

Input

TCPC

Input

CCPG

Review,

WECC

Project

Review Process

CCPG

Review,

WECC

Project

Review Process