Black Hills Colorado Electric

2010 Local Transmission Plan

Study Scope

- Background

As specified in Attachment K to the Black Hills Colorado Transmission (BHCT) Open Access Transmission Tariff (OATT), the Transmission Provider (TP) will develop a Local Transmission Plan (“LTP”) on an annual basis to ensure the transmission system is designed to reliably accommodate resource and load growth as well as transmission service obligations.  The LTP study will utilize an open and coordinated process involving input from stakeholders consistent with the principles, practices, policy, and procedures set forth in the Attachment K.  Additional information on the LTP process can be found on the BHCT website (http://www.oatioasis.com/BHCT) within the “Transmission Planning” folder.

- Base Case Scenarios

The LTP will focus on 2014 for the near-term study period and 2020 for the far-term study period.  The study years were selected based on several factors including base case availability, planned system upgrades, and previously completed planning studies. For both study years a heavy summer and light winter loading scenario will be created.  All generation and transmission system upgrades currently under construction or submitted for regulatory review will be included in the base case scenarios.  Proposed projects may be included in the base case upon agreement of both the TP and TCPC.  Descriptions of any changes made to a starting case to create a base case scenario will be documented.

The Colorado Coordinated Planning Group (CCPG) 2009 Compliance Study cases will be used to develop the on and off-peak base case scenarios due to the high level of scrutiny they recently endured during the CCPG study process.  Table 1 includes the proposed study cases and their respective starting case.

Table 1: LTP Study Cases

| 2014 LTP Study Case | Starting Case | 2020 LTP Study Case | Starting Case |
| --- | --- | --- | --- |
| 2014 Heavy Summer | CCPG 2014 Heavy Winter | 2020 Heavy Summer | CCPG 2020 Heavy Winter |
| 2014 Light Winter | CCPG 2014 Light Winter | 2020 Light Winter | CCPG 2020 Heavy Winter |

- Uncertainty Scenarios

Uncertainty scenarios will be created for each of the base case scenarios in Table 1 as deemed necessary based on stakeholder input.  Uncertainty scenarios provide an opportunity to evaluate generation and transmission projects submitted for consideration but not included in the base case, as well as demand response resources.

- Power Flow Simulations

For each base case and uncertainty scenario identified above power flow simulations will be run to evaluate system performance under NERC TPL Standard Category A-C events and worst case Category D events.  Black Hills’ gas-fired generation will be dispatched as deemed appropriate to mitigate performance criteria violations.

The study will monitor the performance of the transmission system in the Western Interconnection roughly bounded by the Walsenburg, San Luis Valley, Poncha, Lamar, and Midway substations.

- Dynamic Simulations

Dynamic simulations will be run to evaluate system performance under worst-case NERC TPL Standard Category B, C and D events based upon the results of the power flow simulations.