## Final Loss Calculation
Fall Only |  |  | 284739.4287 |  | 39256.8098 | [5 empty] | 15051680.7615 | 1.892% | 0.2608%
[12 empty] | Transmission | GSU
|  | Control | T-only | T-only | GSU-only | GSU-only | GSU+T | GSU+T |  | GSU |  | Losses | Losses |  |  | GSU | T-only | T-only | GSU-only | GSU-only
|  | Area | Losses | Losses | Losses | Losses | Losses | Losses |  | High Side | POD | vs | vs | Model |  | Low Side | Losses | Losses | Losses | Losses
Date | Time | Load | (MW) | (%) | (MW) | (%) | (MW) | (%) | Hour # | Load (MW) | Load (MW) | POD Load | POD Load | Points | Hour # | Load(MW) | (MW) | Slope | (MW) | Slope
2017-10-22 | 5 | 4497 | 127.0147 | 2.824% | 15.8138 | 0.3517% | 142.8285 | 3.176% | 1 | 4481.1862 | 4354.1715 | 2.917% | 0.3632% |  | 3 | 4557.4424 | 126.1214 | -0.01478 | 15.8045 | -0.00015293
2017-10-22 | 4 | 4500 | 126.9704 | 2.822% | 15.8133 | 0.3514% | 142.7837 | 3.173% | 2 | 4484.1867 | 4357.2163 | 2.914% | 0.3629% |  | 296 | 5537.8252 | 111.6314 | 0.012275 | 15.6546 | 0.0013009
2017-10-01 | 5 | 4540 | 126.3792 | 2.784% | 15.8072 | 0.3482% | 142.1864 | 3.132% | 3 | 4524.1928 | 4397.8136 | 2.874% | 0.3594% | 4555.6536 | 1694 | 7925.9442 | 140.946 | 0.0074822 | 18.7614 | 0.0024757
2017-10-01 | 4 | 4571 | 125.921 | 2.755% | 15.8025 | 0.3457% | 141.7235 | 3.1% | 4 | 4555.1975 | 4429.2765 | 2.843% | 0.3568% |  | 2151 | 10306.461 | 158.7575 | -0.01228 | 24.6549 | 0.0017636
2017-10-22 | 3 | 4585 | 125.7141 | 2.742% | 15.8003 | 0.3446% | 141.5144 | 3.086% | 5 | 4569.1997 | 4443.4856 | 2.829% | 0.3556% |  | 2183 | 11141.8339 | 148.4994 |  | 26.1282
2017-10-01 | 6 | 4589 | 125.655 | 2.738% | 15.7997 | 0.3443% | 141.4547 | 3.082% | 6 | 4573.2003 | 4447.5453 | 2.825% | 0.3552%
2017-11-05 | 4 | 4590 | 125.6402 | 2.737% | 15.7996 | 0.3442% | 141.4397 | 3.081% | 7 | 4574.2004 | 4448.5603 | 2.824% | 0.3552%
2017-10-22 | 6 | 4626 | 125.1081 | 2.704% | 15.7941 | 0.3414% | 140.9021 | 3.046% | 8 | 4610.2059 | 4485.0979 | 2.789% | 0.3521%
2017-11-05 | 3 | 4632 | 125.0194 | 2.699% | 15.7931 | 0.341% | 140.8126 | 3.04% | 9 | 4616.2069 | 4491.1874 | 2.784% | 0.3516%
2017-11-05 | 5 | 4637 | 124.9455 | 2.695% | 15.7924 | 0.3406% | 140.7379 | 3.035% | 10 | 4621.2076 | 4496.2621 | 2.779% | 0.3512%
2017-10-01 | 3 | 4639 | 124.916 | 2.693% | 15.7921 | 0.3404% | 140.708 | 3.033% | 11 | 4623.2079 | 4498.292 | 2.777% | 0.3511%
2017-09-10 | 5 | 4668 | 124.4873 | 2.667% | 15.7876 | 0.3382% | 140.275 | 3.005% | 12 | 4652.2124 | 4527.725 | 2.749% | 0.3487%
2017-10-29 | 5 | 4674 | 124.3987 | 2.662% | 15.7867 | 0.3378% | 140.1854 | 2.999% | 13 | 4658.2133 | 4533.8146 | 2.744% | 0.3482%
2017-10-02 | 4 | 4676 | 124.3691 | 2.66% | 15.7864 | 0.3376% | 140.1555 | 2.997% | 14 | 4660.2136 | 4535.8445 | 2.742% | 0.348%
2017-09-11 | 4 | 4677 | 124.3543 | 2.659% | 15.7863 | 0.3375% | 140.1406 | 2.996% | 15 | 4661.2137 | 4536.8594 | 2.741% | 0.348%
2017-10-29 | 4 | 4681 | 124.2952 | 2.655% | 15.7856 | 0.3372% | 140.0808 | 2.993% | 16 | 4665.2144 | 4540.9192 | 2.737% | 0.3476%
2017-10-02 | 3 | 4697 | 124.0587 | 2.641% | 15.7832 | 0.336% | 139.8419 | 2.977% | 17 | 4681.2168 | 4557.1581 | 2.722% | 0.3463%
2017-11-06 | 3 | 4699 | 124.0292 | 2.639% | 15.7829 | 0.3359% | 139.812 | 2.975% | 18 | 4683.2171 | 4559.188 | 2.72% | 0.3462%
2017-09-11 | 3 | 4709 | 123.8814 | 2.631% | 15.7814 | 0.3351% | 139.6627 | 2.966% | 19 | 4693.2186 | 4569.3373 | 2.711% | 0.3454%
2017-09-10 | 4 | 4719 | 123.7336 | 2.622% | 15.7798 | 0.3344% | 139.5134 | 2.956% | 20 | 4703.2202 | 4579.4866 | 2.702% | 0.3446%
2017-11-05 | 2 | 4723 | 123.6744 | 2.619% | 15.7792 | 0.3341% | 139.4537 | 2.953% | 21 | 4707.2208 | 4583.5463 | 2.698% | 0.3443%
2017-10-21 | 4 | 4725 | 123.6449 | 2.617% | 15.7789 | 0.3339% | 139.4238 | 2.951% | 22 | 4709.2211 | 4585.5762 | 2.696% | 0.3441%
2017-11-06 | 4 | 4725 | 123.6449 | 2.617% | 15.7789 | 0.3339% | 139.4238 | 2.951% | 23 | 4709.2211 | 4585.5762 | 2.696% | 0.3441%
2017-09-10 | 6 | 4730 | 123.571 | 2.612% | 15.7781 | 0.3336% | 139.3491 | 2.946% | 24 | 4714.2219 | 4590.6509 | 2.692% | 0.3437%
2017-10-23 | 4 | 4731 | 123.5562 | 2.612% | 15.778 | 0.3335% | 139.3342 | 2.945% | 25 | 4715.222 | 4591.6658 | 2.691% | 0.3436%
2017-10-22 | 2 | 4736 | 123.4823 | 2.607% | 15.7772 | 0.3331% | 139.2595 | 2.94% | 26 | 4720.2228 | 4596.7405 | 2.686% | 0.3432%
2017-10-29 | 3 | 4744 | 123.3641 | 2.6% | 15.776 | 0.3325% | 139.1401 | 2.933% | 27 | 4728.224 | 4604.8599 | 2.679% | 0.3426%
2017-11-04 | 4 | 4748 | 123.3049 | 2.597% | 15.7754 | 0.3323% | 139.0803 | 2.929% | 28 | 4732.2246 | 4608.9197 | 2.675% | 0.3423%
2017-10-23 | 3 | 4750 | 123.2754 | 2.595% | 15.7751 | 0.3321% | 139.0505 | 2.927% | 29 | 4734.2249 | 4610.9495 | 2.674% | 0.3421%
2017-10-29 | 6 | 4751 | 123.2606 | 2.594% | 15.7749 | 0.332% | 139.0355 | 2.926% | 30 | 4735.2251 | 4611.9645 | 2.673% | 0.342%
2017-11-05 | 6 | 4762 | 123.098 | 2.585% | 15.7733 | 0.3312% | 138.8713 | 2.916% | 31 | 4746.2267 | 4623.1287 | 2.663% | 0.3412%
2017-10-21 | 5 | 4766 | 123.0389 | 2.582% | 15.7726 | 0.3309% | 138.8115 | 2.913% | 32 | 4750.2274 | 4627.1885 | 2.659% | 0.3409%
2017-11-04 | 5 | 4773 | 122.9354 | 2.576% | 15.7716 | 0.3304% | 138.707 | 2.906% | 33 | 4757.2284 | 4634.293 | 2.653% | 0.3403%
2017-10-01 | 7 | 4778 | 122.8615 | 2.571% | 15.7708 | 0.3301% | 138.6324 | 2.901% | 34 | 4762.2292 | 4639.3676 | 2.648% | 0.3399%
2017-10-17 | 3 | 4782 | 122.8024 | 2.568% | 15.7702 | 0.3298% | 138.5726 | 2.898% | 35 | 4766.2298 | 4643.4274 | 2.645% | 0.3396%
2017-10-17 | 4 | 4782 | 122.8024 | 2.568% | 15.7702 | 0.3298% | 138.5726 | 2.898% | 36 | 4766.2298 | 4643.4274 | 2.645% | 0.3396%
2017-11-06 | 2 | 4782 | 122.8024 | 2.568% | 15.7702 | 0.3298% | 138.5726 | 2.898% | 37 | 4766.2298 | 4643.4274 | 2.645% | 0.3396%
2017-09-11 | 5 | 4789 | 122.699 | 2.562% | 15.7691 | 0.3293% | 138.4681 | 2.891% | 38 | 4773.2309 | 4650.5319 | 2.638% | 0.3391%
2017-10-02 | 2 | 4795 | 122.6103 | 2.557% | 15.7682 | 0.3288% | 138.3785 | 2.886% | 39 | 4779.2318 | 4656.6215 | 2.633% | 0.3386%
2017-09-10 | 3 | 4798 | 122.5659 | 2.555% | 15.7677 | 0.3286% | 138.3337 | 2.883% | 40 | 4782.2323 | 4659.6663 | 2.63% | 0.3384%
2017-10-02 | 5 | 4801 | 122.5216 | 2.552% | 15.7673 | 0.3284% | 138.2889 | 2.88% | 41 | 4785.2327 | 4662.7111 | 2.628% | 0.3382%
2017-09-11 | 2 | 4803 | 122.492 | 2.55% | 15.767 | 0.3283% | 138.259 | 2.879% | 42 | 4787.233 | 4664.741 | 2.626% | 0.338%
2017-10-01 | 2 | 4804 | 122.4773 | 2.549% | 15.7668 | 0.3282% | 138.2441 | 2.878% | 43 | 4788.2332 | 4665.7559 | 2.625% | 0.3379%
2017-09-09 | 5 | 4813 | 122.3442 | 2.542% | 15.7655 | 0.3276% | 138.1097 | 2.87% | 44 | 4797.2345 | 4674.8903 | 2.617% | 0.3372%
2017-10-29 | 2 | 4813 | 122.3442 | 2.542% | 15.7655 | 0.3276% | 138.1097 | 2.87% | 45 | 4797.2345 | 4674.8903 | 2.617% | 0.3372%
2017-10-25 | 4 | 4828 | 122.1225 | 2.529% | 15.7632 | 0.3265% | 137.8857 | 2.856% | 46 | 4812.2368 | 4690.1143 | 2.604% | 0.3361%
2017-11-19 | 4 | 4828 | 122.1225 | 2.529% | 15.7632 | 0.3265% | 137.8857 | 2.856% | 47 | 4812.2368 | 4690.1143 | 2.604% | 0.3361%
2017-11-04 | 3 | 4832 | 122.0634 | 2.526% | 15.7625 | 0.3262% | 137.826 | 2.852% | 48 | 4816.2375 | 4694.174 | 2.6% | 0.3358%
2017-11-05 | 2 | 4835 | 122.0191 | 2.524% | 15.7621 | 0.326% | 137.7812 | 2.85% | 49 | 4819.2379 | 4697.2188 | 2.598% | 0.3356%
2017-10-25 | 3 | 4836 | 122.0043 | 2.523% | 15.7619 | 0.3259% | 137.7662 | 2.849% | 50 | 4820.2381 | 4698.2338 | 2.597% | 0.3355%
2017-09-10 | 7 | 4839 | 121.96 | 2.52% | 15.7615 | 0.3257% | 137.7214 | 2.846% | 51 | 4823.2385 | 4701.2786 | 2.594% | 0.3353%
2017-10-15 | 5 | 4840 | 121.9452 | 2.52% | 15.7613 | 0.3256% | 137.7065 | 2.845% | 52 | 4824.2387 | 4702.2935 | 2.593% | 0.3352%
2017-09-09 | 4 | 4841 | 121.9304 | 2.519% | 15.7612 | 0.3256% | 137.6916 | 2.844% | 53 | 4825.2388 | 4703.3084 | 2.592% | 0.3351%
2017-10-03 | 4 | 4847 | 121.8417 | 2.514% | 15.7603 | 0.3252% | 137.602 | 2.839% | 54 | 4831.2397 | 4709.398 | 2.587% | 0.3347%
2017-10-22 | 7 | 4847 | 121.8417 | 2.514% | 15.7603 | 0.3252% | 137.602 | 2.839% | 55 | 4831.2397 | 4709.398 | 2.587% | 0.3347%
2017-11-19 | 5 | 4850 | 121.7974 | 2.511% | 15.7598 | 0.3249% | 137.5572 | 2.836% | 56 | 4834.2402 | 4712.4428 | 2.585% | 0.3344%
2017-10-23 | 5 | 4856 | 121.7087 | 2.506% | 15.7589 | 0.3245% | 137.4676 | 2.831% | 57 | 4840.2411 | 4718.5324 | 2.579% | 0.334%
2017-11-19 | 3 | 4858 | 121.6791 | 2.505% | 15.7586 | 0.3244% | 137.4377 | 2.829% | 58 | 4842.2414 | 4720.5623 | 2.578% | 0.3338%
2017-10-15 | 4 | 4864 | 121.5905 | 2.5% | 15.7577 | 0.324% | 137.3481 | 2.824% | 59 | 4848.2423 | 4726.6519 | 2.572% | 0.3334%
2017-11-07 | 4 | 4869 | 121.5166 | 2.496% | 15.7569 | 0.3236% | 137.2735 | 2.819% | 60 | 4853.2431 | 4731.7265 | 2.568% | 0.333%
2017-11-03 | 4 | 4873 | 121.4574 | 2.492% | 15.7563 | 0.3233% | 137.2137 | 2.816% | 61 | 4857.2437 | 4735.7863 | 2.565% | 0.3327%
2017-10-23 | 2 | 4878 | 121.3836 | 2.488% | 15.7555 | 0.323% | 137.1391 | 2.811% | 62 | 4862.2445 | 4740.8609 | 2.56% | 0.3323%
2017-10-17 | 2 | 4886 | 121.2653 | 2.482% | 15.7543 | 0.3224% | 137.0196 | 2.804% | 63 | 4870.2457 | 4748.9804 | 2.554% | 0.3317%
2017-09-09 | 6 | 4892 | 121.1766 | 2.477% | 15.7534 | 0.322% | 136.93 | 2.799% | 64 | 4876.2466 | 4755.07 | 2.548% | 0.3313%
2017-11-04 | 6 | 4893 | 121.1619 | 2.476% | 15.7532 | 0.322% | 136.9151 | 2.798% | 65 | 4877.2468 | 4756.0849 | 2.548% | 0.3312%
2017-10-15 | 6 | 4898 | 121.088 | 2.472% | 15.7525 | 0.3216% | 136.8404 | 2.794% | 66 | 4882.2475 | 4761.1596 | 2.543% | 0.3309%
2017-11-06 | 5 | 4899 | 121.0732 | 2.471% | 15.7523 | 0.3215% | 136.8255 | 2.793% | 67 | 4883.2477 | 4762.1745 | 2.542% | 0.3308%
2017-10-04 | 4 | 4902 | 121.0288 | 2.469% | 15.7518 | 0.3213% | 136.7807 | 2.79% | 68 | 4886.2482 | 4765.2193 | 2.54% | 0.3306%
2017-10-17 | 5 | 4903 | 121.0141 | 2.468% | 15.7517 | 0.3213% | 136.7657 | 2.789% | 69 | 4887.2483 | 4766.2343 | 2.539% | 0.3305%
2017-11-03 | 3 | 4904 | 120.9993 | 2.467% | 15.7515 | 0.3212% | 136.7508 | 2.789% | 70 | 4888.2485 | 4767.2492 | 2.538% | 0.3304%
2017-10-21 | 2 | 4909 | 120.9254 | 2.463% | 15.7508 | 0.3209% | 136.6761 | 2.784% | 71 | 4893.2492 | 4772.3239 | 2.534% | 0.33%
2017-10-03 | 3 | 4913 | 120.8663 | 2.46% | 15.7502 | 0.3206% | 136.6164 | 2.781% | 72 | 4897.2498 | 4776.3836 | 2.53% | 0.3298%
2017-11-07 | 3 | 4914 | 120.8515 | 2.459% | 15.75 | 0.3205% | 136.6015 | 2.78% | 73 | 4898.25 | 4777.3985 | 2.53% | 0.3297%
2017-09-04 | 5 | 4915 | 120.8367 | 2.459% | 15.7499 | 0.3204% | 136.5865 | 2.779% | 74 | 4899.2501 | 4778.4135 | 2.529% | 0.3296%
2017-10-21 | 3 | 4918 | 120.7924 | 2.456% | 15.7494 | 0.3202% | 136.5417 | 2.776% | 75 | 4902.2506 | 4781.4583 | 2.526% | 0.3294%
2017-09-08 | 4 | 4919 | 120.7776 | 2.455% | 15.7492 | 0.3202% | 136.5268 | 2.775% | 76 | 4903.2508 | 4782.4732 | 2.525% | 0.3293%
2017-10-20 | 3 | 4925 | 120.6889 | 2.451% | 15.7483 | 0.3198% | 136.4372 | 2.77% | 77 | 4909.2517 | 4788.5628 | 2.52% | 0.3289%
2017-10-03 | 5 | 4927 | 120.6593 | 2.449% | 15.748 | 0.3196% | 136.4074 | 2.769% | 78 | 4911.252 | 4790.5926 | 2.519% | 0.3287%
2017-10-20 | 4 | 4927 | 120.6593 | 2.449% | 15.748 | 0.3196% | 136.4074 | 2.769% | 79 | 4911.252 | 4790.5926 | 2.519% | 0.3287%
2017-11-02 | 4 | 4927 | 120.6593 | 2.449% | 15.748 | 0.3196% | 136.4074 | 2.769% | 80 | 4911.252 | 4790.5926 | 2.519% | 0.3287%
2017-10-21 | 6 | 4932 | 120.5854 | 2.445% | 15.7473 | 0.3193% | 136.3327 | 2.764% | 81 | 4916.2527 | 4795.6673 | 2.514% | 0.3284%
2017-11-06 | 1 | 4934 | 120.5559 | 2.443% | 15.7469 | 0.3192% | 136.3028 | 2.763% | 82 | 4918.2531 | 4797.6972 | 2.513% | 0.3282%
2017-11-02 | 3 | 4938 | 120.4968 | 2.44% | 15.7463 | 0.3189% | 136.2431 | 2.759% | 83 | 4922.2537 | 4801.7569 | 2.509% | 0.3279%
2017-09-04 | 4 | 4943 | 120.4229 | 2.436% | 15.7456 | 0.3185% | 136.1684 | 2.755% | 84 | 4927.2544 | 4806.8316 | 2.505% | 0.3276%
2017-09-09 | 3 | 4948 | 120.349 | 2.432% | 15.7448 | 0.3182% | 136.0938 | 2.75% | 85 | 4932.2552 | 4811.9062 | 2.501% | 0.3272%
2017-10-04 | 3 | 4954 | 120.2603 | 2.428% | 15.7439 | 0.3178% | 136.0042 | 2.745% | 86 | 4938.2561 | 4817.9958 | 2.496% | 0.3268%
2017-10-24 | 4 | 4955 | 120.2455 | 2.427% | 15.7437 | 0.3177% | 135.9892 | 2.744% | 87 | 4939.2563 | 4819.0108 | 2.495% | 0.3267%
2017-10-29 | 7 | 4955 | 120.2455 | 2.427% | 15.7437 | 0.3177% | 135.9892 | 2.744% | 88 | 4939.2563 | 4819.0108 | 2.495% | 0.3267%
2017-10-25 | 2 | 4957 | 120.2159 | 2.425% | 15.7434 | 0.3176% | 135.9594 | 2.743% | 89 | 4941.2566 | 4821.0406 | 2.494% | 0.3266%
2017-11-03 | 5 | 4958 | 120.2012 | 2.424% | 15.7433 | 0.3175% | 135.9444 | 2.742% | 90 | 4942.2567 | 4822.0556 | 2.493% | 0.3265%
2017-10-25 | 5 | 4962 | 120.142 | 2.421% | 15.7427 | 0.3173% | 135.8847 | 2.739% | 91 | 4946.2573 | 4826.1153 | 2.489% | 0.3262%
2017-10-22 | 1 | 4970 | 120.0238 | 2.415% | 15.7414 | 0.3167% | 135.7652 | 2.732% | 92 | 4954.2586 | 4834.2348 | 2.483% | 0.3256%
2017-11-19 | 6 | 4972 | 119.9942 | 2.413% | 15.7411 | 0.3166% | 135.7354 | 2.73% | 93 | 4956.2589 | 4836.2646 | 2.481% | 0.3255%
2017-10-15 | 3 | 4976 | 119.9351 | 2.41% | 15.7405 | 0.3163% | 135.6756 | 2.727% | 94 | 4960.2595 | 4840.3244 | 2.478% | 0.3252%
2017-10-02 | 1 | 4979 | 119.8908 | 2.408% | 15.7401 | 0.3161% | 135.6308 | 2.724% | 95 | 4963.2599 | 4843.3692 | 2.475% | 0.325%
2017-11-19 | 2 | 4979 | 119.8908 | 2.408% | 15.7401 | 0.3161% | 135.6308 | 2.724% | 96 | 4963.2599 | 4843.3692 | 2.475% | 0.325%
2017-11-07 | 5 | 4984 | 119.8169 | 2.404% | 15.7393 | 0.3158% | 135.5562 | 2.72% | 97 | 4968.2607 | 4848.4438 | 2.471% | 0.3246%
2017-11-03 | 2 | 4986 | 119.7873 | 2.402% | 15.739 | 0.3157% | 135.5263 | 2.718% | 98 | 4970.261 | 4850.4737 | 2.47% | 0.3245%
2017-10-01 | 8 | 4990 | 119.7282 | 2.399% | 15.7384 | 0.3154% | 135.4666 | 2.715% | 99 | 4974.2616 | 4854.5334 | 2.466% | 0.3242%
2017-09-04 | 6 | 4993 | 119.6839 | 2.397% | 15.7379 | 0.3152% | 135.4218 | 2.712% | 100 | 4977.2621 | 4857.5782 | 2.464% | 0.324%
2017-10-20 | 2 | 4998 | 119.61 | 2.393% | 15.7372 | 0.3149% | 135.3471 | 2.708% | 101 | 4982.2628 | 4862.6529 | 2.46% | 0.3236%
2017-09-08 | 5 | 4999 | 119.5952 | 2.392% | 15.737 | 0.3148% | 135.3322 | 2.707% | 102 | 4983.263 | 4863.6678 | 2.459% | 0.3236%
2017-09-30 | 5 | 5000 | 119.5804 | 2.392% | 15.7369 | 0.3147% | 135.3173 | 2.706% | 103 | 4984.2631 | 4864.6827 | 2.458% | 0.3235%
2017-11-04 | 2 | 5002 | 119.5508 | 2.39% | 15.7366 | 0.3146% | 135.2874 | 2.705% | 104 | 4986.2634 | 4866.7126 | 2.457% | 0.3234%
2017-09-11 | 1 | 5003 | 119.5361 | 2.389% | 15.7364 | 0.3145% | 135.2725 | 2.704% | 105 | 4987.2636 | 4867.7275 | 2.456% | 0.3233%
2017-09-10 | 2 | 5004 | 119.5213 | 2.389% | 15.7362 | 0.3145% | 135.2575 | 2.703% | 106 | 4988.2638 | 4868.7425 | 2.455% | 0.3232%
2017-11-05 | 7 | 5006 | 119.4917 | 2.387% | 15.7359 | 0.3143% | 135.2277 | 2.701% | 107 | 4990.2641 | 4870.7723 | 2.453% | 0.3231%
2017-09-08 | 3 | 5008 | 119.4622 | 2.385% | 15.7356 | 0.3142% | 135.1978 | 2.7% | 108 | 4992.2644 | 4872.8022 | 2.452% | 0.3229%
2017-10-04 | 5 | 5009 | 119.4474 | 2.385% | 15.7355 | 0.3141% | 135.1829 | 2.699% | 109 | 4993.2645 | 4873.8171 | 2.451% | 0.3229%
2017-10-14 | 5 | 5011 | 119.4178 | 2.383% | 15.7352 | 0.314% | 135.153 | 2.697% | 110 | 4995.2648 | 4875.847 | 2.449% | 0.3227%
2017-09-30 | 4 | 5021 | 119.27 | 2.375% | 15.7336 | 0.3134% | 135.0037 | 2.689% | 111 | 5005.2664 | 4885.9963 | 2.441% | 0.322%
2017-10-14 | 4 | 5027 | 119.1813 | 2.371% | 15.7327 | 0.313% | 134.9141 | 2.684% | 112 | 5011.2673 | 4892.0859 | 2.436% | 0.3216%
2017-11-07 | 2 | 5034 | 119.0779 | 2.365% | 15.7317 | 0.3125% | 134.8095 | 2.678% | 113 | 5018.2683 | 4899.1905 | 2.431% | 0.3211%
2017-09-10 | 8 | 5036 | 119.0483 | 2.364% | 15.7314 | 0.3124% | 134.7797 | 2.676% | 114 | 5020.2686 | 4901.2203 | 2.429% | 0.321%
2017-10-28 | 4 | 5037 | 119.0335 | 2.363% | 15.7312 | 0.3123% | 134.7647 | 2.675% | 115 | 5021.2688 | 4902.2353 | 2.428% | 0.3209%
2017-11-02 | 5 | 5037 | 119.0335 | 2.363% | 15.7312 | 0.3123% | 134.7647 | 2.675% | 116 | 5021.2688 | 4902.2353 | 2.428% | 0.3209%
2017-10-24 | 5 | 5039 | 119.004 | 2.362% | 15.7309 | 0.3122% | 134.7349 | 2.674% | 117 | 5023.2691 | 4904.2651 | 2.427% | 0.3208%
2017-10-28 | 3 | 5040 | 118.9892 | 2.361% | 15.7307 | 0.3121% | 134.7199 | 2.673% | 118 | 5024.2693 | 4905.2801 | 2.426% | 0.3207%
2017-10-17 | 1 | 5044 | 118.9301 | 2.358% | 15.7301 | 0.3119% | 134.6602 | 2.67% | 119 | 5028.2699 | 4909.3398 | 2.423% | 0.3204%
2017-11-02 | 2 | 5049 | 118.8562 | 2.354% | 15.7294 | 0.3115% | 134.5855 | 2.666% | 120 | 5033.2706 | 4914.4145 | 2.419% | 0.3201%
2017-10-05 | 4 | 5052 | 118.8118 | 2.352% | 15.7289 | 0.3113% | 134.5407 | 2.663% | 121 | 5036.2711 | 4917.4593 | 2.416% | 0.3199%
2017-09-04 | 7 | 5053 | 118.7971 | 2.351% | 15.7288 | 0.3113% | 134.5258 | 2.662% | 122 | 5037.2712 | 4918.4742 | 2.415% | 0.3198%
2017-10-01 | 1 | 5057 | 118.7379 | 2.348% | 15.7281 | 0.311% | 134.4661 | 2.659% | 123 | 5041.2719 | 4922.5339 | 2.412% | 0.3195%
2017-11-08 | 3 | 5058 | 118.7232 | 2.347% | 15.728 | 0.311% | 134.4511 | 2.658% | 124 | 5042.272 | 4923.5489 | 2.411% | 0.3194%
2017-10-24 | 3 | 5060 | 118.6936 | 2.346% | 15.7277 | 0.3108% | 134.4213 | 2.657% | 125 | 5044.2723 | 4925.5787 | 2.41% | 0.3193%
2017-10-03 | 2 | 5063 | 118.6493 | 2.343% | 15.7272 | 0.3106% | 134.3765 | 2.654% | 126 | 5047.2728 | 4928.6235 | 2.407% | 0.3191%
2017-11-08 | 4 | 5063 | 118.6493 | 2.343% | 15.7272 | 0.3106% | 134.3765 | 2.654% | 127 | 5047.2728 | 4928.6235 | 2.407% | 0.3191%
2017-10-22 | 8 | 5074 | 118.4867 | 2.335% | 15.7255 | 0.3099% | 134.2122 | 2.645% | 128 | 5058.2745 | 4939.7878 | 2.399% | 0.3183%
2017-10-19 | 3 | 5075 | 118.4719 | 2.334% | 15.7254 | 0.3099% | 134.1973 | 2.644% | 129 | 5059.2746 | 4940.8027 | 2.398% | 0.3183%
2017-09-30 | 6 | 5076 | 118.4571 | 2.334% | 15.7252 | 0.3098% | 134.1824 | 2.643% | 130 | 5060.2748 | 4941.8176 | 2.397% | 0.3182%
2017-10-25 | 1 | 5076 | 118.4571 | 2.334% | 15.7252 | 0.3098% | 134.1824 | 2.643% | 131 | 5060.2748 | 4941.8176 | 2.397% | 0.3182%
2017-10-20 | 5 | 5083 | 118.3537 | 2.328% | 15.7242 | 0.3093% | 134.0778 | 2.638% | 132 | 5067.2758 | 4948.9222 | 2.392% | 0.3177%
2017-10-19 | 4 | 5087 | 118.2945 | 2.325% | 15.7236 | 0.3091% | 134.0181 | 2.635% | 133 | 5071.2764 | 4952.9819 | 2.388% | 0.3175%
2017-09-04 | 3 | 5089 | 118.265 | 2.324% | 15.7232 | 0.309% | 133.9882 | 2.633% | 134 | 5073.2768 | 4955.0118 | 2.387% | 0.3173%
2017-10-28 | 2 | 5091 | 118.2354 | 2.322% | 15.7229 | 0.3088% | 133.9584 | 2.631% | 135 | 5075.2771 | 4957.0416 | 2.385% | 0.3172%
2017-10-15 | 7 | 5092 | 118.2206 | 2.322% | 15.7228 | 0.3088% | 133.9434 | 2.63% | 136 | 5076.2772 | 4958.0566 | 2.384% | 0.3171%
2017-11-05 | 1 | 5095 | 118.1763 | 2.319% | 15.7223 | 0.3086% | 133.8986 | 2.628% | 137 | 5079.2777 | 4961.1014 | 2.382% | 0.3169%
2017-10-23 | 1 | 5098 | 118.132 | 2.317% | 15.7219 | 0.3084% | 133.8538 | 2.626% | 138 | 5082.2781 | 4964.1462 | 2.38% | 0.3167%
2017-09-12 | 4 | 5099 | 118.1172 | 2.316% | 15.7217 | 0.3083% | 133.8389 | 2.625% | 139 | 5083.2783 | 4965.1611 | 2.379% | 0.3166%
2017-10-07 | 4 | 5101 | 118.0876 | 2.315% | 15.7214 | 0.3082% | 133.809 | 2.623% | 140 | 5085.2786 | 4967.191 | 2.377% | 0.3165%
2017-10-07 | 5 | 5103 | 118.0581 | 2.314% | 15.7211 | 0.3081% | 133.7792 | 2.622% | 141 | 5087.2789 | 4969.2208 | 2.376% | 0.3164%
2017-10-04 | 2 | 5110 | 117.9546 | 2.308% | 15.72 | 0.3076% | 133.6746 | 2.616% | 142 | 5094.28 | 4976.3254 | 2.37% | 0.3159%
2017-10-14 | 6 | 5111 | 117.9398 | 2.308% | 15.7199 | 0.3076% | 133.6597 | 2.615% | 143 | 5095.2801 | 4977.3403 | 2.37% | 0.3158%
2017-09-07 | 4 | 5118 | 117.8364 | 2.302% | 15.7188 | 0.3071% | 133.5552 | 2.61% | 144 | 5102.2812 | 4984.4448 | 2.364% | 0.3154%
2017-09-12 | 3 | 5122 | 117.7772 | 2.299% | 15.7182 | 0.3069% | 133.4954 | 2.606% | 145 | 5106.2818 | 4988.5046 | 2.361% | 0.3151%
2017-09-09 | 7 | 5123 | 117.7625 | 2.299% | 15.718 | 0.3068% | 133.4805 | 2.606% | 146 | 5107.282 | 4989.5195 | 2.36% | 0.315%
2017-10-06 | 4 | 5123 | 117.7625 | 2.299% | 15.718 | 0.3068% | 133.4805 | 2.606% | 147 | 5107.282 | 4989.5195 | 2.36% | 0.315%
2017-10-16 | 4 | 5124 | 117.7477 | 2.298% | 15.7179 | 0.3068% | 133.4656 | 2.605% | 148 | 5108.2821 | 4990.5344 | 2.359% | 0.315%
2017-10-21 | 1 | 5124 | 117.7477 | 2.298% | 15.7179 | 0.3068% | 133.4656 | 2.605% | 149 | 5108.2821 | 4990.5344 | 2.359% | 0.315%
2017-10-29 | 1 | 5126 | 117.7181 | 2.296% | 15.7176 | 0.3066% | 133.4357 | 2.603% | 150 | 5110.2824 | 4992.5643 | 2.358% | 0.3148%
2017-10-19 | 2 | 5127 | 117.7033 | 2.296% | 15.7174 | 0.3066% | 133.4208 | 2.602% | 151 | 5111.2826 | 4993.5792 | 2.357% | 0.3148%
2017-10-26 | 3 | 5128 | 117.6886 | 2.295% | 15.7173 | 0.3065% | 133.4058 | 2.602% | 152 | 5112.2827 | 4994.5942 | 2.356% | 0.3147%
2017-09-24 | 5 | 5129 | 117.6738 | 2.294% | 15.7171 | 0.3064% | 133.3909 | 2.601% | 153 | 5113.2829 | 4995.6091 | 2.356% | 0.3146%
2017-10-28 | 5 | 5131 | 117.6442 | 2.293% | 15.7168 | 0.3063% | 133.361 | 2.599% | 154 | 5115.2832 | 4997.639 | 2.354% | 0.3145%
2017-10-05 | 5 | 5132 | 117.6294 | 2.292% | 15.7167 | 0.3062% | 133.3461 | 2.598% | 155 | 5116.2833 | 4998.6539 | 2.353% | 0.3144%
2017-10-15 | 2 | 5134 | 117.5999 | 2.291% | 15.7164 | 0.3061% | 133.3162 | 2.597% | 156 | 5118.2836 | 5000.6838 | 2.352% | 0.3143%
2017-09-09 | 2 | 5138 | 117.5408 | 2.288% | 15.7158 | 0.3059% | 133.2565 | 2.594% | 157 | 5122.2842 | 5004.7435 | 2.349% | 0.314%
2017-10-26 | 4 | 5138 | 117.5408 | 2.288% | 15.7158 | 0.3059% | 133.2565 | 2.594% | 158 | 5122.2842 | 5004.7435 | 2.349% | 0.314%
2017-10-18 | 3 | 5139 | 117.526 | 2.287% | 15.7156 | 0.3058% | 133.2416 | 2.593% | 159 | 5123.2844 | 5005.7584 | 2.348% | 0.314%
2017-10-14 | 3 | 5144 | 117.4521 | 2.283% | 15.7148 | 0.3055% | 133.1669 | 2.589% | 160 | 5128.2852 | 5010.8331 | 2.344% | 0.3136%
2017-11-08 | 2 | 5150 | 117.3634 | 2.279% | 15.7139 | 0.3051% | 133.0773 | 2.584% | 161 | 5134.2861 | 5016.9227 | 2.339% | 0.3132%
2017-09-04 | 8 | 5153 | 117.3191 | 2.277% | 15.7135 | 0.3049% | 133.0325 | 2.582% | 162 | 5137.2865 | 5019.9675 | 2.337% | 0.313%
2017-09-24 | 6 | 5153 | 117.3191 | 2.277% | 15.7135 | 0.3049% | 133.0325 | 2.582% | 163 | 5137.2865 | 5019.9675 | 2.337% | 0.313%
2017-10-05 | 3 | 5153 | 117.3191 | 2.277% | 15.7135 | 0.3049% | 133.0325 | 2.582% | 164 | 5137.2865 | 5019.9675 | 2.337% | 0.313%
2017-09-08 | 2 | 5155 | 117.2895 | 2.275% | 15.7132 | 0.3048% | 133.0027 | 2.58% | 165 | 5139.2868 | 5021.9973 | 2.336% | 0.3129%
2017-09-30 | 3 | 5155 | 117.2895 | 2.275% | 15.7132 | 0.3048% | 133.0027 | 2.58% | 166 | 5139.2868 | 5021.9973 | 2.336% | 0.3129%
2017-11-04 | 7 | 5161 | 117.2008 | 2.271% | 15.7122 | 0.3044% | 132.9131 | 2.575% | 167 | 5145.2878 | 5028.0869 | 2.331% | 0.3125%
2017-09-07 | 5 | 5165 | 117.1417 | 2.268% | 15.7116 | 0.3042% | 132.8533 | 2.572% | 168 | 5149.2884 | 5032.1467 | 2.328% | 0.3122%
2017-10-06 | 5 | 5171 | 117.053 | 2.264% | 15.7107 | 0.3038% | 132.7637 | 2.567% | 169 | 5155.2893 | 5038.2363 | 2.323% | 0.3118%
2017-10-18 | 4 | 5177 | 116.9643 | 2.259% | 15.7098 | 0.3035% | 132.6741 | 2.563% | 170 | 5161.2902 | 5044.3259 | 2.319% | 0.3114%
2017-10-20 | 1 | 5179 | 116.9348 | 2.258% | 15.7095 | 0.3033% | 132.6443 | 2.561% | 171 | 5163.2905 | 5046.3557 | 2.317% | 0.3113%
2017-09-12 | 5 | 5181 | 116.9052 | 2.256% | 15.7092 | 0.3032% | 132.6144 | 2.56% | 172 | 5165.2908 | 5048.3856 | 2.316% | 0.3112%
2017-10-16 | 3 | 5188 | 116.8018 | 2.251% | 15.7081 | 0.3028% | 132.5099 | 2.554% | 173 | 5172.2919 | 5055.4901 | 2.31% | 0.3107%
2017-09-25 | 4 | 5194 | 116.7131 | 2.247% | 15.7072 | 0.3024% | 132.4203 | 2.549% | 174 | 5178.2928 | 5061.5797 | 2.306% | 0.3103%
2017-10-26 | 2 | 5196 | 116.6835 | 2.246% | 15.7069 | 0.3023% | 132.3904 | 2.548% | 175 | 5180.2931 | 5063.6096 | 2.304% | 0.3102%
2017-10-18 | 2 | 5200 | 116.6244 | 2.243% | 15.7063 | 0.302% | 132.3307 | 2.545% | 176 | 5184.2937 | 5067.6693 | 2.301% | 0.3099%
2017-09-07 | 3 | 5204 | 116.5653 | 2.24% | 15.7057 | 0.3018% | 132.2709 | 2.542% | 177 | 5188.2943 | 5071.7291 | 2.298% | 0.3097%
2017-11-19 | 1 | 5215 | 116.4027 | 2.232% | 15.704 | 0.3011% | 132.1067 | 2.533% | 178 | 5199.296 | 5082.8933 | 2.29% | 0.309%
2017-10-06 | 3 | 5217 | 116.3731 | 2.231% | 15.7037 | 0.301% | 132.0768 | 2.532% | 179 | 5201.2963 | 5084.9232 | 2.289% | 0.3088%
2017-10-16 | 5 | 5222 | 116.2992 | 2.227% | 15.7029 | 0.3007% | 132.0022 | 2.528% | 180 | 5206.2971 | 5089.9978 | 2.285% | 0.3085%
2017-09-12 | 2 | 5223 | 116.2845 | 2.226% | 15.7028 | 0.3006% | 131.9872 | 2.527% | 181 | 5207.2972 | 5091.0128 | 2.284% | 0.3084%
2017-09-11 | 6 | 5225 | 116.2549 | 2.225% | 15.7024 | 0.3005% | 131.9574 | 2.525% | 182 | 5209.2976 | 5093.0426 | 2.283% | 0.3083%
2017-11-08 | 5 | 5228 | 116.2106 | 2.223% | 15.702 | 0.3003% | 131.9126 | 2.523% | 183 | 5212.298 | 5096.0874 | 2.28% | 0.3081%
2017-10-07 | 3 | 5229 | 116.1958 | 2.222% | 15.7018 | 0.3003% | 131.8976 | 2.522% | 184 | 5213.2982 | 5097.1024 | 2.28% | 0.3081%
2017-10-29 | 8 | 5232 | 116.1514 | 2.22% | 15.7014 | 0.3001% | 131.8528 | 2.52% | 185 | 5216.2986 | 5100.1472 | 2.277% | 0.3079%
2017-09-24 | 4 | 5234 | 116.1219 | 2.219% | 15.7011 | 0.3% | 131.823 | 2.519% | 186 | 5218.2989 | 5102.177 | 2.276% | 0.3077%
2017-10-07 | 6 | 5235 | 116.1071 | 2.218% | 15.7009 | 0.2999% | 131.808 | 2.518% | 187 | 5219.2991 | 5103.192 | 2.275% | 0.3077%
2017-10-21 | 7 | 5236 | 116.0923 | 2.217% | 15.7008 | 0.2999% | 131.7931 | 2.517% | 188 | 5220.2992 | 5104.2069 | 2.274% | 0.3076%
2017-11-07 | 1 | 5236 | 116.0923 | 2.217% | 15.7008 | 0.2999% | 131.7931 | 2.517% | 189 | 5220.2992 | 5104.2069 | 2.274% | 0.3076%
2017-11-19 | 7 | 5239 | 116.048 | 2.215% | 15.7003 | 0.2997% | 131.7483 | 2.515% | 190 | 5223.2997 | 5107.2517 | 2.272% | 0.3074%
2017-09-17 | 5 | 5245 | 115.9593 | 2.211% | 15.6994 | 0.2993% | 131.6587 | 2.51% | 191 | 5229.3006 | 5113.3413 | 2.268% | 0.307%
2017-10-28 | 1 | 5246 | 115.9445 | 2.21% | 15.6992 | 0.2993% | 131.6438 | 2.509% | 192 | 5230.3008 | 5114.3562 | 2.267% | 0.307%
2017-10-19 | 5 | 5255 | 115.8115 | 2.204% | 15.6979 | 0.2987% | 131.5094 | 2.503% | 193 | 5239.3021 | 5123.4906 | 2.26% | 0.3064%
2017-10-02 | 6 | 5257 | 115.7819 | 2.202% | 15.6976 | 0.2986% | 131.4795 | 2.501% | 194 | 5241.3024 | 5125.5205 | 2.259% | 0.3063%
2017-10-24 | 2 | 5257 | 115.7819 | 2.202% | 15.6976 | 0.2986% | 131.4795 | 2.501% | 195 | 5241.3024 | 5125.5205 | 2.259% | 0.3063%
2017-09-25 | 5 | 5260 | 115.7376 | 2.2% | 15.6971 | 0.2984% | 131.4347 | 2.499% | 196 | 5244.3029 | 5128.5653 | 2.257% | 0.3061%
2017-11-02 | 1 | 5268 | 115.6194 | 2.195% | 15.6959 | 0.2979% | 131.3152 | 2.493% | 197 | 5252.3041 | 5136.6848 | 2.251% | 0.3056%
2017-11-03 | 1 | 5268 | 115.6194 | 2.195% | 15.6959 | 0.2979% | 131.3152 | 2.493% | 198 | 5252.3041 | 5136.6848 | 2.251% | 0.3056%
2017-09-24 | 7 | 5271 | 115.575 | 2.193% | 15.6954 | 0.2978% | 131.2704 | 2.49% | 199 | 5255.3046 | 5139.7296 | 2.249% | 0.3054%
2017-11-04 | 1 | 5274 | 115.5307 | 2.191% | 15.695 | 0.2976% | 131.2256 | 2.488% | 200 | 5258.305 | 5142.7744 | 2.246% | 0.3052%
2017-09-03 | 6 | 5278 | 115.4716 | 2.188% | 15.6943 | 0.2974% | 131.1659 | 2.485% | 201 | 5262.3057 | 5146.8341 | 2.244% | 0.3049%
2017-09-03 | 5 | 5284 | 115.3829 | 2.184% | 15.6934 | 0.297% | 131.0763 | 2.481% | 202 | 5268.3066 | 5152.9237 | 2.239% | 0.3046%
2017-10-03 | 1 | 5286 | 115.3533 | 2.182% | 15.6931 | 0.2969% | 131.0464 | 2.479% | 203 | 5270.3069 | 5154.9536 | 2.238% | 0.3044%
2017-10-19 | 1 | 5287 | 115.3386 | 2.182% | 15.693 | 0.2968% | 131.0315 | 2.478% | 204 | 5271.307 | 5155.9685 | 2.237% | 0.3044%
2017-09-25 | 3 | 5290 | 115.2942 | 2.179% | 15.6925 | 0.2966% | 130.9867 | 2.476% | 205 | 5274.3075 | 5159.0133 | 2.235% | 0.3042%
2017-09-17 | 6 | 5296 | 115.2055 | 2.175% | 15.6916 | 0.2963% | 130.8971 | 2.472% | 206 | 5280.3084 | 5165.1029 | 2.23% | 0.3038%
2017-09-30 | 7 | 5297 | 115.1908 | 2.175% | 15.6914 | 0.2962% | 130.8822 | 2.471% | 207 | 5281.3086 | 5166.1178 | 2.23% | 0.3037%
2017-10-28 | 6 | 5304 | 115.0873 | 2.17% | 15.6904 | 0.2958% | 130.7777 | 2.466% | 208 | 5288.3096 | 5173.2223 | 2.225% | 0.3033%
2017-11-08 | 1 | 5305 | 115.0725 | 2.169% | 15.6902 | 0.2958% | 130.7627 | 2.465% | 209 | 5289.3098 | 5174.2373 | 2.224% | 0.3032%
2017-10-16 | 2 | 5308 | 115.0282 | 2.167% | 15.6898 | 0.2956% | 130.7179 | 2.463% | 210 | 5292.3102 | 5177.2821 | 2.222% | 0.3031%
2017-09-04 | 2 | 5314 | 114.9395 | 2.163% | 15.6888 | 0.2952% | 130.6283 | 2.458% | 211 | 5298.3112 | 5183.3717 | 2.217% | 0.3027%
2017-09-09 | 8 | 5315 | 114.9247 | 2.162% | 15.6887 | 0.2952% | 130.6134 | 2.457% | 212 | 5299.3113 | 5184.3866 | 2.217% | 0.3026%
2017-09-10 | 1 | 5322 | 114.8213 | 2.157% | 15.6876 | 0.2948% | 130.5089 | 2.452% | 213 | 5306.3124 | 5191.4911 | 2.212% | 0.3022%
2017-10-26 | 5 | 5323 | 114.8065 | 2.157% | 15.6875 | 0.2947% | 130.4939 | 2.452% | 214 | 5307.3125 | 5192.5061 | 2.211% | 0.3021%
2017-10-15 | 8 | 5325 | 114.7769 | 2.155% | 15.6872 | 0.2946% | 130.4641 | 2.45% | 215 | 5309.3128 | 5194.5359 | 2.21% | 0.302%
2017-10-05 | 2 | 5331 | 114.6882 | 2.151% | 15.6862 | 0.2942% | 130.3745 | 2.446% | 216 | 5315.3138 | 5200.6255 | 2.205% | 0.3016%
2017-10-14 | 2 | 5335 | 114.6291 | 2.149% | 15.6856 | 0.294% | 130.3147 | 2.443% | 217 | 5319.3144 | 5204.6853 | 2.202% | 0.3014%
2017-10-01 | 24 | 5337 | 114.5996 | 2.147% | 15.6853 | 0.2939% | 130.2849 | 2.441% | 218 | 5321.3147 | 5206.7151 | 2.201% | 0.3013%
2017-10-21 | 24 | 5337 | 114.5996 | 2.147% | 15.6853 | 0.2939% | 130.2849 | 2.441% | 219 | 5321.3147 | 5206.7151 | 2.201% | 0.3013%
2017-09-03 | 7 | 5338 | 114.5848 | 2.147% | 15.6852 | 0.2938% | 130.2699 | 2.44% | 220 | 5322.3148 | 5207.7301 | 2.2% | 0.3012%
2017-11-05 | 24 | 5338 | 114.5848 | 2.147% | 15.6852 | 0.2938% | 130.2699 | 2.44% | 221 | 5322.3148 | 5207.7301 | 2.2% | 0.3012%
2017-09-17 | 4 | 5346 | 114.4665 | 2.141% | 15.6839 | 0.2934% | 130.1505 | 2.435% | 222 | 5330.3161 | 5215.8495 | 2.195% | 0.3007%
2017-10-03 | 6 | 5346 | 114.4665 | 2.141% | 15.6839 | 0.2934% | 130.1505 | 2.435% | 223 | 5330.3161 | 5215.8495 | 2.195% | 0.3007%
2017-10-14 | 7 | 5347 | 114.4518 | 2.14% | 15.6838 | 0.2933% | 130.1355 | 2.434% | 224 | 5331.3162 | 5216.8645 | 2.194% | 0.3006%
2017-09-30 | 2 | 5348 | 114.437 | 2.14% | 15.6836 | 0.2933% | 130.1206 | 2.433% | 225 | 5332.3164 | 5217.8794 | 2.193% | 0.3006%
2017-11-01 | 3 | 5353 | 114.3631 | 2.136% | 15.6829 | 0.293% | 130.0459 | 2.429% | 226 | 5337.3171 | 5222.9541 | 2.19% | 0.3003%
2017-10-04 | 1 | 5358 | 114.2892 | 2.133% | 15.6821 | 0.2927% | 129.9713 | 2.426% | 227 | 5342.3179 | 5228.0287 | 2.186% | 0.3%
2017-10-17 | 6 | 5359 | 114.2744 | 2.132% | 15.682 | 0.2926% | 129.9563 | 2.425% | 228 | 5343.318 | 5229.0437 | 2.185% | 0.2999%
2017-09-07 | 2 | 5361 | 114.2448 | 2.131% | 15.6816 | 0.2925% | 129.9265 | 2.424% | 229 | 5345.3184 | 5231.0735 | 2.184% | 0.2998%
2017-11-05 | 8 | 5361 | 114.2448 | 2.131% | 15.6816 | 0.2925% | 129.9265 | 2.424% | 230 | 5345.3184 | 5231.0735 | 2.184% | 0.2998%
2017-09-23 | 5 | 5366 | 114.1709 | 2.128% | 15.6809 | 0.2922% | 129.8518 | 2.42% | 231 | 5350.3191 | 5236.1482 | 2.18% | 0.2995%
2017-10-23 | 6 | 5366 | 114.1709 | 2.128% | 15.6809 | 0.2922% | 129.8518 | 2.42% | 232 | 5350.3191 | 5236.1482 | 2.18% | 0.2995%
2017-09-18 | 4 | 5371 | 114.097 | 2.124% | 15.6801 | 0.2919% | 129.7772 | 2.416% | 233 | 5355.3199 | 5241.2228 | 2.177% | 0.2992%
2017-10-18 | 1 | 5371 | 114.097 | 2.124% | 15.6801 | 0.2919% | 129.7772 | 2.416% | 234 | 5355.3199 | 5241.2228 | 2.177% | 0.2992%
2017-10-18 | 5 | 5371 | 114.097 | 2.124% | 15.6801 | 0.2919% | 129.7772 | 2.416% | 235 | 5355.3199 | 5241.2228 | 2.177% | 0.2992%
2017-11-01 | 2 | 5374 | 114.0527 | 2.122% | 15.6797 | 0.2918% | 129.7324 | 2.414% | 236 | 5358.3203 | 5244.2676 | 2.175% | 0.299%
2017-09-08 | 6 | 5375 | 114.0379 | 2.122% | 15.6795 | 0.2917% | 129.7174 | 2.413% | 237 | 5359.3205 | 5245.2826 | 2.174% | 0.2989%
2017-09-12 | 1 | 5381 | 113.9492 | 2.118% | 15.6786 | 0.2914% | 129.6278 | 2.409% | 238 | 5365.3214 | 5251.3722 | 2.17% | 0.2986%
2017-10-06 | 2 | 5390 | 113.8162 | 2.112% | 15.6772 | 0.2909% | 129.4934 | 2.402% | 239 | 5374.3228 | 5260.5066 | 2.164% | 0.298%
2017-10-26 | 1 | 5390 | 113.8162 | 2.112% | 15.6772 | 0.2909% | 129.4934 | 2.402% | 240 | 5374.3228 | 5260.5066 | 2.164% | 0.298%
2017-09-16 | 5 | 5391 | 113.8014 | 2.111% | 15.6771 | 0.2908% | 129.4785 | 2.402% | 241 | 5375.3229 | 5261.5215 | 2.163% | 0.298%
2017-09-03 | 4 | 5398 | 113.698 | 2.106% | 15.676 | 0.2904% | 129.374 | 2.397% | 242 | 5382.324 | 5268.626 | 2.158% | 0.2975%
2017-10-24 | 6 | 5400 | 113.6684 | 2.105% | 15.6757 | 0.2903% | 129.3441 | 2.395% | 243 | 5384.3243 | 5270.6559 | 2.157% | 0.2974%
2017-10-07 | 2 | 5404 | 113.6093 | 2.102% | 15.6751 | 0.2901% | 129.2844 | 2.392% | 244 | 5388.3249 | 5274.7156 | 2.154% | 0.2972%
2017-10-04 | 6 | 5406 | 113.5797 | 2.101% | 15.6748 | 0.29% | 129.2545 | 2.391% | 245 | 5390.3252 | 5276.7455 | 2.152% | 0.2971%
2017-11-01 | 4 | 5408 | 113.5502 | 2.1% | 15.6745 | 0.2898% | 129.2246 | 2.39% | 246 | 5392.3255 | 5278.7754 | 2.151% | 0.2969%
2017-11-03 | 6 | 5411 | 113.5058 | 2.098% | 15.674 | 0.2897% | 129.1798 | 2.387% | 247 | 5395.326 | 5281.8202 | 2.149% | 0.2968%
2017-11-06 | 6 | 5414 | 113.4615 | 2.096% | 15.6735 | 0.2895% | 129.135 | 2.385% | 248 | 5398.3265 | 5284.865 | 2.147% | 0.2966%
2017-10-01 | 9 | 5418 | 113.4024 | 2.093% | 15.6729 | 0.2893% | 129.0753 | 2.382% | 249 | 5402.3271 | 5288.9247 | 2.144% | 0.2963%
2017-09-23 | 6 | 5423 | 113.3285 | 2.09% | 15.6722 | 0.289% | 129.0006 | 2.379% | 250 | 5407.3278 | 5293.9994 | 2.141% | 0.296%
2017-09-20 | 4 | 5424 | 113.3137 | 2.089% | 15.672 | 0.2889% | 128.9857 | 2.378% | 251 | 5408.328 | 5295.0143 | 2.14% | 0.296%
2017-09-23 | 4 | 5428 | 113.2546 | 2.086% | 15.6714 | 0.2887% | 128.926 | 2.375% | 252 | 5412.3286 | 5299.074 | 2.137% | 0.2957%
2017-09-13 | 5 | 5429 | 113.2398 | 2.086% | 15.6713 | 0.2887% | 128.911 | 2.374% | 253 | 5413.3287 | 5300.089 | 2.137% | 0.2957%
2017-09-13 | 4 | 5430 | 113.225 | 2.085% | 15.6711 | 0.2886% | 128.8961 | 2.374% | 254 | 5414.3289 | 5301.1039 | 2.136% | 0.2956%
2017-09-09 | 1 | 5432 | 113.1955 | 2.084% | 15.6708 | 0.2885% | 128.8662 | 2.372% | 255 | 5416.3292 | 5303.1338 | 2.135% | 0.2955%
2017-09-24 | 3 | 5434 | 113.1659 | 2.083% | 15.6705 | 0.2884% | 128.8364 | 2.371% | 256 | 5418.3295 | 5305.1636 | 2.133% | 0.2954%
2017-09-10 | 24 | 5436 | 113.1363 | 2.081% | 15.6702 | 0.2883% | 128.8065 | 2.37% | 257 | 5420.3298 | 5307.1935 | 2.132% | 0.2953%
2017-11-01 | 1 | 5440 | 113.0772 | 2.079% | 15.6696 | 0.288% | 128.7468 | 2.367% | 258 | 5424.3304 | 5311.2532 | 2.129% | 0.295%
2017-10-25 | 6 | 5447 | 112.9738 | 2.074% | 15.6685 | 0.2877% | 128.6423 | 2.362% | 259 | 5431.3315 | 5318.3577 | 2.124% | 0.2946%
2017-11-04 | 24 | 5447 | 112.9738 | 2.074% | 15.6685 | 0.2877% | 128.6423 | 2.362% | 260 | 5431.3315 | 5318.3577 | 2.124% | 0.2946%
2017-09-16 | 6 | 5449 | 112.9442 | 2.073% | 15.6682 | 0.2875% | 128.6124 | 2.36% | 261 | 5433.3318 | 5320.3876 | 2.123% | 0.2945%
2017-09-30 | 8 | 5449 | 112.9442 | 2.073% | 15.6682 | 0.2875% | 128.6124 | 2.36% | 262 | 5433.3318 | 5320.3876 | 2.123% | 0.2945%
2017-09-17 | 7 | 5450 | 112.9294 | 2.072% | 15.668 | 0.2875% | 128.5975 | 2.36% | 263 | 5434.332 | 5321.4025 | 2.122% | 0.2944%
2017-10-15 | 1 | 5450 | 112.9294 | 2.072% | 15.668 | 0.2875% | 128.5975 | 2.36% | 264 | 5434.332 | 5321.4025 | 2.122% | 0.2944%
2017-10-28 | 24 | 5451 | 112.9146 | 2.071% | 15.6679 | 0.2874% | 128.5825 | 2.359% | 265 | 5435.3321 | 5322.4175 | 2.121% | 0.2944%
2017-11-07 | 6 | 5455 | 112.8555 | 2.069% | 15.6673 | 0.2872% | 128.5228 | 2.356% | 266 | 5439.3327 | 5326.4772 | 2.119% | 0.2941%
2017-09-22 | 4 | 5456 | 112.8407 | 2.068% | 15.6671 | 0.2872% | 128.5079 | 2.355% | 267 | 5440.3329 | 5327.4921 | 2.118% | 0.2941%
2017-09-08 | 1 | 5459 | 112.7964 | 2.066% | 15.6667 | 0.287% | 128.4631 | 2.353% | 268 | 5443.3333 | 5330.5369 | 2.116% | 0.2939%
2017-09-20 | 5 | 5459 | 112.7964 | 2.066% | 15.6667 | 0.287% | 128.4631 | 2.353% | 269 | 5443.3333 | 5330.5369 | 2.116% | 0.2939%
2017-09-24 | 8 | 5460 | 112.7816 | 2.066% | 15.6665 | 0.2869% | 128.4481 | 2.353% | 270 | 5444.3335 | 5331.5519 | 2.115% | 0.2938%
2017-10-16 | 24 | 5463 | 112.7373 | 2.064% | 15.6661 | 0.2868% | 128.4033 | 2.35% | 271 | 5447.3339 | 5334.5967 | 2.113% | 0.2937%
2017-09-03 | 8 | 5464 | 112.7225 | 2.063% | 15.6659 | 0.2867% | 128.3884 | 2.35% | 272 | 5448.3341 | 5335.6116 | 2.113% | 0.2936%
2017-09-05 | 4 | 5464 | 112.7225 | 2.063% | 15.6659 | 0.2867% | 128.3884 | 2.35% | 273 | 5448.3341 | 5335.6116 | 2.113% | 0.2936%
2017-09-22 | 5 | 5471 | 112.619 | 2.058% | 15.6648 | 0.2863% | 128.2839 | 2.345% | 274 | 5455.3352 | 5342.7161 | 2.108% | 0.2932%
2017-09-10 | 9 | 5472 | 112.6043 | 2.058% | 15.6647 | 0.2863% | 128.2689 | 2.344% | 275 | 5456.3353 | 5343.7311 | 2.107% | 0.2931%
2017-09-16 | 4 | 5474 | 112.5747 | 2.057% | 15.6644 | 0.2862% | 128.2391 | 2.343% | 276 | 5458.3356 | 5345.7609 | 2.106% | 0.293%
2017-09-18 | 3 | 5474 | 112.5747 | 2.057% | 15.6644 | 0.2862% | 128.2391 | 2.343% | 277 | 5458.3356 | 5345.7609 | 2.106% | 0.293%
2017-09-18 | 5 | 5479 | 112.5008 | 2.053% | 15.6636 | 0.2859% | 128.1644 | 2.339% | 278 | 5463.3364 | 5350.8356 | 2.102% | 0.2927%
2017-09-19 | 4 | 5486 | 112.3973 | 2.049% | 15.6625 | 0.2855% | 128.0599 | 2.334% | 279 | 5470.3375 | 5357.9401 | 2.098% | 0.2923%
2017-11-04 | 8 | 5486 | 112.3973 | 2.049% | 15.6625 | 0.2855% | 128.0599 | 2.334% | 280 | 5470.3375 | 5357.9401 | 2.098% | 0.2923%
2017-11-22 | 4 | 5487 | 112.3826 | 2.048% | 15.6624 | 0.2854% | 128.0449 | 2.334% | 281 | 5471.3376 | 5358.9551 | 2.097% | 0.2923%
2017-11-22 | 3 | 5488 | 112.3678 | 2.048% | 15.6622 | 0.2854% | 128.03 | 2.333% | 282 | 5472.3378 | 5359.97 | 2.096% | 0.2922%
2017-10-07 | 7 | 5494 | 112.2791 | 2.044% | 15.6613 | 0.2851% | 127.9404 | 2.329% | 283 | 5478.3387 | 5366.0596 | 2.092% | 0.2919%
2017-10-05 | 6 | 5498 | 112.22 | 2.041% | 15.6607 | 0.2848% | 127.8807 | 2.326% | 284 | 5482.3393 | 5370.1193 | 2.09% | 0.2916%
2017-11-02 | 6 | 5501 | 112.1756 | 2.039% | 15.6602 | 0.2847% | 127.8359 | 2.324% | 285 | 5485.3398 | 5373.1641 | 2.088% | 0.2915%
2017-10-24 | 24 | 5503 | 112.1461 | 2.038% | 15.6599 | 0.2846% | 127.806 | 2.322% | 286 | 5487.3401 | 5375.194 | 2.086% | 0.2913%
2017-09-30 | 24 | 5505 | 112.1165 | 2.037% | 15.6596 | 0.2845% | 127.7762 | 2.321% | 287 | 5489.3404 | 5377.2238 | 2.085% | 0.2912%
2017-09-17 | 3 | 5508 | 112.0722 | 2.035% | 15.6592 | 0.2843% | 127.7314 | 2.319% | 288 | 5492.3408 | 5380.2686 | 2.083% | 0.291%
2017-09-07 | 6 | 5511 | 112.0278 | 2.033% | 15.6587 | 0.2841% | 127.6866 | 2.317% | 289 | 5495.3413 | 5383.3134 | 2.081% | 0.2909%
2017-10-22 | 9 | 5512 | 112.0131 | 2.032% | 15.6586 | 0.2841% | 127.6716 | 2.316% | 290 | 5496.3414 | 5384.3284 | 2.08% | 0.2908%
2017-11-18 | 24 | 5515 | 111.9687 | 2.03% | 15.6581 | 0.2839% | 127.6268 | 2.314% | 291 | 5499.3419 | 5387.3732 | 2.078% | 0.2906%
2017-09-25 | 2 | 5516 | 111.9539 | 2.03% | 15.6579 | 0.2839% | 127.6119 | 2.313% | 292 | 5500.3421 | 5388.3881 | 2.078% | 0.2906%
2017-10-20 | 24 | 5521 | 111.88 | 2.026% | 15.6572 | 0.2836% | 127.5372 | 2.31% | 293 | 5505.3428 | 5393.4628 | 2.074% | 0.2903%
2017-10-22 | 24 | 5521 | 111.88 | 2.026% | 15.6572 | 0.2836% | 127.5372 | 2.31% | 294 | 5505.3428 | 5393.4628 | 2.074% | 0.2903%
2017-10-06 | 6 | 5527 | 111.7914 | 2.023% | 15.6563 | 0.2833% | 127.4476 | 2.306% | 295 | 5511.3437 | 5399.5524 | 2.07% | 0.29%
2017-09-05 | 3 | 5537 | 111.6436 | 2.016% | 15.6547 | 0.2827% | 127.2983 | 2.299% | 296 | 5521.3453 | 5409.7017 | 2.064% | 0.2894% | 5537.2588
2017-10-21 | 8 | 5538 | 111.6335 | 2.016% | 15.6548 | 0.2827% | 127.2883 | 2.298% | 297 | 5522.3452 | 5410.7117 | 2.063% | 0.2893%
2017-09-05 | 5 | 5549 | 111.7685 | 2.014% | 15.6691 | 0.2824% | 127.4377 | 2.297% | 298 | 5533.3309 | 5421.5623 | 2.062% | 0.289%
2017-10-19 | 24 | 5551 | 111.7931 | 2.014% | 15.6717 | 0.2823% | 127.4648 | 2.296% | 299 | 5535.3283 | 5423.5352 | 2.061% | 0.289%
2017-09-19 | 5 | 5552 | 111.8054 | 2.014% | 15.673 | 0.2823% | 127.4784 | 2.296% | 300 | 5536.327 | 5424.5216 | 2.061% | 0.2889%
2017-10-20 | 6 | 5554 | 111.8299 | 2.014% | 15.6757 | 0.2822% | 127.5056 | 2.296% | 301 | 5538.3243 | 5426.4944 | 2.061% | 0.2889%
2017-09-20 | 3 | 5556 | 111.8545 | 2.013% | 15.6783 | 0.2822% | 127.5327 | 2.295% | 302 | 5540.3217 | 5428.4673 | 2.061% | 0.2888%
2017-09-15 | 4 | 5563 | 111.9404 | 2.012% | 15.6874 | 0.282% | 127.6278 | 2.294% | 303 | 5547.3126 | 5435.3722 | 2.059% | 0.2886%
2017-10-27 | 3 | 5565 | 111.9649 | 2.012% | 15.69 | 0.2819% | 127.6549 | 2.294% | 304 | 5549.31 | 5437.3451 | 2.059% | 0.2886%
2017-10-14 | 8 | 5568 | 112.0018 | 2.012% | 15.6939 | 0.2819% | 127.6956 | 2.293% | 305 | 5552.3061 | 5440.3044 | 2.059% | 0.2885%
2017-10-24 | 1 | 5570 | 112.0263 | 2.011% | 15.6965 | 0.2818% | 127.7228 | 2.293% | 306 | 5554.3035 | 5442.2772 | 2.058% | 0.2884%
2017-09-14 | 4 | 5571 | 112.0386 | 2.011% | 15.6978 | 0.2818% | 127.7364 | 2.293% | 307 | 5555.3022 | 5443.2636 | 2.058% | 0.2884%
2017-09-23 | 7 | 5571 | 112.0386 | 2.011% | 15.6978 | 0.2818% | 127.7364 | 2.293% | 308 | 5555.3022 | 5443.2636 | 2.058% | 0.2884%
2017-09-02 | 5 | 5573 | 112.0631 | 2.011% | 15.7004 | 0.2817% | 127.7635 | 2.293% | 309 | 5557.2996 | 5445.2365 | 2.058% | 0.2883%
2017-09-13 | 3 | 5575 | 112.0877 | 2.011% | 15.703 | 0.2817% | 127.7907 | 2.292% | 310 | 5559.297 | 5447.2093 | 2.058% | 0.2883%
2017-11-22 | 2 | 5576 | 112.1 | 2.01% | 15.7043 | 0.2816% | 127.8042 | 2.292% | 311 | 5560.2957 | 5448.1958 | 2.058% | 0.2882%
2017-10-27 | 24 | 5577 | 112.1122 | 2.01% | 15.7056 | 0.2816% | 127.8178 | 2.292% | 312 | 5561.2944 | 5449.1822 | 2.057% | 0.2882%
2017-09-03 | 3 | 5580 | 112.1491 | 2.01% | 15.7095 | 0.2815% | 127.8585 | 2.291% | 313 | 5564.2905 | 5452.1415 | 2.057% | 0.2881%
2017-09-12 | 6 | 5581 | 112.1613 | 2.01% | 15.7108 | 0.2815% | 127.8721 | 2.291% | 314 | 5565.2892 | 5453.1279 | 2.057% | 0.2881%
2017-10-18 | 24 | 5586 | 112.2227 | 2.009% | 15.7173 | 0.2814% | 127.94 | 2.29% | 315 | 5570.2827 | 5458.06 | 2.056% | 0.288%
2017-09-15 | 5 | 5589 | 112.2595 | 2.009% | 15.7212 | 0.2813% | 127.9807 | 2.29% | 316 | 5573.2788 | 5461.0193 | 2.056% | 0.2879%
2017-10-13 | 4 | 5589 | 112.2595 | 2.009% | 15.7212 | 0.2813% | 127.9807 | 2.29% | 317 | 5573.2788 | 5461.0193 | 2.056% | 0.2879%
2017-09-19 | 3 | 5591 | 112.2841 | 2.008% | 15.7238 | 0.2812% | 128.0079 | 2.29% | 318 | 5575.2762 | 5462.9921 | 2.055% | 0.2878%
2017-11-19 | 8 | 5593 | 112.3086 | 2.008% | 15.7264 | 0.2812% | 128.035 | 2.289% | 319 | 5577.2736 | 5464.965 | 2.055% | 0.2878%
2017-09-02 | 6 | 5601 | 112.4068 | 2.007% | 15.7368 | 0.281% | 128.1436 | 2.288% | 320 | 5585.2632 | 5472.8564 | 2.054% | 0.2875%
2017-11-06 | 24 | 5603 | 112.4314 | 2.007% | 15.7394 | 0.2809% | 128.1708 | 2.288% | 321 | 5587.2606 | 5474.8292 | 2.054% | 0.2875%
2017-10-30 | 2 | 5605 | 112.456 | 2.006% | 15.742 | 0.2809% | 128.1979 | 2.287% | 322 | 5589.258 | 5476.8021 | 2.053% | 0.2874%
2017-10-13 | 5 | 5607 | 112.4805 | 2.006% | 15.7446 | 0.2808% | 128.2251 | 2.287% | 323 | 5591.2554 | 5478.7749 | 2.053% | 0.2874%
2017-10-14 | 1 | 5610 | 112.5173 | 2.006% | 15.7485 | 0.2807% | 128.2658 | 2.286% | 324 | 5594.2515 | 5481.7342 | 2.053% | 0.2873%
2017-10-29 | 9 | 5614 | 112.5664 | 2.005% | 15.7537 | 0.2806% | 128.3201 | 2.286% | 325 | 5598.2463 | 5485.6799 | 2.052% | 0.2872%
2017-11-22 | 5 | 5614 | 112.5664 | 2.005% | 15.7537 | 0.2806% | 128.3201 | 2.286% | 326 | 5598.2463 | 5485.6799 | 2.052% | 0.2872%
2017-09-22 | 3 | 5615 | 112.5787 | 2.005% | 15.755 | 0.2806% | 128.3337 | 2.286% | 327 | 5599.245 | 5486.6663 | 2.052% | 0.2872%
2017-10-05 | 1 | 5620 | 112.6401 | 2.004% | 15.7615 | 0.2805% | 128.4016 | 2.285% | 328 | 5604.2385 | 5491.5984 | 2.051% | 0.287%
2017-10-27 | 2 | 5624 | 112.6892 | 2.004% | 15.7667 | 0.2803% | 128.4559 | 2.284% | 329 | 5608.2333 | 5495.5441 | 2.051% | 0.2869%
2017-11-01 | 24 | 5625 | 112.7015 | 2.004% | 15.768 | 0.2803% | 128.4695 | 2.284% | 330 | 5609.232 | 5496.5305 | 2.05% | 0.2869%
2017-10-28 | 7 | 5626 | 112.7137 | 2.003% | 15.7693 | 0.2803% | 128.483 | 2.284% | 331 | 5610.2307 | 5497.517 | 2.05% | 0.2868%
2017-11-01 | 5 | 5632 | 112.7874 | 2.003% | 15.7771 | 0.2801% | 128.5645 | 2.283% | 332 | 5616.2229 | 5503.4355 | 2.049% | 0.2867%
2017-10-16 | 1 | 5633 | 112.7997 | 2.002% | 15.7784 | 0.2801% | 128.5781 | 2.283% | 333 | 5617.2216 | 5504.4219 | 2.049% | 0.2866%
2017-09-16 | 7 | 5634 | 112.8119 | 2.002% | 15.7797 | 0.2801% | 128.5917 | 2.282% | 334 | 5618.2203 | 5505.4083 | 2.049% | 0.2866%
2017-10-30 | 1 | 5639 | 112.8733 | 2.002% | 15.7862 | 0.2799% | 128.6595 | 2.282% | 335 | 5623.2138 | 5510.3405 | 2.048% | 0.2865%
2017-09-07 | 1 | 5641 | 112.8979 | 2.001% | 15.7888 | 0.2799% | 128.6867 | 2.281% | 336 | 5625.2112 | 5512.3133 | 2.048% | 0.2864%
2017-10-30 | 3 | 5641 | 112.8979 | 2.001% | 15.7888 | 0.2799% | 128.6867 | 2.281% | 337 | 5625.2112 | 5512.3133 | 2.048% | 0.2864%
2017-10-16 | 6 | 5642 | 112.9101 | 2.001% | 15.7901 | 0.2799% | 128.7003 | 2.281% | 338 | 5626.2099 | 5513.2997 | 2.048% | 0.2864%
2017-09-14 | 5 | 5643 | 112.9224 | 2.001% | 15.7914 | 0.2798% | 128.7138 | 2.281% | 339 | 5627.2086 | 5514.2862 | 2.048% | 0.2864%
2017-10-17 | 24 | 5643 | 112.9224 | 2.001% | 15.7914 | 0.2798% | 128.7138 | 2.281% | 340 | 5627.2086 | 5514.2862 | 2.048% | 0.2864%
2017-09-17 | 8 | 5645 | 112.947 | 2.001% | 15.794 | 0.2798% | 128.741 | 2.281% | 341 | 5629.206 | 5516.259 | 2.048% | 0.2863%
2017-09-16 | 3 | 5647 | 112.9715 | 2.001% | 15.7966 | 0.2797% | 128.7681 | 2.28% | 342 | 5631.2034 | 5518.2319 | 2.047% | 0.2863%
2017-09-23 | 3 | 5647 | 112.9715 | 2.001% | 15.7966 | 0.2797% | 128.7681 | 2.28% | 343 | 5631.2034 | 5518.2319 | 2.047% | 0.2863%
2017-11-02 | 24 | 5650 | 113.0083 | 2% | 15.8005 | 0.2797% | 128.8089 | 2.28% | 344 | 5634.1995 | 5521.1911 | 2.047% | 0.2862%
2017-11-07 | 24 | 5653 | 113.0452 | 2% | 15.8044 | 0.2796% | 128.8496 | 2.279% | 345 | 5637.1956 | 5524.1504 | 2.046% | 0.2861%
2017-09-18 | 2 | 5655 | 113.0697 | 1.999% | 15.807 | 0.2795% | 128.8768 | 2.279% | 346 | 5639.193 | 5526.1232 | 2.046% | 0.286%
2017-09-02 | 4 | 5662 | 113.1556 | 1.999% | 15.8162 | 0.2793% | 128.9718 | 2.278% | 347 | 5646.1838 | 5533.0282 | 2.045% | 0.2858%
2017-10-25 | 24 | 5670 | 113.2538 | 1.997% | 15.8266 | 0.2791% | 129.0804 | 2.277% | 348 | 5654.1734 | 5540.9196 | 2.044% | 0.2856%
2017-10-06 | 1 | 5674 | 113.3029 | 1.997% | 15.8318 | 0.279% | 129.1347 | 2.276% | 349 | 5658.1682 | 5544.8653 | 2.043% | 0.2855%
2017-09-04 | 9 | 5677 | 113.3398 | 1.996% | 15.8357 | 0.2789% | 129.1754 | 2.275% | 350 | 5661.1643 | 5547.8246 | 2.043% | 0.2854%
2017-11-10 | 3 | 5678 | 113.352 | 1.996% | 15.837 | 0.2789% | 129.189 | 2.275% | 351 | 5662.163 | 5548.811 | 2.043% | 0.2854%
2017-09-04 | 1 | 5683 | 113.4134 | 1.996% | 15.8435 | 0.2788% | 129.2569 | 2.274% | 352 | 5667.1565 | 5553.7431 | 2.042% | 0.2853%
2017-09-15 | 3 | 5684 | 113.4257 | 1.996% | 15.8448 | 0.2788% | 129.2705 | 2.274% | 353 | 5668.1552 | 5554.7295 | 2.042% | 0.2852%
2017-10-27 | 4 | 5686 | 113.4502 | 1.995% | 15.8474 | 0.2787% | 129.2976 | 2.274% | 354 | 5670.1526 | 5556.7024 | 2.042% | 0.2852%
2017-09-25 | 6 | 5688 | 113.4748 | 1.995% | 15.85 | 0.2787% | 129.3248 | 2.274% | 355 | 5672.15 | 5558.6752 | 2.041% | 0.2851%
2017-09-29 | 5 | 5689 | 113.4871 | 1.995% | 15.8513 | 0.2786% | 129.3383 | 2.273% | 356 | 5673.1487 | 5559.6617 | 2.041% | 0.2851%
2017-09-26 | 4 | 5693 | 113.5362 | 1.994% | 15.8565 | 0.2785% | 129.3926 | 2.273% | 357 | 5677.1435 | 5563.6074 | 2.041% | 0.285%
2017-09-14 | 3 | 5694 | 113.5484 | 1.994% | 15.8578 | 0.2785% | 129.4062 | 2.273% | 358 | 5678.1422 | 5564.5938 | 2.041% | 0.285%
2017-09-24 | 2 | 5695 | 113.5607 | 1.994% | 15.8591 | 0.2785% | 129.4198 | 2.273% | 359 | 5679.1409 | 5565.5802 | 2.04% | 0.2849%
2017-10-01 | 10 | 5696 | 113.573 | 1.994% | 15.8604 | 0.2784% | 129.4334 | 2.272% | 360 | 5680.1396 | 5566.5666 | 2.04% | 0.2849%
2017-09-30 | 1 | 5699 | 113.6098 | 1.994% | 15.8643 | 0.2784% | 129.4741 | 2.272% | 361 | 5683.1357 | 5569.5259 | 2.04% | 0.2848%
2017-10-13 | 3 | 5704 | 113.6712 | 1.993% | 15.8708 | 0.2782% | 129.542 | 2.271% | 362 | 5688.1292 | 5574.458 | 2.039% | 0.2847%
2017-11-03 | 24 | 5717 | 113.8308 | 1.991% | 15.8877 | 0.2779% | 129.7185 | 2.269% | 363 | 5701.1123 | 5587.2815 | 2.037% | 0.2844%
2017-09-23 | 8 | 5719 | 113.8553 | 1.991% | 15.8903 | 0.2779% | 129.7456 | 2.269% | 364 | 5703.1097 | 5589.2544 | 2.037% | 0.2843%
2017-10-07 | 1 | 5720 | 113.8676 | 1.991% | 15.8916 | 0.2778% | 129.7592 | 2.269% | 365 | 5704.1084 | 5590.2408 | 2.037% | 0.2843%
2017-10-31 | 24 | 5721 | 113.8799 | 1.991% | 15.8929 | 0.2778% | 129.7728 | 2.268% | 366 | 5705.1071 | 5591.2272 | 2.037% | 0.2842%
2017-10-27 | 1 | 5723 | 113.9044 | 1.99% | 15.8955 | 0.2777% | 129.7999 | 2.268% | 367 | 5707.1045 | 5593.2001 | 2.036% | 0.2842%
2017-11-10 | 4 | 5725 | 113.929 | 1.99% | 15.8981 | 0.2777% | 129.8271 | 2.268% | 368 | 5709.1019 | 5595.1729 | 2.036% | 0.2841%
2017-11-13 | 3 | 5725 | 113.929 | 1.99% | 15.8981 | 0.2777% | 129.8271 | 2.268% | 369 | 5709.1019 | 5595.1729 | 2.036% | 0.2841%
2017-11-13 | 2 | 5728 | 113.9658 | 1.99% | 15.902 | 0.2776% | 129.8678 | 2.267% | 370 | 5712.098 | 5598.1322 | 2.036% | 0.2841%
2017-10-01 | 11 | 5732 | 114.0149 | 1.989% | 15.9072 | 0.2775% | 129.9221 | 2.267% | 371 | 5716.0928 | 5602.0779 | 2.035% | 0.284%
2017-11-05 | 11 | 5733 | 114.0272 | 1.989% | 15.9085 | 0.2775% | 129.9357 | 2.266% | 372 | 5717.0915 | 5603.0643 | 2.035% | 0.2839%
2017-10-15 | 9 | 5743 | 114.1499 | 1.988% | 15.9215 | 0.2772% | 130.0715 | 2.265% | 373 | 5727.0785 | 5612.9285 | 2.034% | 0.2837%
2017-11-10 | 2 | 5745 | 114.1745 | 1.987% | 15.9241 | 0.2772% | 130.0986 | 2.265% | 374 | 5729.0759 | 5614.9014 | 2.033% | 0.2836%
2017-10-30 | 4 | 5746 | 114.1868 | 1.987% | 15.9254 | 0.2772% | 130.1122 | 2.264% | 375 | 5730.0746 | 5615.8878 | 2.033% | 0.2836%
2017-09-21 | 4 | 5749 | 114.2236 | 1.987% | 15.9293 | 0.2771% | 130.1529 | 2.264% | 376 | 5733.0707 | 5618.8471 | 2.033% | 0.2835%
2017-10-21 | 23 | 5749 | 114.2236 | 1.987% | 15.9293 | 0.2771% | 130.1529 | 2.264% | 377 | 5733.0707 | 5618.8471 | 2.033% | 0.2835%
2017-11-22 | 1 | 5749 | 114.2236 | 1.987% | 15.9293 | 0.2771% | 130.1529 | 2.264% | 378 | 5733.0707 | 5618.8471 | 2.033% | 0.2835%
2017-09-09 | 9 | 5750 | 114.2359 | 1.987% | 15.9306 | 0.2771% | 130.1665 | 2.264% | 379 | 5734.0694 | 5619.8335 | 2.033% | 0.2835%
2017-09-29 | 4 | 5751 | 114.2481 | 1.987% | 15.9319 | 0.277% | 130.1801 | 2.264% | 380 | 5735.0681 | 5620.8199 | 2.033% | 0.2834%
2017-10-02 | 24 | 5752 | 114.2604 | 1.986% | 15.9332 | 0.277% | 130.1936 | 2.263% | 381 | 5736.0668 | 5621.8064 | 2.032% | 0.2834%
2017-09-11 | 24 | 5759 | 114.3463 | 1.986% | 15.9423 | 0.2768% | 130.2887 | 2.262% | 382 | 5743.0577 | 5628.7113 | 2.031% | 0.2832%
2017-09-28 | 4 | 5761 | 114.3709 | 1.985% | 15.9449 | 0.2768% | 130.3158 | 2.262% | 383 | 5745.0551 | 5630.6842 | 2.031% | 0.2832%
2017-09-28 | 5 | 5761 | 114.3709 | 1.985% | 15.9449 | 0.2768% | 130.3158 | 2.262% | 384 | 5745.0551 | 5630.6842 | 2.031% | 0.2832%
2017-09-26 | 5 | 5762 | 114.3832 | 1.985% | 15.9462 | 0.2767% | 130.3294 | 2.262% | 385 | 5746.0538 | 5631.6706 | 2.031% | 0.2832%
2017-10-22 | 10 | 5762 | 114.3832 | 1.985% | 15.9462 | 0.2767% | 130.3294 | 2.262% | 386 | 5746.0538 | 5631.6706 | 2.031% | 0.2832%
2017-09-02 | 7 | 5766 | 114.4323 | 1.985% | 15.9514 | 0.2766% | 130.3837 | 2.261% | 387 | 5750.0486 | 5635.6163 | 2.031% | 0.283%
2017-09-21 | 5 | 5769 | 114.4691 | 1.984% | 15.9553 | 0.2766% | 130.4244 | 2.261% | 388 | 5753.0447 | 5638.5756 | 2.03% | 0.283%
2017-09-20 | 2 | 5770 | 114.4814 | 1.984% | 15.9566 | 0.2765% | 130.438 | 2.261% | 389 | 5754.0434 | 5639.562 | 2.03% | 0.2829%
2017-09-17 | 2 | 5772 | 114.5059 | 1.984% | 15.9593 | 0.2765% | 130.4652 | 2.26% | 390 | 5756.0407 | 5641.5348 | 2.03% | 0.2829%
2017-10-28 | 23 | 5773 | 114.5182 | 1.984% | 15.9606 | 0.2765% | 130.4787 | 2.26% | 391 | 5757.0394 | 5642.5213 | 2.03% | 0.2829%
2017-09-13 | 6 | 5774 | 114.5305 | 1.984% | 15.9619 | 0.2764% | 130.4923 | 2.26% | 392 | 5758.0381 | 5643.5077 | 2.029% | 0.2828%
2017-10-07 | 8 | 5776 | 114.555 | 1.983% | 15.9645 | 0.2764% | 130.5195 | 2.26% | 393 | 5760.0355 | 5645.4805 | 2.029% | 0.2828%
2017-10-03 | 24 | 5778 | 114.5796 | 1.983% | 15.9671 | 0.2763% | 130.5466 | 2.259% | 394 | 5762.0329 | 5647.4534 | 2.029% | 0.2827%
2017-11-05 | 23 | 5778 | 114.5796 | 1.983% | 15.9671 | 0.2763% | 130.5466 | 2.259% | 395 | 5762.0329 | 5647.4534 | 2.029% | 0.2827%
2017-11-26 | 2 | 5784 | 114.6532 | 1.982% | 15.9749 | 0.2762% | 130.6281 | 2.258% | 396 | 5768.0251 | 5653.3719 | 2.028% | 0.2826%
2017-10-19 | 6 | 5786 | 114.6778 | 1.982% | 15.9775 | 0.2761% | 130.6552 | 2.258% | 397 | 5770.0225 | 5655.3448 | 2.028% | 0.2825%
2017-11-09 | 4 | 5787 | 114.69 | 1.982% | 15.9788 | 0.2761% | 130.6688 | 2.258% | 398 | 5771.0212 | 5656.3312 | 2.028% | 0.2825%
2017-11-26 | 3 | 5787 | 114.69 | 1.982% | 15.9788 | 0.2761% | 130.6688 | 2.258% | 399 | 5771.0212 | 5656.3312 | 2.028% | 0.2825%
2017-09-26 | 3 | 5791 | 114.7391 | 1.981% | 15.984 | 0.276% | 130.7231 | 2.257% | 400 | 5775.016 | 5660.2769 | 2.027% | 0.2824%
2017-11-13 | 4 | 5791 | 114.7391 | 1.981% | 15.984 | 0.276% | 130.7231 | 2.257% | 401 | 5775.016 | 5660.2769 | 2.027% | 0.2824%
2017-09-09 | 24 | 5792 | 114.7514 | 1.981% | 15.9853 | 0.276% | 130.7367 | 2.257% | 402 | 5776.0147 | 5661.2633 | 2.027% | 0.2824%
2017-09-05 | 2 | 5793 | 114.7637 | 1.981% | 15.9866 | 0.276% | 130.7503 | 2.257% | 403 | 5777.0134 | 5662.2497 | 2.027% | 0.2823%
2017-11-08 | 6 | 5799 | 114.8373 | 1.98% | 15.9944 | 0.2758% | 130.8317 | 2.256% | 404 | 5783.0056 | 5668.1683 | 2.026% | 0.2822%
2017-11-09 | 3 | 5799 | 114.8373 | 1.98% | 15.9944 | 0.2758% | 130.8317 | 2.256% | 405 | 5783.0056 | 5668.1683 | 2.026% | 0.2822%
2017-11-05 | 9 | 5801 | 114.8619 | 1.98% | 15.997 | 0.2758% | 130.8589 | 2.256% | 406 | 5785.003 | 5670.1411 | 2.026% | 0.2821%
2017-11-26 | 4 | 5802 | 114.8742 | 1.98% | 15.9983 | 0.2757% | 130.8724 | 2.256% | 407 | 5786.0017 | 5671.1276 | 2.026% | 0.2821%
2017-09-10 | 10 | 5803 | 114.8864 | 1.98% | 15.9996 | 0.2757% | 130.886 | 2.255% | 408 | 5787.0004 | 5672.114 | 2.025% | 0.2821%
2017-09-20 | 6 | 5812 | 114.9969 | 1.979% | 16.0113 | 0.2755% | 131.0082 | 2.254% | 409 | 5795.9887 | 5680.9918 | 2.024% | 0.2818%
2017-09-13 | 2 | 5821 | 115.1074 | 1.977% | 16.023 | 0.2753% | 131.1304 | 2.253% | 410 | 5804.977 | 5689.8696 | 2.023% | 0.2816%
2017-11-04 | 9 | 5824 | 115.1442 | 1.977% | 16.0269 | 0.2752% | 131.1711 | 2.252% | 411 | 5807.9731 | 5692.8289 | 2.023% | 0.2815%
2017-09-19 | 2 | 5825 | 115.1565 | 1.977% | 16.0282 | 0.2752% | 131.1847 | 2.252% | 412 | 5808.9718 | 5693.8153 | 2.022% | 0.2815%
2017-09-02 | 3 | 5826 | 115.1688 | 1.977% | 16.0295 | 0.2751% | 131.1983 | 2.252% | 413 | 5809.9705 | 5694.8017 | 2.022% | 0.2815%
2017-09-03 | 2 | 5826 | 115.1688 | 1.977% | 16.0295 | 0.2751% | 131.1983 | 2.252% | 414 | 5809.9705 | 5694.8017 | 2.022% | 0.2815%
2017-10-01 | 12 | 5834 | 115.267 | 1.976% | 16.0399 | 0.2749% | 131.3069 | 2.251% | 415 | 5817.9601 | 5702.6931 | 2.021% | 0.2813%
2017-10-14 | 24 | 5834 | 115.267 | 1.976% | 16.0399 | 0.2749% | 131.3069 | 2.251% | 416 | 5817.9601 | 5702.6931 | 2.021% | 0.2813%
2017-11-13 | 1 | 5839 | 115.3283 | 1.975% | 16.0464 | 0.2748% | 131.3748 | 2.25% | 417 | 5822.9536 | 5707.6252 | 2.021% | 0.2811%
2017-09-22 | 6 | 5844 | 115.3897 | 1.974% | 16.0529 | 0.2747% | 131.4426 | 2.249% | 418 | 5827.9471 | 5712.5574 | 2.02% | 0.281%
2017-11-26 | 1 | 5846 | 115.4143 | 1.974% | 16.0555 | 0.2746% | 131.4698 | 2.249% | 419 | 5829.9445 | 5714.5302 | 2.02% | 0.281%
2017-09-16 | 8 | 5847 | 115.4265 | 1.974% | 16.0568 | 0.2746% | 131.4834 | 2.249% | 420 | 5830.9432 | 5715.5166 | 2.02% | 0.2809%
2017-10-21 | 9 | 5855 | 115.5247 | 1.973% | 16.0672 | 0.2744% | 131.592 | 2.248% | 421 | 5838.9328 | 5723.408 | 2.018% | 0.2807%
2017-10-01 | 23 | 5857 | 115.5493 | 1.973% | 16.0698 | 0.2744% | 131.6191 | 2.247% | 422 | 5840.9302 | 5725.3809 | 2.018% | 0.2807%
2017-10-29 | 10 | 5857 | 115.5493 | 1.973% | 16.0698 | 0.2744% | 131.6191 | 2.247% | 423 | 5840.9302 | 5725.3809 | 2.018% | 0.2807%
2017-09-30 | 9 | 5860 | 115.5861 | 1.972% | 16.0737 | 0.2743% | 131.6599 | 2.247% | 424 | 5843.9263 | 5728.3401 | 2.018% | 0.2806%
2017-09-25 | 1 | 5861 | 115.5984 | 1.972% | 16.075 | 0.2743% | 131.6734 | 2.247% | 425 | 5844.925 | 5729.3266 | 2.018% | 0.2806%
2017-10-26 | 6 | 5866 | 115.6598 | 1.972% | 16.0815 | 0.2741% | 131.7413 | 2.246% | 426 | 5849.9185 | 5734.2587 | 2.017% | 0.2804%
2017-11-04 | 23 | 5866 | 115.6598 | 1.972% | 16.0815 | 0.2741% | 131.7413 | 2.246% | 427 | 5849.9185 | 5734.2587 | 2.017% | 0.2804%
2017-10-29 | 24 | 5872 | 115.7334 | 1.971% | 16.0893 | 0.274% | 131.8228 | 2.245% | 428 | 5855.9107 | 5740.1772 | 2.016% | 0.2803%
2017-09-22 | 2 | 5875 | 115.7703 | 1.971% | 16.0932 | 0.2739% | 131.8635 | 2.244% | 429 | 5858.9068 | 5743.1365 | 2.016% | 0.2802%
2017-10-22 | 11 | 5882 | 115.8562 | 1.97% | 16.1024 | 0.2738% | 131.9585 | 2.243% | 430 | 5865.8976 | 5750.0415 | 2.015% | 0.28%
2017-10-27 | 5 | 5886 | 115.9053 | 1.969% | 16.1076 | 0.2737% | 132.0128 | 2.243% | 431 | 5869.8924 | 5753.9872 | 2.014% | 0.2799%
2017-10-08 | 5 | 5893 | 115.9912 | 1.968% | 16.1167 | 0.2735% | 132.1079 | 2.242% | 432 | 5876.8833 | 5760.8921 | 2.013% | 0.2798%
2017-11-10 | 1 | 5894 | 116.0035 | 1.968% | 16.118 | 0.2735% | 132.1214 | 2.242% | 433 | 5877.882 | 5761.8786 | 2.013% | 0.2797%
2017-09-06 | 5 | 5895 | 116.0158 | 1.968% | 16.1193 | 0.2734% | 132.135 | 2.241% | 434 | 5878.8807 | 5762.865 | 2.013% | 0.2797%
2017-11-09 | 2 | 5899 | 116.0649 | 1.968% | 16.1245 | 0.2733% | 132.1893 | 2.241% | 435 | 5882.8755 | 5766.8107 | 2.013% | 0.2796%
2017-09-14 | 2 | 5903 | 116.114 | 1.967% | 16.1297 | 0.2732% | 132.2436 | 2.24% | 436 | 5886.8703 | 5770.7564 | 2.012% | 0.2795%
2017-11-05 | 10 | 5906 | 116.1508 | 1.967% | 16.1336 | 0.2732% | 132.2844 | 2.24% | 437 | 5889.8664 | 5773.7156 | 2.012% | 0.2794%
2017-09-06 | 4 | 5907 | 116.1631 | 1.967% | 16.1349 | 0.2731% | 132.2979 | 2.24% | 438 | 5890.8651 | 5774.7021 | 2.012% | 0.2794%
2017-09-18 | 6 | 5911 | 116.2122 | 1.966% | 16.1401 | 0.2731% | 132.3522 | 2.239% | 439 | 5894.8599 | 5778.6478 | 2.011% | 0.2793%
2017-09-16 | 2 | 5915 | 116.2613 | 1.966% | 16.1453 | 0.273% | 132.4065 | 2.238% | 440 | 5898.8547 | 5782.5935 | 2.011% | 0.2792%
2017-10-18 | 6 | 5920 | 116.3226 | 1.965% | 16.1518 | 0.2728% | 132.4744 | 2.238% | 441 | 5903.8482 | 5787.5256 | 2.01% | 0.2791%
2017-09-21 | 3 | 5921 | 116.3349 | 1.965% | 16.1531 | 0.2728% | 132.488 | 2.238% | 442 | 5904.8469 | 5788.512 | 2.01% | 0.2791%
2017-09-08 | 24 | 5922 | 116.3472 | 1.965% | 16.1544 | 0.2728% | 132.5016 | 2.237% | 443 | 5905.8456 | 5789.4984 | 2.01% | 0.279%
2017-09-28 | 3 | 5923 | 116.3595 | 1.965% | 16.1557 | 0.2728% | 132.5152 | 2.237% | 444 | 5906.8443 | 5790.4848 | 2.009% | 0.279%
2017-10-28 | 8 | 5923 | 116.3595 | 1.965% | 16.1557 | 0.2728% | 132.5152 | 2.237% | 445 | 5906.8443 | 5790.4848 | 2.009% | 0.279%
2017-09-23 | 2 | 5928 | 116.4208 | 1.964% | 16.1622 | 0.2726% | 132.583 | 2.237% | 446 | 5911.8378 | 5795.417 | 2.009% | 0.2789%
2017-11-18 | 23 | 5928 | 116.4208 | 1.964% | 16.1622 | 0.2726% | 132.583 | 2.237% | 447 | 5911.8378 | 5795.417 | 2.009% | 0.2789%
2017-11-25 | 16 | 5928 | 116.4208 | 1.964% | 16.1622 | 0.2726% | 132.583 | 2.237% | 448 | 5911.8378 | 5795.417 | 2.009% | 0.2789%
2017-09-10 | 11 | 5929 | 116.4331 | 1.964% | 16.1635 | 0.2726% | 132.5966 | 2.236% | 449 | 5912.8365 | 5796.4034 | 2.009% | 0.2789%
2017-09-15 | 2 | 5930 | 116.4454 | 1.964% | 16.1648 | 0.2726% | 132.6102 | 2.236% | 450 | 5913.8352 | 5797.3898 | 2.009% | 0.2788%
2017-09-15 | 6 | 5934 | 116.4945 | 1.963% | 16.17 | 0.2725% | 132.6645 | 2.236% | 451 | 5917.83 | 5801.3355 | 2.008% | 0.2787%
2017-10-08 | 6 | 5936 | 116.519 | 1.963% | 16.1726 | 0.2724% | 132.6916 | 2.235% | 452 | 5919.8274 | 5803.3084 | 2.008% | 0.2787%
2017-11-09 | 5 | 5936 | 116.519 | 1.963% | 16.1726 | 0.2724% | 132.6916 | 2.235% | 453 | 5919.8274 | 5803.3084 | 2.008% | 0.2787%
2017-09-11 | 7 | 5937 | 116.5313 | 1.963% | 16.1739 | 0.2724% | 132.7052 | 2.235% | 454 | 5920.8261 | 5804.2948 | 2.008% | 0.2787%
2017-10-27 | 23 | 5940 | 116.5681 | 1.962% | 16.1778 | 0.2724% | 132.7459 | 2.235% | 455 | 5923.8222 | 5807.2541 | 2.007% | 0.2786%
2017-09-02 | 8 | 5943 | 116.605 | 1.962% | 16.1817 | 0.2723% | 132.7867 | 2.234% | 456 | 5926.8183 | 5810.2133 | 2.007% | 0.2785%
2017-10-13 | 2 | 5943 | 116.605 | 1.962% | 16.1817 | 0.2723% | 132.7867 | 2.234% | 457 | 5926.8183 | 5810.2133 | 2.007% | 0.2785%
2017-09-19 | 6 | 5944 | 116.6172 | 1.962% | 16.183 | 0.2723% | 132.8003 | 2.234% | 458 | 5927.817 | 5811.1997 | 2.007% | 0.2785%
2017-11-10 | 5 | 5945 | 116.6295 | 1.962% | 16.1843 | 0.2722% | 132.8138 | 2.234% | 459 | 5928.8157 | 5812.1862 | 2.007% | 0.2785%
2017-11-25 | 15 | 5946 | 116.6418 | 1.962% | 16.1856 | 0.2722% | 132.8274 | 2.234% | 460 | 5929.8144 | 5813.1726 | 2.007% | 0.2784%
2017-11-26 | 15 | 5946 | 116.6418 | 1.962% | 16.1856 | 0.2722% | 132.8274 | 2.234% | 461 | 5929.8144 | 5813.1726 | 2.007% | 0.2784%
2017-09-05 | 6 | 5947 | 116.6541 | 1.962% | 16.1869 | 0.2722% | 132.841 | 2.234% | 462 | 5930.8131 | 5814.159 | 2.006% | 0.2784%
2017-10-20 | 23 | 5948 | 116.6663 | 1.961% | 16.1882 | 0.2722% | 132.8546 | 2.234% | 463 | 5931.8118 | 5815.1454 | 2.006% | 0.2784%
2017-09-01 | 4 | 5953 | 116.7277 | 1.961% | 16.1947 | 0.272% | 132.9224 | 2.233% | 464 | 5936.8053 | 5820.0776 | 2.006% | 0.2783%
2017-09-10 | 23 | 5955 | 116.7523 | 1.961% | 16.1973 | 0.272% | 132.9496 | 2.233% | 465 | 5938.8027 | 5822.0504 | 2.005% | 0.2782%
2017-11-26 | 16 | 5957 | 116.7768 | 1.96% | 16.1999 | 0.2719% | 132.9767 | 2.232% | 466 | 5940.8001 | 5824.0233 | 2.005% | 0.2782%
2017-10-08 | 4 | 5960 | 116.8136 | 1.96% | 16.2038 | 0.2719% | 133.0175 | 2.232% | 467 | 5943.7962 | 5826.9825 | 2.005% | 0.2781%
2017-09-07 | 24 | 5962 | 116.8382 | 1.96% | 16.2064 | 0.2718% | 133.0446 | 2.232% | 468 | 5945.7936 | 5828.9554 | 2.004% | 0.278%
2017-11-05 | 12 | 5965 | 116.875 | 1.959% | 16.2103 | 0.2718% | 133.0854 | 2.231% | 469 | 5948.7897 | 5831.9146 | 2.004% | 0.278%
2017-09-27 | 4 | 5972 | 116.9609 | 1.958% | 16.2194 | 0.2716% | 133.1804 | 2.23% | 470 | 5955.7806 | 5838.8196 | 2.003% | 0.2778%
2017-11-26 | 5 | 5972 | 116.9609 | 1.958% | 16.2194 | 0.2716% | 133.1804 | 2.23% | 471 | 5955.7806 | 5838.8196 | 2.003% | 0.2778%
2017-10-01 | 13 | 5975 | 116.9978 | 1.958% | 16.2233 | 0.2715% | 133.2211 | 2.23% | 472 | 5958.7767 | 5841.7789 | 2.003% | 0.2777%
2017-09-29 | 3 | 5976 | 117.01 | 1.958% | 16.2246 | 0.2715% | 133.2347 | 2.229% | 473 | 5959.7754 | 5842.7653 | 2.003% | 0.2777%
2017-11-05 | 13 | 5977 | 117.0223 | 1.958% | 16.2259 | 0.2715% | 133.2483 | 2.229% | 474 | 5960.7741 | 5843.7517 | 2.003% | 0.2777%
2017-09-29 | 6 | 5980 | 117.0591 | 1.958% | 16.2298 | 0.2714% | 133.289 | 2.229% | 475 | 5963.7702 | 5846.711 | 2.002% | 0.2776%
2017-10-13 | 6 | 5980 | 117.0591 | 1.958% | 16.2298 | 0.2714% | 133.289 | 2.229% | 476 | 5963.7702 | 5846.711 | 2.002% | 0.2776%
2017-09-03 | 9 | 5983 | 117.096 | 1.957% | 16.2337 | 0.2713% | 133.3297 | 2.228% | 477 | 5966.7663 | 5849.6703 | 2.002% | 0.2775%
2017-09-01 | 5 | 5985 | 117.1205 | 1.957% | 16.2363 | 0.2713% | 133.3569 | 2.228% | 478 | 5968.7637 | 5851.6431 | 2.001% | 0.2775%
2017-09-26 | 2 | 5986 | 117.1328 | 1.957% | 16.2376 | 0.2713% | 133.3704 | 2.228% | 479 | 5969.7624 | 5852.6296 | 2.001% | 0.2774%
2017-10-31 | 3 | 5987 | 117.1451 | 1.957% | 16.2389 | 0.2712% | 133.384 | 2.228% | 480 | 5970.7611 | 5853.616 | 2.001% | 0.2774%
2017-10-31 | 2 | 5997 | 117.2678 | 1.955% | 16.252 | 0.271% | 133.5198 | 2.226% | 481 | 5980.748 | 5863.4802 | 2% | 0.2772%
2017-10-16 | 23 | 5998 | 117.2801 | 1.955% | 16.2533 | 0.271% | 133.5334 | 2.226% | 482 | 5981.7467 | 5864.4666 | 2% | 0.2771%
2017-09-24 | 9 | 6003 | 117.3415 | 1.955% | 16.2598 | 0.2709% | 133.6012 | 2.226% | 483 | 5986.7402 | 5869.3988 | 1.999% | 0.277%
2017-11-26 | 14 | 6004 | 117.3538 | 1.955% | 16.2611 | 0.2708% | 133.6148 | 2.225% | 484 | 5987.7389 | 5870.3852 | 1.999% | 0.277%
2017-10-26 | 24 | 6005 | 117.366 | 1.954% | 16.2624 | 0.2708% | 133.6284 | 2.225% | 485 | 5988.7376 | 5871.3716 | 1.999% | 0.277%
2017-10-02 | 7 | 6006 | 117.3783 | 1.954% | 16.2637 | 0.2708% | 133.642 | 2.225% | 486 | 5989.7363 | 5872.358 | 1.999% | 0.277%
2017-11-22 | 6 | 6007 | 117.3906 | 1.954% | 16.265 | 0.2708% | 133.6555 | 2.225% | 487 | 5990.735 | 5873.3445 | 1.999% | 0.2769%
2017-10-22 | 12 | 6010 | 117.4274 | 1.954% | 16.2689 | 0.2707% | 133.6963 | 2.225% | 488 | 5993.7311 | 5876.3037 | 1.998% | 0.2769%
2017-09-18 | 1 | 6014 | 117.4765 | 1.953% | 16.2741 | 0.2706% | 133.7506 | 2.224% | 489 | 5997.7259 | 5880.2494 | 1.998% | 0.2768%
2017-10-28 | 14 | 6014 | 117.4765 | 1.953% | 16.2741 | 0.2706% | 133.7506 | 2.224% | 490 | 5997.7259 | 5880.2494 | 1.998% | 0.2768%
2017-11-19 | 15 | 6017 | 117.5133 | 1.953% | 16.278 | 0.2705% | 133.7913 | 2.224% | 491 | 6000.722 | 5883.2087 | 1.997% | 0.2767%
2017-11-19 | 14 | 6018 | 117.5256 | 1.953% | 16.2793 | 0.2705% | 133.8049 | 2.223% | 492 | 6001.7207 | 5884.1951 | 1.997% | 0.2767%
2017-09-27 | 5 | 6024 | 117.5993 | 1.952% | 16.2871 | 0.2704% | 133.8863 | 2.223% | 493 | 6007.7129 | 5890.1137 | 1.997% | 0.2765%
2017-10-14 | 9 | 6024 | 117.5993 | 1.952% | 16.2871 | 0.2704% | 133.8863 | 2.223% | 494 | 6007.7129 | 5890.1137 | 1.997% | 0.2765%
2017-09-30 | 23 | 6027 | 117.6361 | 1.952% | 16.291 | 0.2703% | 133.9271 | 2.222% | 495 | 6010.709 | 5893.0729 | 1.996% | 0.2764%
2017-09-08 | 7 | 6030 | 117.6729 | 1.951% | 16.2949 | 0.2702% | 133.9678 | 2.222% | 496 | 6013.7051 | 5896.0322 | 1.996% | 0.2764%
2017-09-02 | 2 | 6035 | 117.7343 | 1.951% | 16.3014 | 0.2701% | 134.0357 | 2.221% | 497 | 6018.6986 | 5900.9643 | 1.995% | 0.2762%
2017-10-04 | 24 | 6036 | 117.7466 | 1.951% | 16.3027 | 0.2701% | 134.0493 | 2.221% | 498 | 6019.6973 | 5901.9507 | 1.995% | 0.2762%
2017-10-29 | 11 | 6039 | 117.7834 | 1.95% | 16.3066 | 0.27% | 134.09 | 2.22% | 499 | 6022.6934 | 5904.91 | 1.995% | 0.2762%
2017-10-21 | 10 | 6041 | 117.8079 | 1.95% | 16.3092 | 0.27% | 134.1171 | 2.22% | 500 | 6024.6908 | 5906.8829 | 1.994% | 0.2761%
2017-11-13 | 5 | 6041 | 117.8079 | 1.95% | 16.3092 | 0.27% | 134.1171 | 2.22% | 501 | 6024.6908 | 5906.8829 | 1.994% | 0.2761%
2017-10-18 | 23 | 6045 | 117.857 | 1.95% | 16.3144 | 0.2699% | 134.1714 | 2.22% | 502 | 6028.6856 | 5910.8286 | 1.994% | 0.276%
2017-10-28 | 15 | 6047 | 117.8816 | 1.949% | 16.317 | 0.2698% | 134.1986 | 2.219% | 503 | 6030.683 | 5912.8014 | 1.994% | 0.276%
2017-09-14 | 6 | 6048 | 117.8939 | 1.949% | 16.3183 | 0.2698% | 134.2122 | 2.219% | 504 | 6031.6817 | 5913.7878 | 1.994% | 0.2759%
2017-11-19 | 16 | 6053 | 117.9552 | 1.949% | 16.3248 | 0.2697% | 134.28 | 2.218% | 505 | 6036.6752 | 5918.72 | 1.993% | 0.2758%
2017-10-15 | 24 | 6054 | 117.9675 | 1.949% | 16.3261 | 0.2697% | 134.2936 | 2.218% | 506 | 6037.6739 | 5919.7064 | 1.993% | 0.2758%
2017-10-30 | 5 | 6055 | 117.9798 | 1.948% | 16.3274 | 0.2697% | 134.3072 | 2.218% | 507 | 6038.6726 | 5920.6928 | 1.993% | 0.2758%
2017-11-09 | 1 | 6056 | 117.9921 | 1.948% | 16.3287 | 0.2696% | 134.3208 | 2.218% | 508 | 6039.6713 | 5921.6792 | 1.993% | 0.2757%
2017-10-31 | 1 | 6057 | 118.0043 | 1.948% | 16.33 | 0.2696% | 134.3344 | 2.218% | 509 | 6040.67 | 5922.6656 | 1.992% | 0.2757%
2017-11-25 | 17 | 6060 | 118.0412 | 1.948% | 16.3339 | 0.2695% | 134.3751 | 2.217% | 510 | 6043.6661 | 5925.6249 | 1.992% | 0.2756%
2017-09-06 | 3 | 6062 | 118.0657 | 1.948% | 16.3365 | 0.2695% | 134.4022 | 2.217% | 511 | 6045.6635 | 5927.5978 | 1.992% | 0.2756%
2017-09-10 | 12 | 6063 | 118.078 | 1.948% | 16.3378 | 0.2695% | 134.4158 | 2.217% | 512 | 6046.6622 | 5928.5842 | 1.992% | 0.2756%
2017-10-22 | 23 | 6066 | 118.1148 | 1.947% | 16.3417 | 0.2694% | 134.4565 | 2.217% | 513 | 6049.6583 | 5931.5435 | 1.991% | 0.2755%
2017-11-25 | 24 | 6066 | 118.1148 | 1.947% | 16.3417 | 0.2694% | 134.4565 | 2.217% | 514 | 6049.6583 | 5931.5435 | 1.991% | 0.2755%
2017-09-24 | 1 | 6070 | 118.1639 | 1.947% | 16.3469 | 0.2693% | 134.5108 | 2.216% | 515 | 6053.6531 | 5935.4892 | 1.991% | 0.2754%
2017-09-01 | 3 | 6074 | 118.213 | 1.946% | 16.3521 | 0.2692% | 134.5651 | 2.215% | 516 | 6057.6479 | 5939.4349 | 1.99% | 0.2753%
2017-10-23 | 24 | 6075 | 118.2253 | 1.946% | 16.3534 | 0.2692% | 134.5787 | 2.215% | 517 | 6058.6466 | 5940.4213 | 1.99% | 0.2753%
2017-10-29 | 12 | 6077 | 118.2498 | 1.946% | 16.356 | 0.2691% | 134.6059 | 2.215% | 518 | 6060.644 | 5942.3941 | 1.99% | 0.2752%
2017-11-18 | 16 | 6077 | 118.2498 | 1.946% | 16.356 | 0.2691% | 134.6059 | 2.215% | 519 | 6060.644 | 5942.3941 | 1.99% | 0.2752%
2017-11-25 | 14 | 6077 | 118.2498 | 1.946% | 16.356 | 0.2691% | 134.6059 | 2.215% | 520 | 6060.644 | 5942.3941 | 1.99% | 0.2752%
2017-10-13 | 24 | 6078 | 118.2621 | 1.946% | 16.3573 | 0.2691% | 134.6195 | 2.215% | 521 | 6061.6427 | 5943.3805 | 1.99% | 0.2752%
2017-11-19 | 9 | 6079 | 118.2744 | 1.946% | 16.3586 | 0.2691% | 134.633 | 2.215% | 522 | 6062.6414 | 5944.367 | 1.99% | 0.2752%
2017-10-31 | 4 | 6080 | 118.2867 | 1.946% | 16.3599 | 0.2691% | 134.6466 | 2.215% | 523 | 6063.6401 | 5945.3534 | 1.99% | 0.2752%
2017-10-08 | 7 | 6082 | 118.3112 | 1.945% | 16.3625 | 0.269% | 134.6738 | 2.214% | 524 | 6065.6375 | 5947.3262 | 1.989% | 0.2751%
2017-10-29 | 13 | 6082 | 118.3112 | 1.945% | 16.3625 | 0.269% | 134.6738 | 2.214% | 525 | 6065.6375 | 5947.3262 | 1.989% | 0.2751%
2017-09-27 | 3 | 6084 | 118.3358 | 1.945% | 16.3651 | 0.269% | 134.7009 | 2.214% | 526 | 6067.6349 | 5949.2991 | 1.989% | 0.2751%
2017-10-09 | 4 | 6086 | 118.3603 | 1.945% | 16.3677 | 0.2689% | 134.7281 | 2.214% | 527 | 6069.6323 | 5951.2719 | 1.989% | 0.275%
2017-10-12 | 4 | 6088 | 118.3849 | 1.945% | 16.3703 | 0.2689% | 134.7552 | 2.213% | 528 | 6071.6297 | 5953.2448 | 1.989% | 0.275%
2017-11-18 | 15 | 6090 | 118.4094 | 1.944% | 16.3729 | 0.2688% | 134.7824 | 2.213% | 529 | 6073.6271 | 5955.2176 | 1.988% | 0.2749%
2017-10-29 | 14 | 6091 | 118.4217 | 1.944% | 16.3742 | 0.2688% | 134.7959 | 2.213% | 530 | 6074.6258 | 5956.2041 | 1.988% | 0.2749%
2017-09-09 | 10 | 6094 | 118.4585 | 1.944% | 16.3781 | 0.2688% | 134.8367 | 2.213% | 531 | 6077.6219 | 5959.1633 | 1.988% | 0.2748%
2017-11-19 | 13 | 6094 | 118.4585 | 1.944% | 16.3781 | 0.2688% | 134.8367 | 2.213% | 532 | 6077.6219 | 5959.1633 | 1.988% | 0.2748%
2017-11-30 | 24 | 6097 | 118.4953 | 1.944% | 16.3821 | 0.2687% | 134.8774 | 2.212% | 533 | 6080.6179 | 5962.1226 | 1.987% | 0.2748%
2017-09-28 | 6 | 6103 | 118.569 | 1.943% | 16.3899 | 0.2686% | 134.9589 | 2.211% | 534 | 6086.6101 | 5968.0411 | 1.987% | 0.2746%
2017-10-03 | 7 | 6103 | 118.569 | 1.943% | 16.3899 | 0.2686% | 134.9589 | 2.211% | 535 | 6086.6101 | 5968.0411 | 1.987% | 0.2746%
2017-10-28 | 13 | 6105 | 118.5935 | 1.943% | 16.3925 | 0.2685% | 134.986 | 2.211% | 536 | 6088.6075 | 5970.014 | 1.986% | 0.2746%
2017-10-08 | 3 | 6108 | 118.6304 | 1.942% | 16.3964 | 0.2684% | 135.0267 | 2.211% | 537 | 6091.6036 | 5972.9733 | 1.986% | 0.2745%
2017-10-17 | 23 | 6109 | 118.6426 | 1.942% | 16.3977 | 0.2684% | 135.0403 | 2.211% | 538 | 6092.6023 | 5973.9597 | 1.986% | 0.2745%
2017-10-28 | 16 | 6111 | 118.6672 | 1.942% | 16.4003 | 0.2684% | 135.0675 | 2.21% | 539 | 6094.5997 | 5975.9325 | 1.986% | 0.2744%
2017-10-21 | 12 | 6112 | 118.6795 | 1.942% | 16.4016 | 0.2684% | 135.081 | 2.21% | 540 | 6095.5984 | 5976.919 | 1.986% | 0.2744%
2017-11-12 | 24 | 6112 | 118.6795 | 1.942% | 16.4016 | 0.2684% | 135.081 | 2.21% | 541 | 6095.5984 | 5976.919 | 1.986% | 0.2744%
2017-11-24 | 15 | 6114 | 118.704 | 1.942% | 16.4042 | 0.2683% | 135.1082 | 2.21% | 542 | 6097.5958 | 5978.8918 | 1.985% | 0.2744%
2017-11-05 | 14 | 6115 | 118.7163 | 1.941% | 16.4055 | 0.2683% | 135.1218 | 2.21% | 543 | 6098.5945 | 5979.8782 | 1.985% | 0.2743%
2017-11-19 | 12 | 6115 | 118.7163 | 1.941% | 16.4055 | 0.2683% | 135.1218 | 2.21% | 544 | 6098.5945 | 5979.8782 | 1.985% | 0.2743%
2017-10-21 | 11 | 6116 | 118.7286 | 1.941% | 16.4068 | 0.2683% | 135.1353 | 2.21% | 545 | 6099.5932 | 5980.8647 | 1.985% | 0.2743%
2017-10-19 | 23 | 6117 | 118.7409 | 1.941% | 16.4081 | 0.2682% | 135.1489 | 2.209% | 546 | 6100.5919 | 5981.8511 | 1.985% | 0.2743%
2017-11-06 | 23 | 6118 | 118.7531 | 1.941% | 16.4094 | 0.2682% | 135.1625 | 2.209% | 547 | 6101.5906 | 5982.8375 | 1.985% | 0.2743%
2017-09-20 | 1 | 6121 | 118.79 | 1.941% | 16.4133 | 0.2681% | 135.2032 | 2.209% | 548 | 6104.5867 | 5985.7968 | 1.985% | 0.2742%
2017-09-21 | 6 | 6125 | 118.8391 | 1.94% | 16.4185 | 0.2681% | 135.2575 | 2.208% | 549 | 6108.5815 | 5989.7425 | 1.984% | 0.2741%
2017-10-01 | 14 | 6127 | 118.8636 | 1.94% | 16.4211 | 0.268% | 135.2847 | 2.208% | 550 | 6110.5789 | 5991.7153 | 1.984% | 0.2741%
2017-10-15 | 10 | 6127 | 118.8636 | 1.94% | 16.4211 | 0.268% | 135.2847 | 2.208% | 551 | 6110.5789 | 5991.7153 | 1.984% | 0.2741%
2017-11-24 | 16 | 6127 | 118.8636 | 1.94% | 16.4211 | 0.268% | 135.2847 | 2.208% | 552 | 6110.5789 | 5991.7153 | 1.984% | 0.2741%
2017-10-28 | 22 | 6129 | 118.8882 | 1.94% | 16.4237 | 0.268% | 135.3118 | 2.208% | 553 | 6112.5763 | 5993.6882 | 1.984% | 0.274%
2017-11-05 | 22 | 6135 | 118.9618 | 1.939% | 16.4315 | 0.2678% | 135.3933 | 2.207% | 554 | 6118.5685 | 5999.6067 | 1.983% | 0.2739%
2017-11-04 | 10 | 6136 | 118.9741 | 1.939% | 16.4328 | 0.2678% | 135.4069 | 2.207% | 555 | 6119.5672 | 6000.5931 | 1.983% | 0.2739%
2017-10-12 | 5 | 6139 | 119.0109 | 1.939% | 16.4367 | 0.2677% | 135.4476 | 2.206% | 556 | 6122.5633 | 6003.5524 | 1.982% | 0.2738%
2017-11-26 | 13 | 6140 | 119.0232 | 1.938% | 16.438 | 0.2677% | 135.4612 | 2.206% | 557 | 6123.562 | 6004.5388 | 1.982% | 0.2738%
2017-09-05 | 1 | 6143 | 119.06 | 1.938% | 16.4419 | 0.2677% | 135.5019 | 2.206% | 558 | 6126.5581 | 6007.4981 | 1.982% | 0.2737%
2017-11-21 | 24 | 6147 | 119.1091 | 1.938% | 16.4471 | 0.2676% | 135.5562 | 2.205% | 559 | 6130.5529 | 6011.4438 | 1.981% | 0.2736%
2017-10-23 | 7 | 6148 | 119.1214 | 1.938% | 16.4484 | 0.2675% | 135.5698 | 2.205% | 560 | 6131.5516 | 6012.4302 | 1.981% | 0.2736%
2017-10-28 | 17 | 6155 | 119.2073 | 1.937% | 16.4575 | 0.2674% | 135.6648 | 2.204% | 561 | 6138.5425 | 6019.3352 | 1.98% | 0.2734%
2017-09-17 | 1 | 6156 | 119.2196 | 1.937% | 16.4588 | 0.2674% | 135.6784 | 2.204% | 562 | 6139.5412 | 6020.3216 | 1.98% | 0.2734%
2017-10-21 | 22 | 6160 | 119.2687 | 1.936% | 16.464 | 0.2673% | 135.7327 | 2.203% | 563 | 6143.536 | 6024.2673 | 1.98% | 0.2733%
2017-10-29 | 15 | 6161 | 119.281 | 1.936% | 16.4653 | 0.2673% | 135.7463 | 2.203% | 564 | 6144.5347 | 6025.2537 | 1.98% | 0.2733%
2017-11-03 | 7 | 6163 | 119.3055 | 1.936% | 16.4679 | 0.2672% | 135.7734 | 2.203% | 565 | 6146.5321 | 6027.2266 | 1.979% | 0.2732%
2017-10-29 | 16 | 6168 | 119.3669 | 1.935% | 16.4744 | 0.2671% | 135.8413 | 2.202% | 566 | 6151.5256 | 6032.1587 | 1.979% | 0.2731%
2017-11-07 | 23 | 6169 | 119.3792 | 1.935% | 16.4757 | 0.2671% | 135.8549 | 2.202% | 567 | 6152.5243 | 6033.1451 | 1.979% | 0.2731%
2017-10-04 | 7 | 6170 | 119.3914 | 1.935% | 16.477 | 0.2671% | 135.8685 | 2.202% | 568 | 6153.523 | 6034.1315 | 1.979% | 0.2731%
2017-09-13 | 1 | 6175 | 119.4528 | 1.934% | 16.4835 | 0.2669% | 135.9363 | 2.201% | 569 | 6158.5165 | 6039.0637 | 1.978% | 0.2729%
2017-10-24 | 7 | 6175 | 119.4528 | 1.934% | 16.4835 | 0.2669% | 135.9363 | 2.201% | 570 | 6158.5165 | 6039.0637 | 1.978% | 0.2729%
2017-09-06 | 24 | 6176 | 119.4651 | 1.934% | 16.4848 | 0.2669% | 135.9499 | 2.201% | 571 | 6159.5152 | 6040.0501 | 1.978% | 0.2729%
2017-09-21 | 2 | 6178 | 119.4896 | 1.934% | 16.4874 | 0.2669% | 135.9771 | 2.201% | 572 | 6161.5126 | 6042.0229 | 1.978% | 0.2729%
2017-09-26 | 6 | 6184 | 119.5633 | 1.933% | 16.4952 | 0.2667% | 136.0585 | 2.2% | 573 | 6167.5048 | 6047.9415 | 1.977% | 0.2727%
2017-10-09 | 5 | 6184 | 119.5633 | 1.933% | 16.4952 | 0.2667% | 136.0585 | 2.2% | 574 | 6167.5048 | 6047.9415 | 1.977% | 0.2727%
2017-10-29 | 23 | 6184 | 119.5633 | 1.933% | 16.4952 | 0.2667% | 136.0585 | 2.2% | 575 | 6167.5048 | 6047.9415 | 1.977% | 0.2727%
2017-09-29 | 24 | 6187 | 119.6001 | 1.933% | 16.4991 | 0.2667% | 136.0992 | 2.2% | 576 | 6170.5009 | 6050.9008 | 1.977% | 0.2727%
2017-10-09 | 3 | 6187 | 119.6001 | 1.933% | 16.4991 | 0.2667% | 136.0992 | 2.2% | 577 | 6170.5009 | 6050.9008 | 1.977% | 0.2727%
2017-10-05 | 24 | 6188 | 119.6124 | 1.933% | 16.5004 | 0.2667% | 136.1128 | 2.2% | 578 | 6171.4996 | 6051.8872 | 1.976% | 0.2726%
2017-09-19 | 1 | 6189 | 119.6247 | 1.933% | 16.5017 | 0.2666% | 136.1264 | 2.199% | 579 | 6172.4983 | 6052.8736 | 1.976% | 0.2726%
2017-11-18 | 14 | 6189 | 119.6247 | 1.933% | 16.5017 | 0.2666% | 136.1264 | 2.199% | 580 | 6172.4983 | 6052.8736 | 1.976% | 0.2726%
2017-10-25 | 23 | 6190 | 119.6369 | 1.933% | 16.503 | 0.2666% | 136.14 | 2.199% | 581 | 6173.497 | 6053.86 | 1.976% | 0.2726%
2017-09-03 | 1 | 6191 | 119.6492 | 1.933% | 16.5043 | 0.2666% | 136.1536 | 2.199% | 582 | 6174.4957 | 6054.8464 | 1.976% | 0.2726%
2017-11-03 | 23 | 6193 | 119.6738 | 1.932% | 16.5069 | 0.2665% | 136.1807 | 2.199% | 583 | 6176.4931 | 6056.8193 | 1.976% | 0.2725%
2017-09-17 | 9 | 6194 | 119.686 | 1.932% | 16.5082 | 0.2665% | 136.1943 | 2.199% | 584 | 6177.4918 | 6057.8057 | 1.976% | 0.2725%
2017-11-14 | 3 | 6194 | 119.686 | 1.932% | 16.5082 | 0.2665% | 136.1943 | 2.199% | 585 | 6177.4918 | 6057.8057 | 1.976% | 0.2725%
2017-11-14 | 2 | 6195 | 119.6983 | 1.932% | 16.5095 | 0.2665% | 136.2079 | 2.199% | 586 | 6178.4905 | 6058.7921 | 1.976% | 0.2725%
2017-10-28 | 9 | 6196 | 119.7106 | 1.932% | 16.5108 | 0.2665% | 136.2214 | 2.199% | 587 | 6179.4892 | 6059.7786 | 1.975% | 0.2725%
2017-11-01 | 23 | 6196 | 119.7106 | 1.932% | 16.5108 | 0.2665% | 136.2214 | 2.199% | 588 | 6179.4892 | 6059.7786 | 1.975% | 0.2725%
2017-09-07 | 7 | 6199 | 119.7474 | 1.932% | 16.5147 | 0.2664% | 136.2622 | 2.198% | 589 | 6182.4853 | 6062.7378 | 1.975% | 0.2724%
2017-10-06 | 7 | 6201 | 119.772 | 1.931% | 16.5173 | 0.2664% | 136.2893 | 2.198% | 590 | 6184.4827 | 6064.7107 | 1.975% | 0.2724%
2017-11-19 | 11 | 6203 | 119.7965 | 1.931% | 16.5199 | 0.2663% | 136.3165 | 2.198% | 591 | 6186.4801 | 6066.6835 | 1.975% | 0.2723%
2017-10-28 | 12 | 6205 | 119.8211 | 1.931% | 16.5226 | 0.2663% | 136.3436 | 2.197% | 592 | 6188.4774 | 6068.6564 | 1.974% | 0.2723%
2017-11-01 | 6 | 6207 | 119.8456 | 1.931% | 16.5252 | 0.2662% | 136.3708 | 2.197% | 593 | 6190.4748 | 6070.6292 | 1.974% | 0.2722%
2017-10-24 | 23 | 6208 | 119.8579 | 1.931% | 16.5265 | 0.2662% | 136.3843 | 2.197% | 594 | 6191.4735 | 6071.6157 | 1.974% | 0.2722%
2017-11-23 | 2 | 6208 | 119.8579 | 1.931% | 16.5265 | 0.2662% | 136.3843 | 2.197% | 595 | 6191.4735 | 6071.6157 | 1.974% | 0.2722%
2017-10-17 | 7 | 6211 | 119.8947 | 1.93% | 16.5304 | 0.2661% | 136.4251 | 2.197% | 596 | 6194.4696 | 6074.5749 | 1.974% | 0.2721%
2017-10-31 | 23 | 6213 | 119.9193 | 1.93% | 16.533 | 0.2661% | 136.4522 | 2.196% | 597 | 6196.467 | 6076.5478 | 1.973% | 0.2721%
2017-11-26 | 17 | 6214 | 119.9315 | 1.93% | 16.5343 | 0.2661% | 136.4658 | 2.196% | 598 | 6197.4657 | 6077.5342 | 1.973% | 0.2721%
2017-11-30 | 2 | 6214 | 119.9315 | 1.93% | 16.5343 | 0.2661% | 136.4658 | 2.196% | 599 | 6197.4657 | 6077.5342 | 1.973% | 0.2721%
2017-09-10 | 13 | 6218 | 119.9806 | 1.93% | 16.5395 | 0.266% | 136.5201 | 2.196% | 600 | 6201.4605 | 6081.4799 | 1.973% | 0.272%
2017-09-14 | 1 | 6223 | 120.042 | 1.929% | 16.546 | 0.2659% | 136.588 | 2.195% | 601 | 6206.454 | 6086.412 | 1.972% | 0.2719%
2017-10-02 | 8 | 6223 | 120.042 | 1.929% | 16.546 | 0.2659% | 136.588 | 2.195% | 602 | 6206.454 | 6086.412 | 1.972% | 0.2719%
2017-10-28 | 18 | 6223 | 120.042 | 1.929% | 16.546 | 0.2659% | 136.588 | 2.195% | 603 | 6206.454 | 6086.412 | 1.972% | 0.2719%
2017-11-02 | 23 | 6224 | 120.0543 | 1.929% | 16.5473 | 0.2659% | 136.6016 | 2.195% | 604 | 6207.4527 | 6087.3984 | 1.972% | 0.2718%
2017-11-07 | 7 | 6226 | 120.0788 | 1.929% | 16.5499 | 0.2658% | 136.6287 | 2.194% | 605 | 6209.4501 | 6089.3713 | 1.972% | 0.2718%
2017-11-18 | 17 | 6226 | 120.0788 | 1.929% | 16.5499 | 0.2658% | 136.6287 | 2.194% | 606 | 6209.4501 | 6089.3713 | 1.972% | 0.2718%
2017-09-28 | 2 | 6227 | 120.0911 | 1.929% | 16.5512 | 0.2658% | 136.6423 | 2.194% | 607 | 6210.4488 | 6090.3577 | 1.972% | 0.2718%
2017-09-11 | 8 | 6230 | 120.1279 | 1.928% | 16.5551 | 0.2657% | 136.683 | 2.194% | 608 | 6213.4449 | 6093.317 | 1.971% | 0.2717%
2017-11-23 | 3 | 6230 | 120.1279 | 1.928% | 16.5551 | 0.2657% | 136.683 | 2.194% | 609 | 6213.4449 | 6093.317 | 1.971% | 0.2717%
2017-09-08 | 8 | 6231 | 120.1402 | 1.928% | 16.5564 | 0.2657% | 136.6966 | 2.194% | 610 | 6214.4436 | 6094.3034 | 1.971% | 0.2717%
2017-11-29 | 3 | 6231 | 120.1402 | 1.928% | 16.5564 | 0.2657% | 136.6966 | 2.194% | 611 | 6214.4436 | 6094.3034 | 1.971% | 0.2717%
2017-09-06 | 6 | 6232 | 120.1525 | 1.928% | 16.5577 | 0.2657% | 136.7102 | 2.194% | 612 | 6215.4423 | 6095.2898 | 1.971% | 0.2716%
2017-11-04 | 22 | 6234 | 120.177 | 1.928% | 16.5603 | 0.2656% | 136.7373 | 2.193% | 613 | 6217.4397 | 6097.2627 | 1.971% | 0.2716%
2017-11-09 | 24 | 6236 | 120.2016 | 1.928% | 16.5629 | 0.2656% | 136.7645 | 2.193% | 614 | 6219.4371 | 6099.2355 | 1.971% | 0.2716%
2017-10-07 | 9 | 6237 | 120.2139 | 1.927% | 16.5642 | 0.2656% | 136.7781 | 2.193% | 615 | 6220.4358 | 6100.2219 | 1.971% | 0.2715%
2017-10-12 | 3 | 6239 | 120.2384 | 1.927% | 16.5668 | 0.2655% | 136.8052 | 2.193% | 616 | 6222.4332 | 6102.1948 | 1.97% | 0.2715%
2017-11-30 | 1 | 6240 | 120.2507 | 1.927% | 16.5681 | 0.2655% | 136.8188 | 2.193% | 617 | 6223.4319 | 6103.1812 | 1.97% | 0.2715%
2017-11-05 | 15 | 6241 | 120.263 | 1.927% | 16.5694 | 0.2655% | 136.8324 | 2.192% | 618 | 6224.4306 | 6104.1676 | 1.97% | 0.2714%
2017-11-26 | 6 | 6241 | 120.263 | 1.927% | 16.5694 | 0.2655% | 136.8324 | 2.192% | 619 | 6224.4306 | 6104.1676 | 1.97% | 0.2714%
2017-10-06 | 24 | 6247 | 120.3366 | 1.926% | 16.5772 | 0.2654% | 136.9138 | 2.192% | 620 | 6230.4228 | 6110.0862 | 1.969% | 0.2713%
2017-09-30 | 10 | 6248 | 120.3489 | 1.926% | 16.5785 | 0.2653% | 136.9274 | 2.192% | 621 | 6231.4215 | 6111.0726 | 1.969% | 0.2713%
2017-10-21 | 13 | 6248 | 120.3489 | 1.926% | 16.5785 | 0.2653% | 136.9274 | 2.192% | 622 | 6231.4215 | 6111.0726 | 1.969% | 0.2713%
2017-09-03 | 24 | 6249 | 120.3612 | 1.926% | 16.5798 | 0.2653% | 136.941 | 2.191% | 623 | 6232.4202 | 6112.059 | 1.969% | 0.2713%
2017-11-19 | 10 | 6250 | 120.3735 | 1.926% | 16.5811 | 0.2653% | 136.9545 | 2.191% | 624 | 6233.4189 | 6113.0455 | 1.969% | 0.2712%
2017-10-01 | 15 | 6255 | 120.4348 | 1.925% | 16.5876 | 0.2652% | 137.0224 | 2.191% | 625 | 6238.4124 | 6117.9776 | 1.969% | 0.2711%
2017-11-18 | 22 | 6256 | 120.4471 | 1.925% | 16.5889 | 0.2652% | 137.036 | 2.19% | 626 | 6239.4111 | 6118.964 | 1.968% | 0.2711%
2017-11-29 | 2 | 6258 | 120.4717 | 1.925% | 16.5915 | 0.2651% | 137.0632 | 2.19% | 627 | 6241.4085 | 6120.9368 | 1.968% | 0.2711%
2017-10-05 | 7 | 6259 | 120.4839 | 1.925% | 16.5928 | 0.2651% | 137.0767 | 2.19% | 628 | 6242.4072 | 6121.9233 | 1.968% | 0.271%
2017-10-29 | 18 | 6259 | 120.4839 | 1.925% | 16.5928 | 0.2651% | 137.0767 | 2.19% | 629 | 6242.4072 | 6121.9233 | 1.968% | 0.271%
2017-11-14 | 1 | 6259 | 120.4839 | 1.925% | 16.5928 | 0.2651% | 137.0767 | 2.19% | 630 | 6242.4072 | 6121.9233 | 1.968% | 0.271%
2017-11-30 | 3 | 6261 | 120.5085 | 1.925% | 16.5954 | 0.2651% | 137.1039 | 2.19% | 631 | 6244.4046 | 6123.8961 | 1.968% | 0.271%
2017-09-11 | 23 | 6264 | 120.5453 | 1.924% | 16.5993 | 0.265% | 137.1446 | 2.189% | 632 | 6247.4007 | 6126.8554 | 1.967% | 0.2709%
2017-09-22 | 1 | 6269 | 120.6067 | 1.924% | 16.6058 | 0.2649% | 137.2125 | 2.189% | 633 | 6252.3942 | 6131.7875 | 1.967% | 0.2708%
2017-11-06 | 7 | 6276 | 120.6926 | 1.923% | 16.6149 | 0.2647% | 137.3075 | 2.188% | 634 | 6259.3851 | 6138.6925 | 1.966% | 0.2707%
2017-11-19 | 17 | 6280 | 120.7417 | 1.923% | 16.6201 | 0.2647% | 137.3618 | 2.187% | 635 | 6263.3799 | 6142.6382 | 1.966% | 0.2706%
2017-10-08 | 8 | 6281 | 120.754 | 1.923% | 16.6214 | 0.2646% | 137.3754 | 2.187% | 636 | 6264.3786 | 6143.6246 | 1.966% | 0.2705%
2017-10-13 | 1 | 6281 | 120.754 | 1.923% | 16.6214 | 0.2646% | 137.3754 | 2.187% | 637 | 6264.3786 | 6143.6246 | 1.966% | 0.2705%
2017-10-25 | 7 | 6282 | 120.7663 | 1.922% | 16.6227 | 0.2646% | 137.389 | 2.187% | 638 | 6265.3773 | 6144.611 | 1.965% | 0.2705%
2017-10-28 | 11 | 6283 | 120.7785 | 1.922% | 16.624 | 0.2646% | 137.4026 | 2.187% | 639 | 6266.376 | 6145.5974 | 1.965% | 0.2705%
2017-10-14 | 10 | 6284 | 120.7908 | 1.922% | 16.6253 | 0.2646% | 137.4161 | 2.187% | 640 | 6267.3747 | 6146.5839 | 1.965% | 0.2705%
2017-10-08 | 2 | 6286 | 120.8154 | 1.922% | 16.6279 | 0.2645% | 137.4433 | 2.186% | 641 | 6269.3721 | 6148.5567 | 1.965% | 0.2704%
2017-10-26 | 15 | 6287 | 120.8276 | 1.922% | 16.6292 | 0.2645% | 137.4569 | 2.186% | 642 | 6270.3708 | 6149.5431 | 1.965% | 0.2704%
2017-11-26 | 12 | 6290 | 120.8645 | 1.922% | 16.6331 | 0.2644% | 137.4976 | 2.186% | 643 | 6273.3669 | 6152.5024 | 1.964% | 0.2703%
2017-10-26 | 16 | 6292 | 120.889 | 1.921% | 16.6357 | 0.2644% | 137.5247 | 2.186% | 644 | 6275.3643 | 6154.4753 | 1.964% | 0.2703%
2017-10-31 | 5 | 6297 | 120.9504 | 1.921% | 16.6422 | 0.2643% | 137.5926 | 2.185% | 645 | 6280.3578 | 6159.4074 | 1.964% | 0.2702%
2017-09-15 | 1 | 6298 | 120.9627 | 1.921% | 16.6435 | 0.2643% | 137.6062 | 2.185% | 646 | 6281.3565 | 6160.3938 | 1.964% | 0.2702%
2017-10-27 | 22 | 6298 | 120.9627 | 1.921% | 16.6435 | 0.2643% | 137.6062 | 2.185% | 647 | 6281.3565 | 6160.3938 | 1.964% | 0.2702%
2017-11-23 | 4 | 6299 | 120.9749 | 1.921% | 16.6448 | 0.2642% | 137.6198 | 2.185% | 648 | 6282.3552 | 6161.3802 | 1.963% | 0.2701%
2017-09-23 | 9 | 6300 | 120.9872 | 1.92% | 16.6461 | 0.2642% | 137.6333 | 2.185% | 649 | 6283.3539 | 6162.3667 | 1.963% | 0.2701%
2017-10-22 | 13 | 6301 | 120.9995 | 1.92% | 16.6474 | 0.2642% | 137.6469 | 2.185% | 650 | 6284.3526 | 6163.3531 | 1.963% | 0.2701%
2017-11-29 | 4 | 6301 | 120.9995 | 1.92% | 16.6474 | 0.2642% | 137.6469 | 2.185% | 651 | 6284.3526 | 6163.3531 | 1.963% | 0.2701%
2017-11-14 | 4 | 6302 | 121.0118 | 1.92% | 16.6487 | 0.2642% | 137.6605 | 2.184% | 652 | 6285.3513 | 6164.3395 | 1.963% | 0.2701%
2017-11-23 | 1 | 6303 | 121.024 | 1.92% | 16.65 | 0.2642% | 137.6741 | 2.184% | 653 | 6286.35 | 6165.3259 | 1.963% | 0.2701%
2017-10-27 | 15 | 6306 | 121.0609 | 1.92% | 16.6539 | 0.2641% | 137.7148 | 2.184% | 654 | 6289.3461 | 6168.2852 | 1.963% | 0.27%
2017-10-09 | 2 | 6309 | 121.0977 | 1.919% | 16.6578 | 0.264% | 137.7555 | 2.183% | 655 | 6292.3422 | 6171.2445 | 1.962% | 0.2699%
2017-09-09 | 23 | 6310 | 121.11 | 1.919% | 16.6591 | 0.264% | 137.7691 | 2.183% | 656 | 6293.3409 | 6172.2309 | 1.962% | 0.2699%
2017-11-24 | 14 | 6310 | 121.11 | 1.919% | 16.6591 | 0.264% | 137.7691 | 2.183% | 657 | 6293.3409 | 6172.2309 | 1.962% | 0.2699%
2017-10-27 | 17 | 6311 | 121.1222 | 1.919% | 16.6604 | 0.264% | 137.7827 | 2.183% | 658 | 6294.3396 | 6173.2173 | 1.962% | 0.2699%
2017-09-06 | 2 | 6313 | 121.1468 | 1.919% | 16.663 | 0.2639% | 137.8098 | 2.183% | 659 | 6296.337 | 6175.1902 | 1.962% | 0.2698%
2017-10-28 | 10 | 6313 | 121.1468 | 1.919% | 16.663 | 0.2639% | 137.8098 | 2.183% | 660 | 6296.337 | 6175.1902 | 1.962% | 0.2698%
2017-11-04 | 11 | 6315 | 121.1713 | 1.919% | 16.6657 | 0.2639% | 137.837 | 2.183% | 661 | 6298.3343 | 6177.163 | 1.962% | 0.2698%
2017-10-17 | 15 | 6316 | 121.1836 | 1.919% | 16.667 | 0.2639% | 137.8506 | 2.183% | 662 | 6299.333 | 6178.1494 | 1.961% | 0.2698%
2017-10-27 | 16 | 6316 | 121.1836 | 1.919% | 16.667 | 0.2639% | 137.8506 | 2.183% | 663 | 6299.333 | 6178.1494 | 1.961% | 0.2698%
2017-10-03 | 8 | 6317 | 121.1959 | 1.919% | 16.6683 | 0.2639% | 137.8641 | 2.182% | 664 | 6300.3317 | 6179.1359 | 1.961% | 0.2698%
2017-09-01 | 2 | 6320 | 121.2327 | 1.918% | 16.6722 | 0.2638% | 137.9049 | 2.182% | 665 | 6303.3278 | 6182.0951 | 1.961% | 0.2697%
2017-09-16 | 1 | 6320 | 121.2327 | 1.918% | 16.6722 | 0.2638% | 137.9049 | 2.182% | 666 | 6303.3278 | 6182.0951 | 1.961% | 0.2697%
2017-09-27 | 2 | 6320 | 121.2327 | 1.918% | 16.6722 | 0.2638% | 137.9049 | 2.182% | 667 | 6303.3278 | 6182.0951 | 1.961% | 0.2697%
2017-10-17 | 16 | 6324 | 121.2818 | 1.918% | 16.6774 | 0.2637% | 137.9592 | 2.182% | 668 | 6307.3226 | 6186.0408 | 1.961% | 0.2696%
2017-09-02 | 9 | 6325 | 121.2941 | 1.918% | 16.6787 | 0.2637% | 137.9728 | 2.181% | 669 | 6308.3213 | 6187.0272 | 1.96% | 0.2696%
2017-09-10 | 14 | 6330 | 121.3555 | 1.917% | 16.6852 | 0.2636% | 138.0406 | 2.181% | 670 | 6313.3148 | 6191.9594 | 1.96% | 0.2695%
2017-10-27 | 18 | 6330 | 121.3555 | 1.917% | 16.6852 | 0.2636% | 138.0406 | 2.181% | 671 | 6313.3148 | 6191.9594 | 1.96% | 0.2695%
2017-10-17 | 14 | 6333 | 121.3923 | 1.917% | 16.6891 | 0.2635% | 138.0814 | 2.18% | 672 | 6316.3109 | 6194.9186 | 1.96% | 0.2694%
2017-11-25 | 13 | 6333 | 121.3923 | 1.917% | 16.6891 | 0.2635% | 138.0814 | 2.18% | 673 | 6316.3109 | 6194.9186 | 1.96% | 0.2694%
2017-10-02 | 9 | 6334 | 121.4046 | 1.917% | 16.6904 | 0.2635% | 138.0949 | 2.18% | 674 | 6317.3096 | 6195.9051 | 1.959% | 0.2694%
2017-09-04 | 10 | 6335 | 121.4168 | 1.917% | 16.6917 | 0.2635% | 138.1085 | 2.18% | 675 | 6318.3083 | 6196.8915 | 1.959% | 0.2694%
2017-09-12 | 7 | 6335 | 121.4168 | 1.917% | 16.6917 | 0.2635% | 138.1085 | 2.18% | 676 | 6318.3083 | 6196.8915 | 1.959% | 0.2694%
2017-09-29 | 2 | 6336 | 121.4291 | 1.916% | 16.693 | 0.2635% | 138.1221 | 2.18% | 677 | 6319.307 | 6197.8779 | 1.959% | 0.2693%
2017-11-02 | 7 | 6339 | 121.4659 | 1.916% | 16.6969 | 0.2634% | 138.1628 | 2.18% | 678 | 6322.3031 | 6200.8372 | 1.959% | 0.2693%
2017-11-25 | 23 | 6339 | 121.4659 | 1.916% | 16.6969 | 0.2634% | 138.1628 | 2.18% | 679 | 6322.3031 | 6200.8372 | 1.959% | 0.2693%
2017-10-26 | 17 | 6340 | 121.4782 | 1.916% | 16.6982 | 0.2634% | 138.1764 | 2.179% | 680 | 6323.3018 | 6201.8236 | 1.959% | 0.2692%
2017-11-24 | 17 | 6345 | 121.5396 | 1.916% | 16.7047 | 0.2633% | 138.2443 | 2.179% | 681 | 6328.2953 | 6206.7557 | 1.958% | 0.2691%
2017-10-28 | 21 | 6348 | 121.5764 | 1.915% | 16.7086 | 0.2632% | 138.285 | 2.178% | 682 | 6331.2914 | 6209.715 | 1.958% | 0.2691%
2017-09-01 | 6 | 6352 | 121.6255 | 1.915% | 16.7138 | 0.2631% | 138.3393 | 2.178% | 683 | 6335.2862 | 6213.6607 | 1.957% | 0.269%
2017-09-26 | 1 | 6356 | 121.6746 | 1.914% | 16.719 | 0.263% | 138.3936 | 2.177% | 684 | 6339.281 | 6217.6064 | 1.957% | 0.2689%
2017-09-23 | 1 | 6357 | 121.6869 | 1.914% | 16.7203 | 0.263% | 138.4072 | 2.177% | 685 | 6340.2797 | 6218.5928 | 1.957% | 0.2689%
2017-10-17 | 13 | 6359 | 121.7114 | 1.914% | 16.7229 | 0.263% | 138.4343 | 2.177% | 686 | 6342.2771 | 6220.5657 | 1.957% | 0.2688%
2017-10-29 | 17 | 6359 | 121.7114 | 1.914% | 16.7229 | 0.263% | 138.4343 | 2.177% | 687 | 6342.2771 | 6220.5657 | 1.957% | 0.2688%
2017-10-02 | 23 | 6361 | 121.736 | 1.914% | 16.7255 | 0.2629% | 138.4615 | 2.177% | 688 | 6344.2745 | 6222.5385 | 1.956% | 0.2688%
2017-10-17 | 17 | 6362 | 121.7483 | 1.914% | 16.7268 | 0.2629% | 138.4751 | 2.177% | 689 | 6345.2732 | 6223.5249 | 1.956% | 0.2688%
2017-10-18 | 14 | 6362 | 121.7483 | 1.914% | 16.7268 | 0.2629% | 138.4751 | 2.177% | 690 | 6345.2732 | 6223.5249 | 1.956% | 0.2688%
2017-09-07 | 8 | 6363 | 121.7605 | 1.914% | 16.7281 | 0.2629% | 138.4886 | 2.176% | 691 | 6346.2719 | 6224.5114 | 1.956% | 0.2687%
2017-10-26 | 14 | 6364 | 121.7728 | 1.913% | 16.7294 | 0.2629% | 138.5022 | 2.176% | 692 | 6347.2706 | 6225.4978 | 1.956% | 0.2687%
2017-10-20 | 22 | 6366 | 121.7974 | 1.913% | 16.732 | 0.2628% | 138.5294 | 2.176% | 693 | 6349.268 | 6227.4706 | 1.956% | 0.2687%
2017-10-11 | 4 | 6368 | 121.8219 | 1.913% | 16.7346 | 0.2628% | 138.5565 | 2.176% | 694 | 6351.2654 | 6229.4435 | 1.956% | 0.2686%
2017-10-20 | 7 | 6369 | 121.8342 | 1.913% | 16.7359 | 0.2628% | 138.5701 | 2.176% | 695 | 6352.2641 | 6230.4299 | 1.955% | 0.2686%
2017-09-11 | 9 | 6371 | 121.8588 | 1.913% | 16.7385 | 0.2627% | 138.5973 | 2.175% | 696 | 6354.2615 | 6232.4027 | 1.955% | 0.2686%
2017-11-29 | 1 | 6371 | 121.8588 | 1.913% | 16.7385 | 0.2627% | 138.5973 | 2.175% | 697 | 6354.2615 | 6232.4027 | 1.955% | 0.2686%
2017-10-18 | 15 | 6374 | 121.8956 | 1.912% | 16.7424 | 0.2627% | 138.638 | 2.175% | 698 | 6357.2576 | 6235.362 | 1.955% | 0.2685%
2017-10-21 | 14 | 6375 | 121.9079 | 1.912% | 16.7437 | 0.2626% | 138.6516 | 2.175% | 699 | 6358.2563 | 6236.3484 | 1.955% | 0.2685%
2017-11-04 | 12 | 6375 | 121.9079 | 1.912% | 16.7437 | 0.2626% | 138.6516 | 2.175% | 700 | 6358.2563 | 6236.3484 | 1.955% | 0.2685%
2017-11-05 | 16 | 6377 | 121.9324 | 1.912% | 16.7463 | 0.2626% | 138.6787 | 2.175% | 701 | 6360.2537 | 6238.3213 | 1.955% | 0.2684%
2017-09-02 | 1 | 6378 | 121.9447 | 1.912% | 16.7476 | 0.2626% | 138.6923 | 2.175% | 702 | 6361.2524 | 6239.3077 | 1.954% | 0.2684%
2017-10-27 | 14 | 6380 | 121.9692 | 1.912% | 16.7502 | 0.2625% | 138.7194 | 2.174% | 703 | 6363.2498 | 6241.2806 | 1.954% | 0.2684%
2017-10-03 | 9 | 6386 | 122.0429 | 1.911% | 16.758 | 0.2624% | 138.8009 | 2.174% | 704 | 6369.242 | 6247.1991 | 1.954% | 0.2682%
2017-10-14 | 23 | 6388 | 122.0674 | 1.911% | 16.7606 | 0.2624% | 138.828 | 2.173% | 705 | 6371.2394 | 6249.172 | 1.953% | 0.2682%
2017-10-15 | 11 | 6388 | 122.0674 | 1.911% | 16.7606 | 0.2624% | 138.828 | 2.173% | 706 | 6371.2394 | 6249.172 | 1.953% | 0.2682%
2017-10-03 | 23 | 6394 | 122.1411 | 1.91% | 16.7684 | 0.2623% | 138.9095 | 2.172% | 707 | 6377.2316 | 6255.0905 | 1.953% | 0.2681%
2017-11-18 | 13 | 6394 | 122.1411 | 1.91% | 16.7684 | 0.2623% | 138.9095 | 2.172% | 708 | 6377.2316 | 6255.0905 | 1.953% | 0.2681%
2017-10-01 | 22 | 6395 | 122.1534 | 1.91% | 16.7697 | 0.2622% | 138.9231 | 2.172% | 709 | 6378.2303 | 6256.0769 | 1.953% | 0.2681%
2017-10-01 | 16 | 6397 | 122.1779 | 1.91% | 16.7723 | 0.2622% | 138.9502 | 2.172% | 710 | 6380.2277 | 6258.0498 | 1.952% | 0.268%
2017-10-11 | 5 | 6397 | 122.1779 | 1.91% | 16.7723 | 0.2622% | 138.9502 | 2.172% | 711 | 6380.2277 | 6258.0498 | 1.952% | 0.268%
2017-11-10 | 15 | 6398 | 122.1902 | 1.91% | 16.7736 | 0.2622% | 138.9638 | 2.172% | 712 | 6381.2264 | 6259.0362 | 1.952% | 0.268%
2017-10-17 | 12 | 6399 | 122.2025 | 1.91% | 16.7749 | 0.2621% | 138.9774 | 2.172% | 713 | 6382.2251 | 6260.0226 | 1.952% | 0.268%
2017-10-18 | 13 | 6400 | 122.2147 | 1.91% | 16.7762 | 0.2621% | 138.991 | 2.172% | 714 | 6383.2238 | 6261.009 | 1.952% | 0.2679%
2017-11-08 | 24 | 6400 | 122.2147 | 1.91% | 16.7762 | 0.2621% | 138.991 | 2.172% | 715 | 6383.2238 | 6261.009 | 1.952% | 0.2679%
2017-09-08 | 9 | 6401 | 122.227 | 1.909% | 16.7775 | 0.2621% | 139.0045 | 2.172% | 716 | 6384.2225 | 6261.9955 | 1.952% | 0.2679%
2017-10-04 | 8 | 6401 | 122.227 | 1.909% | 16.7775 | 0.2621% | 139.0045 | 2.172% | 717 | 6384.2225 | 6261.9955 | 1.952% | 0.2679%
2017-10-27 | 19 | 6405 | 122.2761 | 1.909% | 16.7827 | 0.262% | 139.0588 | 2.171% | 718 | 6388.2173 | 6265.9412 | 1.951% | 0.2678%
2017-09-16 | 9 | 6406 | 122.2884 | 1.909% | 16.784 | 0.262% | 139.0724 | 2.171% | 719 | 6389.216 | 6266.9276 | 1.951% | 0.2678%
2017-09-27 | 6 | 6407 | 122.3007 | 1.909% | 16.7853 | 0.262% | 139.086 | 2.171% | 720 | 6390.2147 | 6267.914 | 1.951% | 0.2678%
2017-10-25 | 15 | 6408 | 122.3129 | 1.909% | 16.7866 | 0.262% | 139.0996 | 2.171% | 721 | 6391.2134 | 6268.9004 | 1.951% | 0.2678%
2017-10-14 | 11 | 6409 | 122.3252 | 1.909% | 16.7879 | 0.2619% | 139.1131 | 2.171% | 722 | 6392.2121 | 6269.8869 | 1.951% | 0.2678%
2017-09-24 | 24 | 6411 | 122.3498 | 1.908% | 16.7905 | 0.2619% | 139.1403 | 2.17% | 723 | 6394.2095 | 6271.8597 | 1.951% | 0.2677%
2017-10-16 | 7 | 6411 | 122.3498 | 1.908% | 16.7905 | 0.2619% | 139.1403 | 2.17% | 724 | 6394.2095 | 6271.8597 | 1.951% | 0.2677%
2017-10-30 | 24 | 6411 | 122.3498 | 1.908% | 16.7905 | 0.2619% | 139.1403 | 2.17% | 725 | 6394.2095 | 6271.8597 | 1.951% | 0.2677%
2017-11-17 | 2 | 6412 | 122.362 | 1.908% | 16.7918 | 0.2619% | 139.1539 | 2.17% | 726 | 6395.2082 | 6272.8461 | 1.951% | 0.2677%
2017-09-10 | 15 | 6416 | 122.4111 | 1.908% | 16.797 | 0.2618% | 139.2082 | 2.17% | 727 | 6399.203 | 6276.7918 | 1.95% | 0.2676%
2017-10-25 | 14 | 6418 | 122.4357 | 1.908% | 16.7996 | 0.2618% | 139.2353 | 2.169% | 728 | 6401.2004 | 6278.7647 | 1.95% | 0.2676%
2017-11-23 | 17 | 6418 | 122.4357 | 1.908% | 16.7996 | 0.2618% | 139.2353 | 2.169% | 729 | 6401.2004 | 6278.7647 | 1.95% | 0.2676%
2017-11-10 | 16 | 6419 | 122.448 | 1.908% | 16.8009 | 0.2617% | 139.2489 | 2.169% | 730 | 6402.1991 | 6279.7511 | 1.95% | 0.2675%
2017-11-10 | 6 | 6421 | 122.4725 | 1.907% | 16.8035 | 0.2617% | 139.2761 | 2.169% | 731 | 6404.1965 | 6281.7239 | 1.95% | 0.2675%
2017-10-25 | 13 | 6422 | 122.4848 | 1.907% | 16.8049 | 0.2617% | 139.2896 | 2.169% | 732 | 6405.1951 | 6282.7104 | 1.95% | 0.2675%
2017-10-28 | 19 | 6425 | 122.5216 | 1.907% | 16.8088 | 0.2616% | 139.3304 | 2.169% | 733 | 6408.1912 | 6285.6696 | 1.949% | 0.2674%
2017-11-04 | 13 | 6427 | 122.5462 | 1.907% | 16.8114 | 0.2616% | 139.3575 | 2.168% | 734 | 6410.1886 | 6287.6425 | 1.949% | 0.2674%
2017-11-29 | 24 | 6429 | 122.5707 | 1.907% | 16.814 | 0.2615% | 139.3847 | 2.168% | 735 | 6412.186 | 6289.6153 | 1.949% | 0.2673%
2017-10-25 | 16 | 6430 | 122.583 | 1.906% | 16.8153 | 0.2615% | 139.3982 | 2.168% | 736 | 6413.1847 | 6290.6018 | 1.949% | 0.2673%
2017-11-23 | 16 | 6430 | 122.583 | 1.906% | 16.8153 | 0.2615% | 139.3982 | 2.168% | 737 | 6413.1847 | 6290.6018 | 1.949% | 0.2673%
2017-10-27 | 13 | 6436 | 122.6566 | 1.906% | 16.8231 | 0.2614% | 139.4797 | 2.167% | 738 | 6419.1769 | 6296.5203 | 1.948% | 0.2672%
2017-10-26 | 13 | 6439 | 122.6935 | 1.905% | 16.827 | 0.2613% | 139.5204 | 2.167% | 739 | 6422.173 | 6299.4796 | 1.948% | 0.2671%
2017-11-04 | 14 | 6440 | 122.7057 | 1.905% | 16.8283 | 0.2613% | 139.534 | 2.167% | 740 | 6423.1717 | 6300.466 | 1.948% | 0.2671%
2017-11-30 | 4 | 6440 | 122.7057 | 1.905% | 16.8283 | 0.2613% | 139.534 | 2.167% | 741 | 6423.1717 | 6300.466 | 1.948% | 0.2671%
2017-09-13 | 7 | 6441 | 122.718 | 1.905% | 16.8296 | 0.2613% | 139.5476 | 2.167% | 742 | 6424.1704 | 6301.4524 | 1.947% | 0.2671%
2017-10-04 | 9 | 6443 | 122.7426 | 1.905% | 16.8322 | 0.2612% | 139.5747 | 2.166% | 743 | 6426.1678 | 6303.4253 | 1.947% | 0.267%
2017-10-26 | 23 | 6443 | 122.7426 | 1.905% | 16.8322 | 0.2612% | 139.5747 | 2.166% | 744 | 6426.1678 | 6303.4253 | 1.947% | 0.267%
2017-10-31 | 15 | 6446 | 122.7794 | 1.905% | 16.8361 | 0.2612% | 139.6155 | 2.166% | 745 | 6429.1639 | 6306.3845 | 1.947% | 0.267%
2017-09-09 | 11 | 6450 | 122.8285 | 1.904% | 16.8413 | 0.2611% | 139.6698 | 2.165% | 746 | 6433.1587 | 6310.3302 | 1.946% | 0.2669%
2017-11-04 | 15 | 6450 | 122.8285 | 1.904% | 16.8413 | 0.2611% | 139.6698 | 2.165% | 747 | 6433.1587 | 6310.3302 | 1.946% | 0.2669%
2017-10-18 | 16 | 6451 | 122.8408 | 1.904% | 16.8426 | 0.2611% | 139.6833 | 2.165% | 748 | 6434.1574 | 6311.3167 | 1.946% | 0.2669%
2017-11-17 | 1 | 6458 | 122.9267 | 1.903% | 16.8517 | 0.2609% | 139.7784 | 2.164% | 749 | 6441.1483 | 6318.2216 | 1.946% | 0.2667%
2017-11-10 | 14 | 6464 | 123.0003 | 1.903% | 16.8595 | 0.2608% | 139.8598 | 2.164% | 750 | 6447.1405 | 6324.1402 | 1.945% | 0.2666%
2017-10-17 | 18 | 6465 | 123.0126 | 1.903% | 16.8608 | 0.2608% | 139.8734 | 2.164% | 751 | 6448.1392 | 6325.1266 | 1.945% | 0.2666%
2017-11-09 | 6 | 6469 | 123.0617 | 1.902% | 16.866 | 0.2607% | 139.9277 | 2.163% | 752 | 6452.134 | 6329.0723 | 1.944% | 0.2665%
2017-11-23 | 5 | 6469 | 123.0617 | 1.902% | 16.866 | 0.2607% | 139.9277 | 2.163% | 753 | 6452.134 | 6329.0723 | 1.944% | 0.2665%
2017-10-30 | 16 | 6471 | 123.0863 | 1.902% | 16.8686 | 0.2607% | 139.9549 | 2.163% | 754 | 6454.1314 | 6331.0451 | 1.944% | 0.2664%
2017-09-25 | 7 | 6473 | 123.1108 | 1.902% | 16.8712 | 0.2606% | 139.982 | 2.163% | 755 | 6456.1288 | 6333.018 | 1.944% | 0.2664%
2017-09-30 | 22 | 6473 | 123.1108 | 1.902% | 16.8712 | 0.2606% | 139.982 | 2.163% | 756 | 6456.1288 | 6333.018 | 1.944% | 0.2664%
2017-11-16 | 15 | 6473 | 123.1108 | 1.902% | 16.8712 | 0.2606% | 139.982 | 2.163% | 757 | 6456.1288 | 6333.018 | 1.944% | 0.2664%
2017-11-12 | 23 | 6474 | 123.1231 | 1.902% | 16.8725 | 0.2606% | 139.9956 | 2.162% | 758 | 6457.1275 | 6334.0044 | 1.944% | 0.2664%
2017-10-05 | 8 | 6478 | 123.1722 | 1.901% | 16.8777 | 0.2605% | 140.0499 | 2.162% | 759 | 6461.1223 | 6337.9501 | 1.943% | 0.2663%
2017-11-06 | 8 | 6479 | 123.1845 | 1.901% | 16.879 | 0.2605% | 140.0635 | 2.162% | 760 | 6462.121 | 6338.9365 | 1.943% | 0.2663%
2017-10-02 | 10 | 6480 | 123.1967 | 1.901% | 16.8803 | 0.2605% | 140.0771 | 2.162% | 761 | 6463.1197 | 6339.9229 | 1.943% | 0.2663%
2017-10-26 | 18 | 6480 | 123.1967 | 1.901% | 16.8803 | 0.2605% | 140.0771 | 2.162% | 762 | 6463.1197 | 6339.9229 | 1.943% | 0.2663%
2017-11-16 | 16 | 6480 | 123.1967 | 1.901% | 16.8803 | 0.2605% | 140.0771 | 2.162% | 763 | 6463.1197 | 6339.9229 | 1.943% | 0.2663%
2017-11-17 | 3 | 6481 | 123.209 | 1.901% | 16.8816 | 0.2605% | 140.0906 | 2.162% | 764 | 6464.1184 | 6340.9094 | 1.943% | 0.2662%
2017-10-25 | 12 | 6482 | 123.2213 | 1.901% | 16.8829 | 0.2605% | 140.1042 | 2.161% | 765 | 6465.1171 | 6341.8958 | 1.943% | 0.2662%
2017-10-25 | 17 | 6482 | 123.2213 | 1.901% | 16.8829 | 0.2605% | 140.1042 | 2.161% | 766 | 6465.1171 | 6341.8958 | 1.943% | 0.2662%
2017-09-08 | 23 | 6484 | 123.2458 | 1.901% | 16.8855 | 0.2604% | 140.1314 | 2.161% | 767 | 6467.1145 | 6343.8686 | 1.943% | 0.2662%
2017-10-21 | 21 | 6485 | 123.2581 | 1.901% | 16.8868 | 0.2604% | 140.1449 | 2.161% | 768 | 6468.1132 | 6344.8551 | 1.943% | 0.2661%
2017-10-06 | 8 | 6486 | 123.2704 | 1.901% | 16.8881 | 0.2604% | 140.1585 | 2.161% | 769 | 6469.1119 | 6345.8415 | 1.943% | 0.2661%
2017-10-18 | 12 | 6486 | 123.2704 | 1.901% | 16.8881 | 0.2604% | 140.1585 | 2.161% | 770 | 6469.1119 | 6345.8415 | 1.943% | 0.2661%
2017-10-17 | 11 | 6488 | 123.2949 | 1.9% | 16.8907 | 0.2603% | 140.1857 | 2.161% | 771 | 6471.1093 | 6347.8143 | 1.942% | 0.2661%
2017-10-11 | 3 | 6490 | 123.3195 | 1.9% | 16.8933 | 0.2603% | 140.2128 | 2.16% | 772 | 6473.1067 | 6349.7872 | 1.942% | 0.266%
2017-10-27 | 6 | 6490 | 123.3195 | 1.9% | 16.8933 | 0.2603% | 140.2128 | 2.16% | 773 | 6473.1067 | 6349.7872 | 1.942% | 0.266%
2017-09-07 | 9 | 6492 | 123.344 | 1.9% | 16.8959 | 0.2603% | 140.24 | 2.16% | 774 | 6475.1041 | 6351.76 | 1.942% | 0.266%
2017-09-10 | 22 | 6492 | 123.344 | 1.9% | 16.8959 | 0.2603% | 140.24 | 2.16% | 775 | 6475.1041 | 6351.76 | 1.942% | 0.266%
2017-10-12 | 2 | 6492 | 123.344 | 1.9% | 16.8959 | 0.2603% | 140.24 | 2.16% | 776 | 6475.1041 | 6351.76 | 1.942% | 0.266%
2017-11-07 | 8 | 6492 | 123.344 | 1.9% | 16.8959 | 0.2603% | 140.24 | 2.16% | 777 | 6475.1041 | 6351.76 | 1.942% | 0.266%
2017-09-10 | 16 | 6499 | 123.43 | 1.899% | 16.905 | 0.2601% | 140.335 | 2.159% | 778 | 6482.095 | 6358.665 | 1.941% | 0.2659%
2017-10-31 | 16 | 6500 | 123.4423 | 1.899% | 16.9063 | 0.2601% | 140.3486 | 2.159% | 779 | 6483.0937 | 6359.6514 | 1.941% | 0.2658%
2017-10-17 | 10 | 6501 | 123.4545 | 1.899% | 16.9076 | 0.2601% | 140.3621 | 2.159% | 780 | 6484.0924 | 6360.6379 | 1.941% | 0.2658%
2017-10-25 | 11 | 6503 | 123.4791 | 1.899% | 16.9102 | 0.26% | 140.3893 | 2.159% | 781 | 6486.0898 | 6362.6107 | 1.941% | 0.2658%
2017-10-27 | 21 | 6504 | 123.4914 | 1.899% | 16.9115 | 0.26% | 140.4029 | 2.159% | 782 | 6487.0885 | 6363.5971 | 1.941% | 0.2658%
2017-11-04 | 16 | 6504 | 123.4914 | 1.899% | 16.9115 | 0.26% | 140.4029 | 2.159% | 783 | 6487.0885 | 6363.5971 | 1.941% | 0.2658%
2017-10-14 | 12 | 6505 | 123.5036 | 1.899% | 16.9128 | 0.26% | 140.4165 | 2.159% | 784 | 6488.0872 | 6364.5835 | 1.94% | 0.2657%
2017-10-25 | 10 | 6507 | 123.5282 | 1.898% | 16.9154 | 0.26% | 140.4436 | 2.158% | 785 | 6490.0846 | 6366.5564 | 1.94% | 0.2657%
2017-11-05 | 17 | 6509 | 123.5527 | 1.898% | 16.918 | 0.2599% | 140.4708 | 2.158% | 786 | 6492.082 | 6368.5292 | 1.94% | 0.2657%
2017-11-17 | 16 | 6510 | 123.565 | 1.898% | 16.9193 | 0.2599% | 140.4843 | 2.158% | 787 | 6493.0807 | 6369.5157 | 1.94% | 0.2656%
2017-10-21 | 15 | 6511 | 123.5773 | 1.898% | 16.9206 | 0.2599% | 140.4979 | 2.158% | 788 | 6494.0794 | 6370.5021 | 1.94% | 0.2656%
2017-10-24 | 9 | 6511 | 123.5773 | 1.898% | 16.9206 | 0.2599% | 140.4979 | 2.158% | 789 | 6494.0794 | 6370.5021 | 1.94% | 0.2656%
2017-10-10 | 4 | 6512 | 123.5896 | 1.898% | 16.9219 | 0.2599% | 140.5115 | 2.158% | 790 | 6495.0781 | 6371.4885 | 1.94% | 0.2656%
2017-10-31 | 14 | 6512 | 123.5896 | 1.898% | 16.9219 | 0.2599% | 140.5115 | 2.158% | 791 | 6495.0781 | 6371.4885 | 1.94% | 0.2656%
2017-10-03 | 10 | 6516 | 123.6387 | 1.897% | 16.9271 | 0.2598% | 140.5658 | 2.157% | 792 | 6499.0729 | 6375.4342 | 1.939% | 0.2655%
2017-10-12 | 6 | 6516 | 123.6387 | 1.897% | 16.9271 | 0.2598% | 140.5658 | 2.157% | 793 | 6499.0729 | 6375.4342 | 1.939% | 0.2655%
2017-11-04 | 17 | 6516 | 123.6387 | 1.897% | 16.9271 | 0.2598% | 140.5658 | 2.157% | 794 | 6499.0729 | 6375.4342 | 1.939% | 0.2655%
2017-11-29 | 5 | 6516 | 123.6387 | 1.897% | 16.9271 | 0.2598% | 140.5658 | 2.157% | 795 | 6499.0729 | 6375.4342 | 1.939% | 0.2655%
2017-11-29 | 15 | 6516 | 123.6387 | 1.897% | 16.9271 | 0.2598% | 140.5658 | 2.157% | 796 | 6499.0729 | 6375.4342 | 1.939% | 0.2655%
2017-11-18 | 21 | 6517 | 123.6509 | 1.897% | 16.9284 | 0.2598% | 140.5794 | 2.157% | 797 | 6500.0716 | 6376.4206 | 1.939% | 0.2655%
2017-10-24 | 8 | 6521 | 123.7 | 1.897% | 16.9336 | 0.2597% | 140.6337 | 2.157% | 798 | 6504.0664 | 6380.3663 | 1.939% | 0.2654%
2017-10-29 | 22 | 6525 | 123.7491 | 1.897% | 16.9388 | 0.2596% | 140.688 | 2.156% | 799 | 6508.0612 | 6384.312 | 1.938% | 0.2653%
2017-11-03 | 9 | 6528 | 123.786 | 1.896% | 16.9427 | 0.2595% | 140.7287 | 2.156% | 800 | 6511.0573 | 6387.2713 | 1.938% | 0.2653%
2017-11-06 | 9 | 6531 | 123.8228 | 1.896% | 16.9467 | 0.2595% | 140.7694 | 2.155% | 801 | 6514.0533 | 6390.2306 | 1.938% | 0.2652%
2017-10-28 | 20 | 6532 | 123.8351 | 1.896% | 16.948 | 0.2595% | 140.783 | 2.155% | 802 | 6515.052 | 6391.217 | 1.938% | 0.2652%
2017-11-16 | 14 | 6532 | 123.8351 | 1.896% | 16.948 | 0.2595% | 140.783 | 2.155% | 803 | 6515.052 | 6391.217 | 1.938% | 0.2652%
2017-09-20 | 7 | 6533 | 123.8473 | 1.896% | 16.9493 | 0.2594% | 140.7966 | 2.155% | 804 | 6516.0507 | 6392.2034 | 1.937% | 0.2652%
2017-11-04 | 18 | 6533 | 123.8473 | 1.896% | 16.9493 | 0.2594% | 140.7966 | 2.155% | 805 | 6516.0507 | 6392.2034 | 1.937% | 0.2652%
2017-11-29 | 16 | 6533 | 123.8473 | 1.896% | 16.9493 | 0.2594% | 140.7966 | 2.155% | 806 | 6516.0507 | 6392.2034 | 1.937% | 0.2652%
2017-10-20 | 12 | 6534 | 123.8596 | 1.896% | 16.9506 | 0.2594% | 140.8102 | 2.155% | 807 | 6517.0494 | 6393.1898 | 1.937% | 0.2651%
2017-11-17 | 15 | 6535 | 123.8719 | 1.896% | 16.9519 | 0.2594% | 140.8237 | 2.155% | 808 | 6518.0481 | 6394.1763 | 1.937% | 0.2651%
2017-10-16 | 22 | 6539 | 123.921 | 1.895% | 16.9571 | 0.2593% | 140.878 | 2.154% | 809 | 6522.0429 | 6398.122 | 1.937% | 0.265%
2017-11-13 | 24 | 6539 | 123.921 | 1.895% | 16.9571 | 0.2593% | 140.878 | 2.154% | 810 | 6522.0429 | 6398.122 | 1.937% | 0.265%
2017-09-11 | 10 | 6540 | 123.9333 | 1.895% | 16.9584 | 0.2593% | 140.8916 | 2.154% | 811 | 6523.0416 | 6399.1084 | 1.937% | 0.265%
2017-10-22 | 14 | 6540 | 123.9333 | 1.895% | 16.9584 | 0.2593% | 140.8916 | 2.154% | 812 | 6523.0416 | 6399.1084 | 1.937% | 0.265%
2017-10-23 | 8 | 6542 | 123.9578 | 1.895% | 16.961 | 0.2593% | 140.9188 | 2.154% | 813 | 6525.039 | 6401.0812 | 1.937% | 0.265%
2017-11-05 | 21 | 6542 | 123.9578 | 1.895% | 16.961 | 0.2593% | 140.9188 | 2.154% | 814 | 6525.039 | 6401.0812 | 1.937% | 0.265%
2017-11-29 | 14 | 6547 | 124.0192 | 1.894% | 16.9675 | 0.2592% | 140.9867 | 2.153% | 815 | 6530.0325 | 6406.0133 | 1.936% | 0.2649%
2017-11-04 | 21 | 6548 | 124.0315 | 1.894% | 16.9688 | 0.2591% | 141.0002 | 2.153% | 816 | 6531.0312 | 6406.9998 | 1.936% | 0.2648%
2017-09-22 | 7 | 6551 | 124.0683 | 1.894% | 16.9727 | 0.2591% | 141.041 | 2.153% | 817 | 6534.0273 | 6409.959 | 1.936% | 0.2648%
2017-11-30 | 16 | 6552 | 124.0806 | 1.894% | 16.974 | 0.2591% | 141.0545 | 2.153% | 818 | 6535.026 | 6410.9455 | 1.935% | 0.2648%
2017-10-25 | 9 | 6554 | 124.1051 | 1.894% | 16.9766 | 0.259% | 141.0817 | 2.153% | 819 | 6537.0234 | 6412.9183 | 1.935% | 0.2647%
2017-11-22 | 7 | 6554 | 124.1051 | 1.894% | 16.9766 | 0.259% | 141.0817 | 2.153% | 820 | 6537.0234 | 6412.9183 | 1.935% | 0.2647%
2017-10-17 | 9 | 6556 | 124.1297 | 1.893% | 16.9792 | 0.259% | 141.1088 | 2.152% | 821 | 6539.0208 | 6414.8912 | 1.935% | 0.2647%
2017-11-07 | 9 | 6556 | 124.1297 | 1.893% | 16.9792 | 0.259% | 141.1088 | 2.152% | 822 | 6539.0208 | 6414.8912 | 1.935% | 0.2647%
2017-11-10 | 17 | 6557 | 124.1419 | 1.893% | 16.9805 | 0.259% | 141.1224 | 2.152% | 823 | 6540.0195 | 6415.8776 | 1.935% | 0.2647%
2017-11-22 | 16 | 6557 | 124.1419 | 1.893% | 16.9805 | 0.259% | 141.1224 | 2.152% | 824 | 6540.0195 | 6415.8776 | 1.935% | 0.2647%
2017-10-31 | 18 | 6561 | 124.191 | 1.893% | 16.9857 | 0.2589% | 141.1767 | 2.152% | 825 | 6544.0143 | 6419.8233 | 1.934% | 0.2646%
2017-10-04 | 10 | 6562 | 124.2033 | 1.893% | 16.987 | 0.2589% | 141.1903 | 2.152% | 826 | 6545.013 | 6420.8097 | 1.934% | 0.2646%
2017-11-30 | 15 | 6563 | 124.2156 | 1.893% | 16.9883 | 0.2588% | 141.2039 | 2.152% | 827 | 6546.0117 | 6421.7961 | 1.934% | 0.2645%
2017-10-25 | 18 | 6564 | 124.2279 | 1.893% | 16.9896 | 0.2588% | 141.2174 | 2.151% | 828 | 6547.0104 | 6422.7826 | 1.934% | 0.2645%
2017-09-10 | 17 | 6573 | 124.3383 | 1.892% | 17.0013 | 0.2587% | 141.3396 | 2.15% | 829 | 6555.9987 | 6431.6604 | 1.933% | 0.2643%
2017-09-17 | 24 | 6573 | 124.3383 | 1.892% | 17.0013 | 0.2587% | 141.3396 | 2.15% | 830 | 6555.9987 | 6431.6604 | 1.933% | 0.2643%
2017-11-10 | 13 | 6573 | 124.3383 | 1.892% | 17.0013 | 0.2587% | 141.3396 | 2.15% | 831 | 6555.9987 | 6431.6604 | 1.933% | 0.2643%
2017-11-22 | 24 | 6574 | 124.3506 | 1.892% | 17.0026 | 0.2586% | 141.3532 | 2.15% | 832 | 6556.9974 | 6432.6468 | 1.933% | 0.2643%
2017-10-13 | 23 | 6575 | 124.3629 | 1.891% | 17.0039 | 0.2586% | 141.3668 | 2.15% | 833 | 6557.9961 | 6433.6332 | 1.933% | 0.2643%
2017-10-18 | 22 | 6575 | 124.3629 | 1.891% | 17.0039 | 0.2586% | 141.3668 | 2.15% | 834 | 6557.9961 | 6433.6332 | 1.933% | 0.2643%
2017-10-30 | 15 | 6575 | 124.3629 | 1.891% | 17.0039 | 0.2586% | 141.3668 | 2.15% | 835 | 6557.9961 | 6433.6332 | 1.933% | 0.2643%
2017-10-31 | 17 | 6577 | 124.3874 | 1.891% | 17.0065 | 0.2586% | 141.3939 | 2.15% | 836 | 6559.9935 | 6435.6061 | 1.933% | 0.2643%
2017-11-12 | 15 | 6578 | 124.3997 | 1.891% | 17.0078 | 0.2586% | 141.4075 | 2.15% | 837 | 6560.9922 | 6436.5925 | 1.933% | 0.2642%
2017-10-10 | 5 | 6579 | 124.412 | 1.891% | 17.0091 | 0.2585% | 141.4211 | 2.15% | 838 | 6561.9909 | 6437.5789 | 1.933% | 0.2642%
2017-10-14 | 13 | 6579 | 124.412 | 1.891% | 17.0091 | 0.2585% | 141.4211 | 2.15% | 839 | 6561.9909 | 6437.5789 | 1.933% | 0.2642%
2017-10-18 | 17 | 6579 | 124.412 | 1.891% | 17.0091 | 0.2585% | 141.4211 | 2.15% | 840 | 6561.9909 | 6437.5789 | 1.933% | 0.2642%
2017-10-26 | 12 | 6579 | 124.412 | 1.891% | 17.0091 | 0.2585% | 141.4211 | 2.15% | 841 | 6561.9909 | 6437.5789 | 1.933% | 0.2642%
2017-09-10 | 19 | 6582 | 124.4488 | 1.891% | 17.013 | 0.2585% | 141.4618 | 2.149% | 842 | 6564.987 | 6440.5382 | 1.932% | 0.2642%
2017-09-03 | 10 | 6583 | 124.4611 | 1.891% | 17.0143 | 0.2585% | 141.4754 | 2.149% | 843 | 6565.9857 | 6441.5246 | 1.932% | 0.2641%
2017-10-30 | 17 | 6585 | 124.4856 | 1.89% | 17.0169 | 0.2584% | 141.5025 | 2.149% | 844 | 6567.9831 | 6443.4975 | 1.932% | 0.2641%
2017-09-21 | 1 | 6586 | 124.4979 | 1.89% | 17.0182 | 0.2584% | 141.5161 | 2.149% | 845 | 6568.9818 | 6444.4839 | 1.932% | 0.2641%
2017-10-01 | 17 | 6586 | 124.4979 | 1.89% | 17.0182 | 0.2584% | 141.5161 | 2.149% | 846 | 6568.9818 | 6444.4839 | 1.932% | 0.2641%
2017-11-22 | 15 | 6586 | 124.4979 | 1.89% | 17.0182 | 0.2584% | 141.5161 | 2.149% | 847 | 6568.9818 | 6444.4839 | 1.932% | 0.2641%
2017-10-17 | 8 | 6588 | 124.5225 | 1.89% | 17.0208 | 0.2584% | 141.5433 | 2.149% | 848 | 6570.9792 | 6446.4567 | 1.932% | 0.264%
2017-10-24 | 10 | 6588 | 124.5225 | 1.89% | 17.0208 | 0.2584% | 141.5433 | 2.149% | 849 | 6570.9792 | 6446.4567 | 1.932% | 0.264%
2017-10-31 | 13 | 6589 | 124.5347 | 1.89% | 17.0221 | 0.2583% | 141.5568 | 2.148% | 850 | 6571.9779 | 6447.4432 | 1.932% | 0.264%
2017-11-25 | 22 | 6590 | 124.547 | 1.89% | 17.0234 | 0.2583% | 141.5704 | 2.148% | 851 | 6572.9766 | 6448.4296 | 1.931% | 0.264%
2017-10-20 | 11 | 6592 | 124.5716 | 1.89% | 17.026 | 0.2583% | 141.5976 | 2.148% | 852 | 6574.974 | 6450.4024 | 1.931% | 0.264%
2017-11-03 | 8 | 6593 | 124.5838 | 1.89% | 17.0273 | 0.2583% | 141.6112 | 2.148% | 853 | 6575.9727 | 6451.3888 | 1.931% | 0.2639%
2017-11-23 | 15 | 6594 | 124.5961 | 1.89% | 17.0286 | 0.2582% | 141.6247 | 2.148% | 854 | 6576.9714 | 6452.3753 | 1.931% | 0.2639%
2017-11-29 | 13 | 6597 | 124.6329 | 1.889% | 17.0325 | 0.2582% | 141.6655 | 2.147% | 855 | 6579.9675 | 6455.3345 | 1.931% | 0.2639%
2017-10-08 | 1 | 6598 | 124.6452 | 1.889% | 17.0338 | 0.2582% | 141.679 | 2.147% | 856 | 6580.9662 | 6456.321 | 1.931% | 0.2638%
2017-11-03 | 22 | 6598 | 124.6452 | 1.889% | 17.0338 | 0.2582% | 141.679 | 2.147% | 857 | 6580.9662 | 6456.321 | 1.931% | 0.2638%
2017-11-14 | 5 | 6599 | 124.6575 | 1.889% | 17.0351 | 0.2581% | 141.6926 | 2.147% | 858 | 6581.9649 | 6457.3074 | 1.93% | 0.2638%
2017-10-20 | 13 | 6601 | 124.682 | 1.889% | 17.0377 | 0.2581% | 141.7198 | 2.147% | 859 | 6583.9623 | 6459.2802 | 1.93% | 0.2638%
2017-11-26 | 11 | 6602 | 124.6943 | 1.889% | 17.039 | 0.2581% | 141.7333 | 2.147% | 860 | 6584.961 | 6460.2667 | 1.93% | 0.2638%
2017-09-10 | 18 | 6606 | 124.7434 | 1.888% | 17.0442 | 0.258% | 141.7876 | 2.146% | 861 | 6588.9558 | 6464.2124 | 1.93% | 0.2637%
2017-09-30 | 11 | 6607 | 124.7557 | 1.888% | 17.0455 | 0.258% | 141.8012 | 2.146% | 862 | 6589.9545 | 6465.1988 | 1.93% | 0.2637%
2017-11-21 | 23 | 6607 | 124.7557 | 1.888% | 17.0455 | 0.258% | 141.8012 | 2.146% | 863 | 6589.9545 | 6465.1988 | 1.93% | 0.2637%
2017-10-25 | 8 | 6608 | 124.768 | 1.888% | 17.0468 | 0.258% | 141.8148 | 2.146% | 864 | 6590.9532 | 6466.1852 | 1.93% | 0.2636%
2017-11-02 | 9 | 6608 | 124.768 | 1.888% | 17.0468 | 0.258% | 141.8148 | 2.146% | 865 | 6590.9532 | 6466.1852 | 1.93% | 0.2636%
2017-09-29 | 7 | 6609 | 124.7802 | 1.888% | 17.0481 | 0.258% | 141.8284 | 2.146% | 866 | 6591.9519 | 6467.1716 | 1.929% | 0.2636%
2017-10-09 | 1 | 6609 | 124.7802 | 1.888% | 17.0481 | 0.258% | 141.8284 | 2.146% | 867 | 6591.9519 | 6467.1716 | 1.929% | 0.2636%
2017-11-01 | 13 | 6612 | 124.8171 | 1.888% | 17.052 | 0.2579% | 141.8691 | 2.146% | 868 | 6594.948 | 6470.1309 | 1.929% | 0.2635%
2017-10-05 | 9 | 6613 | 124.8293 | 1.888% | 17.0533 | 0.2579% | 141.8827 | 2.146% | 869 | 6595.9467 | 6471.1173 | 1.929% | 0.2635%
2017-10-18 | 18 | 6613 | 124.8293 | 1.888% | 17.0533 | 0.2579% | 141.8827 | 2.146% | 870 | 6595.9467 | 6471.1173 | 1.929% | 0.2635%
2017-11-03 | 10 | 6615 | 124.8539 | 1.887% | 17.0559 | 0.2578% | 141.9098 | 2.145% | 871 | 6597.9441 | 6473.0902 | 1.929% | 0.2635%
2017-09-08 | 10 | 6616 | 124.8662 | 1.887% | 17.0572 | 0.2578% | 141.9234 | 2.145% | 872 | 6598.9428 | 6474.0766 | 1.929% | 0.2635%
2017-11-16 | 3 | 6617 | 124.8784 | 1.887% | 17.0585 | 0.2578% | 141.937 | 2.145% | 873 | 6599.9415 | 6475.063 | 1.929% | 0.2634%
2017-11-12 | 16 | 6618 | 124.8907 | 1.887% | 17.0598 | 0.2578% | 141.9506 | 2.145% | 874 | 6600.9402 | 6476.0494 | 1.929% | 0.2634%
2017-11-17 | 4 | 6621 | 124.9275 | 1.887% | 17.0637 | 0.2577% | 141.9913 | 2.145% | 875 | 6603.9363 | 6479.0087 | 1.928% | 0.2634%
2017-11-17 | 14 | 6621 | 124.9275 | 1.887% | 17.0637 | 0.2577% | 141.9913 | 2.145% | 876 | 6603.9363 | 6479.0087 | 1.928% | 0.2634%
2017-10-06 | 9 | 6622 | 124.9398 | 1.887% | 17.065 | 0.2577% | 142.0049 | 2.144% | 877 | 6604.935 | 6479.9951 | 1.928% | 0.2633%
2017-11-06 | 10 | 6622 | 124.9398 | 1.887% | 17.065 | 0.2577% | 142.0049 | 2.144% | 878 | 6604.935 | 6479.9951 | 1.928% | 0.2633%
2017-09-07 | 23 | 6626 | 124.9889 | 1.886% | 17.0702 | 0.2576% | 142.0592 | 2.144% | 879 | 6608.9298 | 6483.9408 | 1.928% | 0.2633%
2017-10-27 | 20 | 6626 | 124.9889 | 1.886% | 17.0702 | 0.2576% | 142.0592 | 2.144% | 880 | 6608.9298 | 6483.9408 | 1.928% | 0.2633%
2017-11-30 | 23 | 6627 | 125.0012 | 1.886% | 17.0715 | 0.2576% | 142.0727 | 2.144% | 881 | 6609.9285 | 6484.9273 | 1.928% | 0.2632%
2017-10-29 | 19 | 6628 | 125.0135 | 1.886% | 17.0728 | 0.2576% | 142.0863 | 2.144% | 882 | 6610.9272 | 6485.9137 | 1.927% | 0.2632%
2017-10-17 | 22 | 6629 | 125.0258 | 1.886% | 17.0741 | 0.2576% | 142.0999 | 2.144% | 883 | 6611.9259 | 6486.9001 | 1.927% | 0.2632%
2017-11-16 | 2 | 6631 | 125.0503 | 1.886% | 17.0767 | 0.2575% | 142.127 | 2.143% | 884 | 6613.9233 | 6488.873 | 1.927% | 0.2632%
2017-10-10 | 3 | 6633 | 125.0749 | 1.886% | 17.0793 | 0.2575% | 142.1542 | 2.143% | 885 | 6615.9207 | 6490.8458 | 1.927% | 0.2631%
2017-10-22 | 22 | 6633 | 125.0749 | 1.886% | 17.0793 | 0.2575% | 142.1542 | 2.143% | 886 | 6615.9207 | 6490.8458 | 1.927% | 0.2631%
2017-11-16 | 17 | 6633 | 125.0749 | 1.886% | 17.0793 | 0.2575% | 142.1542 | 2.143% | 887 | 6615.9207 | 6490.8458 | 1.927% | 0.2631%
2017-11-28 | 24 | 6634 | 125.0871 | 1.886% | 17.0806 | 0.2575% | 142.1678 | 2.143% | 888 | 6616.9194 | 6491.8322 | 1.927% | 0.2631%
2017-11-02 | 10 | 6635 | 125.0994 | 1.885% | 17.0819 | 0.2575% | 142.1813 | 2.143% | 889 | 6617.9181 | 6492.8187 | 1.927% | 0.2631%
2017-10-15 | 12 | 6637 | 125.124 | 1.885% | 17.0845 | 0.2574% | 142.2085 | 2.143% | 890 | 6619.9155 | 6494.7915 | 1.927% | 0.263%
2017-10-23 | 9 | 6640 | 125.1608 | 1.885% | 17.0885 | 0.2574% | 142.2492 | 2.142% | 891 | 6622.9115 | 6497.7508 | 1.926% | 0.263%
2017-10-01 | 19 | 6642 | 125.1853 | 1.885% | 17.0911 | 0.2573% | 142.2764 | 2.142% | 892 | 6624.9089 | 6499.7236 | 1.926% | 0.263%
2017-11-26 | 7 | 6642 | 125.1853 | 1.885% | 17.0911 | 0.2573% | 142.2764 | 2.142% | 893 | 6624.9089 | 6499.7236 | 1.926% | 0.263%
2017-10-31 | 22 | 6643 | 125.1976 | 1.885% | 17.0924 | 0.2573% | 142.29 | 2.142% | 894 | 6625.9076 | 6500.71 | 1.926% | 0.2629%
2017-11-30 | 14 | 6643 | 125.1976 | 1.885% | 17.0924 | 0.2573% | 142.29 | 2.142% | 895 | 6625.9076 | 6500.71 | 1.926% | 0.2629%
2017-09-15 | 7 | 6645 | 125.2222 | 1.884% | 17.095 | 0.2573% | 142.3171 | 2.142% | 896 | 6627.905 | 6502.6829 | 1.926% | 0.2629%
2017-11-01 | 14 | 6646 | 125.2344 | 1.884% | 17.0963 | 0.2572% | 142.3307 | 2.142% | 897 | 6628.9037 | 6503.6693 | 1.926% | 0.2629%
2017-09-28 | 1 | 6647 | 125.2467 | 1.884% | 17.0976 | 0.2572% | 142.3443 | 2.141% | 898 | 6629.9024 | 6504.6557 | 1.925% | 0.2629%
2017-11-22 | 17 | 6647 | 125.2467 | 1.884% | 17.0976 | 0.2572% | 142.3443 | 2.141% | 899 | 6629.9024 | 6504.6557 | 1.925% | 0.2629%
2017-10-09 | 6 | 6648 | 125.259 | 1.884% | 17.0989 | 0.2572% | 142.3578 | 2.141% | 900 | 6630.9011 | 6505.6422 | 1.925% | 0.2628%
2017-10-04 | 11 | 6650 | 125.2835 | 1.884% | 17.1015 | 0.2572% | 142.385 | 2.141% | 901 | 6632.8985 | 6507.615 | 1.925% | 0.2628%
2017-09-23 | 24 | 6651 | 125.2958 | 1.884% | 17.1028 | 0.2571% | 142.3986 | 2.141% | 902 | 6633.8972 | 6508.6014 | 1.925% | 0.2628%
2017-11-24 | 13 | 6652 | 125.3081 | 1.884% | 17.1041 | 0.2571% | 142.4121 | 2.141% | 903 | 6634.8959 | 6509.5879 | 1.925% | 0.2628%
2017-10-20 | 10 | 6653 | 125.3204 | 1.884% | 17.1054 | 0.2571% | 142.4257 | 2.141% | 904 | 6635.8946 | 6510.5743 | 1.925% | 0.2627%
2017-10-27 | 12 | 6653 | 125.3204 | 1.884% | 17.1054 | 0.2571% | 142.4257 | 2.141% | 905 | 6635.8946 | 6510.5743 | 1.925% | 0.2627%
2017-10-02 | 11 | 6656 | 125.3572 | 1.883% | 17.1093 | 0.2571% | 142.4664 | 2.14% | 906 | 6638.8907 | 6513.5336 | 1.925% | 0.2627%
2017-11-16 | 24 | 6656 | 125.3572 | 1.883% | 17.1093 | 0.2571% | 142.4664 | 2.14% | 907 | 6638.8907 | 6513.5336 | 1.925% | 0.2627%
2017-11-22 | 13 | 6657 | 125.3695 | 1.883% | 17.1106 | 0.257% | 142.48 | 2.14% | 908 | 6639.8894 | 6514.52 | 1.924% | 0.2627%
2017-11-03 | 11 | 6658 | 125.3817 | 1.883% | 17.1119 | 0.257% | 142.4936 | 2.14% | 909 | 6640.8881 | 6515.5064 | 1.924% | 0.2626%
2017-10-19 | 13 | 6659 | 125.394 | 1.883% | 17.1132 | 0.257% | 142.5072 | 2.14% | 910 | 6641.8868 | 6516.4928 | 1.924% | 0.2626%
2017-10-18 | 11 | 6660 | 125.4063 | 1.883% | 17.1145 | 0.257% | 142.5208 | 2.14% | 911 | 6642.8855 | 6517.4792 | 1.924% | 0.2626%
2017-10-19 | 22 | 6660 | 125.4063 | 1.883% | 17.1145 | 0.257% | 142.5208 | 2.14% | 912 | 6642.8855 | 6517.4792 | 1.924% | 0.2626%
2017-10-21 | 19 | 6660 | 125.4063 | 1.883% | 17.1145 | 0.257% | 142.5208 | 2.14% | 913 | 6642.8855 | 6517.4792 | 1.924% | 0.2626%
2017-11-18 | 20 | 6660 | 125.4063 | 1.883% | 17.1145 | 0.257% | 142.5208 | 2.14% | 914 | 6642.8855 | 6517.4792 | 1.924% | 0.2626%
2017-10-03 | 11 | 6661 | 125.4186 | 1.883% | 17.1158 | 0.257% | 142.5343 | 2.14% | 915 | 6643.8842 | 6518.4657 | 1.924% | 0.2626%
2017-11-13 | 15 | 6662 | 125.4308 | 1.883% | 17.1171 | 0.2569% | 142.5479 | 2.14% | 916 | 6644.8829 | 6519.4521 | 1.924% | 0.2626%
2017-11-28 | 16 | 6664 | 125.4554 | 1.883% | 17.1197 | 0.2569% | 142.5751 | 2.139% | 917 | 6646.8803 | 6521.4249 | 1.924% | 0.2625%
2017-11-16 | 13 | 6665 | 125.4677 | 1.882% | 17.121 | 0.2569% | 142.5886 | 2.139% | 918 | 6647.879 | 6522.4114 | 1.924% | 0.2625%
2017-11-22 | 14 | 6665 | 125.4677 | 1.882% | 17.121 | 0.2569% | 142.5886 | 2.139% | 919 | 6647.879 | 6522.4114 | 1.924% | 0.2625%
2017-10-19 | 7 | 6666 | 125.4799 | 1.882% | 17.1223 | 0.2569% | 142.6022 | 2.139% | 920 | 6648.8777 | 6523.3978 | 1.924% | 0.2625%
2017-10-19 | 12 | 6666 | 125.4799 | 1.882% | 17.1223 | 0.2569% | 142.6022 | 2.139% | 921 | 6648.8777 | 6523.3978 | 1.924% | 0.2625%
2017-10-31 | 19 | 6668 | 125.5045 | 1.882% | 17.1249 | 0.2568% | 142.6294 | 2.139% | 922 | 6650.8751 | 6525.3706 | 1.923% | 0.2624%
2017-11-29 | 17 | 6669 | 125.5168 | 1.882% | 17.1262 | 0.2568% | 142.6429 | 2.139% | 923 | 6651.8738 | 6526.3571 | 1.923% | 0.2624%
2017-11-28 | 15 | 6670 | 125.529 | 1.882% | 17.1275 | 0.2568% | 142.6565 | 2.139% | 924 | 6652.8725 | 6527.3435 | 1.923% | 0.2624%
2017-09-27 | 1 | 6671 | 125.5413 | 1.882% | 17.1288 | 0.2568% | 142.6701 | 2.139% | 925 | 6653.8712 | 6528.3299 | 1.923% | 0.2624%
2017-10-01 | 18 | 6672 | 125.5536 | 1.882% | 17.1301 | 0.2567% | 142.6837 | 2.139% | 926 | 6654.8699 | 6529.3163 | 1.923% | 0.2624%
2017-11-13 | 6 | 6672 | 125.5536 | 1.882% | 17.1301 | 0.2567% | 142.6837 | 2.139% | 927 | 6654.8699 | 6529.3163 | 1.923% | 0.2624%
2017-09-19 | 7 | 6673 | 125.5659 | 1.882% | 17.1314 | 0.2567% | 142.6972 | 2.138% | 928 | 6655.8686 | 6530.3028 | 1.923% | 0.2623%
2017-10-21 | 18 | 6674 | 125.5781 | 1.882% | 17.1327 | 0.2567% | 142.7108 | 2.138% | 929 | 6656.8673 | 6531.2892 | 1.923% | 0.2623%
2017-11-09 | 23 | 6674 | 125.5781 | 1.882% | 17.1327 | 0.2567% | 142.7108 | 2.138% | 930 | 6656.8673 | 6531.2892 | 1.923% | 0.2623%
2017-10-13 | 7 | 6675 | 125.5904 | 1.882% | 17.134 | 0.2567% | 142.7244 | 2.138% | 931 | 6657.866 | 6532.2756 | 1.923% | 0.2623%
2017-09-13 | 8 | 6676 | 125.6027 | 1.881% | 17.1353 | 0.2567% | 142.738 | 2.138% | 932 | 6658.8647 | 6533.262 | 1.923% | 0.2623%
2017-09-01 | 1 | 6677 | 125.615 | 1.881% | 17.1366 | 0.2567% | 142.7515 | 2.138% | 933 | 6659.8634 | 6534.2485 | 1.922% | 0.2623%
2017-10-21 | 16 | 6677 | 125.615 | 1.881% | 17.1366 | 0.2567% | 142.7515 | 2.138% | 934 | 6659.8634 | 6534.2485 | 1.922% | 0.2623%
2017-11-01 | 15 | 6678 | 125.6272 | 1.881% | 17.1379 | 0.2566% | 142.7651 | 2.138% | 935 | 6660.8621 | 6535.2349 | 1.922% | 0.2622%
2017-11-20 | 1 | 6678 | 125.6272 | 1.881% | 17.1379 | 0.2566% | 142.7651 | 2.138% | 936 | 6660.8621 | 6535.2349 | 1.922% | 0.2622%
2017-11-27 | 15 | 6678 | 125.6272 | 1.881% | 17.1379 | 0.2566% | 142.7651 | 2.138% | 937 | 6660.8621 | 6535.2349 | 1.922% | 0.2622%
2017-11-11 | 16 | 6679 | 125.6395 | 1.881% | 17.1392 | 0.2566% | 142.7787 | 2.138% | 938 | 6661.8608 | 6536.2213 | 1.922% | 0.2622%
2017-11-12 | 14 | 6679 | 125.6395 | 1.881% | 17.1392 | 0.2566% | 142.7787 | 2.138% | 939 | 6661.8608 | 6536.2213 | 1.922% | 0.2622%
2017-09-07 | 10 | 6684 | 125.7009 | 1.881% | 17.1457 | 0.2565% | 142.8466 | 2.137% | 940 | 6666.8543 | 6541.1534 | 1.922% | 0.2621%
2017-11-25 | 18 | 6685 | 125.7132 | 1.881% | 17.147 | 0.2565% | 142.8602 | 2.137% | 941 | 6667.853 | 6542.1398 | 1.922% | 0.2621%
2017-09-18 | 7 | 6689 | 125.7623 | 1.88% | 17.1522 | 0.2564% | 142.9145 | 2.137% | 942 | 6671.8478 | 6546.0855 | 1.921% | 0.262%
2017-11-04 | 19 | 6689 | 125.7623 | 1.88% | 17.1522 | 0.2564% | 142.9145 | 2.137% | 943 | 6671.8478 | 6546.0855 | 1.921% | 0.262%
2017-11-15 | 15 | 6690 | 125.7745 | 1.88% | 17.1535 | 0.2564% | 142.928 | 2.136% | 944 | 6672.8465 | 6547.072 | 1.921% | 0.262%
2017-09-12 | 8 | 6692 | 125.7991 | 1.88% | 17.1561 | 0.2564% | 142.9552 | 2.136% | 945 | 6674.8439 | 6549.0448 | 1.921% | 0.262%
2017-10-20 | 8 | 6693 | 125.8114 | 1.88% | 17.1574 | 0.2563% | 142.9688 | 2.136% | 946 | 6675.8426 | 6550.0312 | 1.921% | 0.2619%
2017-11-08 | 7 | 6693 | 125.8114 | 1.88% | 17.1574 | 0.2563% | 142.9688 | 2.136% | 947 | 6675.8426 | 6550.0312 | 1.921% | 0.2619%
2017-11-27 | 16 | 6693 | 125.8114 | 1.88% | 17.1574 | 0.2563% | 142.9688 | 2.136% | 948 | 6675.8426 | 6550.0312 | 1.921% | 0.2619%
2017-11-30 | 17 | 6694 | 125.8236 | 1.88% | 17.1587 | 0.2563% | 142.9823 | 2.136% | 949 | 6676.8413 | 6551.0177 | 1.921% | 0.2619%
2017-11-02 | 8 | 6695 | 125.8359 | 1.88% | 17.16 | 0.2563% | 142.9959 | 2.136% | 950 | 6677.84 | 6552.0041 | 1.921% | 0.2619%
2017-10-17 | 19 | 6696 | 125.8482 | 1.879% | 17.1613 | 0.2563% | 143.0095 | 2.136% | 951 | 6678.8387 | 6552.9905 | 1.92% | 0.2619%
2017-09-06 | 1 | 6697 | 125.8605 | 1.879% | 17.1626 | 0.2563% | 143.0231 | 2.136% | 952 | 6679.8374 | 6553.9769 | 1.92% | 0.2619%
2017-10-25 | 22 | 6697 | 125.8605 | 1.879% | 17.1626 | 0.2563% | 143.0231 | 2.136% | 953 | 6679.8374 | 6553.9769 | 1.92% | 0.2619%
2017-11-13 | 16 | 6697 | 125.8605 | 1.879% | 17.1626 | 0.2563% | 143.0231 | 2.136% | 954 | 6679.8374 | 6553.9769 | 1.92% | 0.2619%
2017-11-25 | 12 | 6697 | 125.8605 | 1.879% | 17.1626 | 0.2563% | 143.0231 | 2.136% | 955 | 6679.8374 | 6553.9769 | 1.92% | 0.2619%
2017-10-20 | 21 | 6698 | 125.8727 | 1.879% | 17.1639 | 0.2563% | 143.0366 | 2.136% | 956 | 6680.8361 | 6554.9634 | 1.92% | 0.2618%
2017-11-18 | 12 | 6698 | 125.8727 | 1.879% | 17.1639 | 0.2563% | 143.0366 | 2.136% | 957 | 6680.8361 | 6554.9634 | 1.92% | 0.2618%
2017-11-29 | 12 | 6698 | 125.8727 | 1.879% | 17.1639 | 0.2563% | 143.0366 | 2.136% | 958 | 6680.8361 | 6554.9634 | 1.92% | 0.2618%
2017-11-01 | 22 | 6699 | 125.885 | 1.879% | 17.1652 | 0.2562% | 143.0502 | 2.135% | 959 | 6681.8348 | 6555.9498 | 1.92% | 0.2618%
2017-09-24 | 10 | 6700 | 125.8973 | 1.879% | 17.1665 | 0.2562% | 143.0638 | 2.135% | 960 | 6682.8335 | 6556.9362 | 1.92% | 0.2618%
2017-11-18 | 18 | 6701 | 125.9096 | 1.879% | 17.1678 | 0.2562% | 143.0774 | 2.135% | 961 | 6683.8322 | 6557.9226 | 1.92% | 0.2618%
2017-10-14 | 14 | 6702 | 125.9218 | 1.879% | 17.1691 | 0.2562% | 143.0909 | 2.135% | 962 | 6684.8309 | 6558.9091 | 1.92% | 0.2618%
2017-11-07 | 10 | 6702 | 125.9218 | 1.879% | 17.1691 | 0.2562% | 143.0909 | 2.135% | 963 | 6684.8309 | 6558.9091 | 1.92% | 0.2618%
2017-09-11 | 11 | 6707 | 125.9832 | 1.878% | 17.1756 | 0.2561% | 143.1588 | 2.134% | 964 | 6689.8244 | 6563.8412 | 1.919% | 0.2617%
2017-10-21 | 20 | 6708 | 125.9955 | 1.878% | 17.1769 | 0.2561% | 143.1724 | 2.134% | 965 | 6690.8231 | 6564.8276 | 1.919% | 0.2617%
2017-09-09 | 12 | 6711 | 126.0323 | 1.878% | 17.1808 | 0.256% | 143.2131 | 2.134% | 966 | 6693.8192 | 6567.7869 | 1.919% | 0.2616%
2017-10-20 | 9 | 6711 | 126.0323 | 1.878% | 17.1808 | 0.256% | 143.2131 | 2.134% | 967 | 6693.8192 | 6567.7869 | 1.919% | 0.2616%
2017-10-20 | 14 | 6711 | 126.0323 | 1.878% | 17.1808 | 0.256% | 143.2131 | 2.134% | 968 | 6693.8192 | 6567.7869 | 1.919% | 0.2616%
2017-11-17 | 17 | 6712 | 126.0446 | 1.878% | 17.1821 | 0.256% | 143.2267 | 2.134% | 969 | 6694.8179 | 6568.7733 | 1.919% | 0.2616%
2017-10-04 | 23 | 6714 | 126.0691 | 1.878% | 17.1847 | 0.256% | 143.2539 | 2.134% | 970 | 6696.8153 | 6570.7461 | 1.919% | 0.2615%
2017-11-06 | 22 | 6714 | 126.0691 | 1.878% | 17.1847 | 0.256% | 143.2539 | 2.134% | 971 | 6696.8153 | 6570.7461 | 1.919% | 0.2615%
2017-09-16 | 24 | 6715 | 126.0814 | 1.878% | 17.186 | 0.2559% | 143.2674 | 2.134% | 972 | 6697.814 | 6571.7326 | 1.919% | 0.2615%
2017-11-30 | 13 | 6715 | 126.0814 | 1.878% | 17.186 | 0.2559% | 143.2674 | 2.134% | 973 | 6697.814 | 6571.7326 | 1.919% | 0.2615%
2017-11-01 | 12 | 6717 | 126.106 | 1.877% | 17.1886 | 0.2559% | 143.2946 | 2.133% | 974 | 6699.8114 | 6573.7054 | 1.918% | 0.2615%
2017-11-02 | 11 | 6718 | 126.1182 | 1.877% | 17.1899 | 0.2559% | 143.3082 | 2.133% | 975 | 6700.8101 | 6574.6918 | 1.918% | 0.2615%
2017-11-11 | 15 | 6719 | 126.1305 | 1.877% | 17.1912 | 0.2559% | 143.3217 | 2.133% | 976 | 6701.8088 | 6575.6783 | 1.918% | 0.2614%
2017-09-05 | 7 | 6720 | 126.1428 | 1.877% | 17.1925 | 0.2558% | 143.3353 | 2.133% | 977 | 6702.8075 | 6576.6647 | 1.918% | 0.2614%
2017-10-11 | 2 | 6720 | 126.1428 | 1.877% | 17.1925 | 0.2558% | 143.3353 | 2.133% | 978 | 6702.8075 | 6576.6647 | 1.918% | 0.2614%
2017-11-01 | 16 | 6720 | 126.1428 | 1.877% | 17.1925 | 0.2558% | 143.3353 | 2.133% | 979 | 6702.8075 | 6576.6647 | 1.918% | 0.2614%
2017-09-02 | 24 | 6722 | 126.1673 | 1.877% | 17.1951 | 0.2558% | 143.3625 | 2.133% | 980 | 6704.8049 | 6578.6375 | 1.918% | 0.2614%
2017-11-15 | 2 | 6722 | 126.1673 | 1.877% | 17.1951 | 0.2558% | 143.3625 | 2.133% | 981 | 6704.8049 | 6578.6375 | 1.918% | 0.2614%
2017-09-12 | 24 | 6723 | 126.1796 | 1.877% | 17.1964 | 0.2558% | 143.376 | 2.133% | 982 | 6705.8036 | 6579.624 | 1.918% | 0.2614%
2017-11-16 | 4 | 6725 | 126.2042 | 1.877% | 17.199 | 0.2557% | 143.4032 | 2.132% | 983 | 6707.801 | 6581.5968 | 1.918% | 0.2613%
2017-10-23 | 23 | 6726 | 126.2164 | 1.877% | 17.2003 | 0.2557% | 143.4168 | 2.132% | 984 | 6708.7997 | 6582.5832 | 1.917% | 0.2613%
2017-10-24 | 11 | 6726 | 126.2164 | 1.877% | 17.2003 | 0.2557% | 143.4168 | 2.132% | 985 | 6708.7997 | 6582.5832 | 1.917% | 0.2613%
2017-10-30 | 6 | 6727 | 126.2287 | 1.876% | 17.2016 | 0.2557% | 143.4304 | 2.132% | 986 | 6709.7984 | 6583.5696 | 1.917% | 0.2613%
2017-11-19 | 24 | 6727 | 126.2287 | 1.876% | 17.2016 | 0.2557% | 143.4304 | 2.132% | 987 | 6709.7984 | 6583.5696 | 1.917% | 0.2613%
2017-10-19 | 11 | 6728 | 126.241 | 1.876% | 17.2029 | 0.2557% | 143.4439 | 2.132% | 988 | 6710.7971 | 6584.5561 | 1.917% | 0.2613%
2017-09-18 | 24 | 6729 | 126.2533 | 1.876% | 17.2042 | 0.2557% | 143.4575 | 2.132% | 989 | 6711.7958 | 6585.5425 | 1.917% | 0.2612%
2017-11-06 | 11 | 6729 | 126.2533 | 1.876% | 17.2042 | 0.2557% | 143.4575 | 2.132% | 990 | 6711.7958 | 6585.5425 | 1.917% | 0.2612%
2017-11-04 | 20 | 6731 | 126.2778 | 1.876% | 17.2068 | 0.2556% | 143.4847 | 2.132% | 991 | 6713.7932 | 6587.5153 | 1.917% | 0.2612%
2017-09-04 | 24 | 6733 | 126.3024 | 1.876% | 17.2094 | 0.2556% | 143.5118 | 2.131% | 992 | 6715.7906 | 6589.4882 | 1.917% | 0.2612%
2017-11-07 | 22 | 6736 | 126.3392 | 1.876% | 17.2133 | 0.2555% | 143.5525 | 2.131% | 993 | 6718.7867 | 6592.4475 | 1.916% | 0.2611%
2017-10-26 | 11 | 6737 | 126.3515 | 1.875% | 17.2146 | 0.2555% | 143.5661 | 2.131% | 994 | 6719.7854 | 6593.4339 | 1.916% | 0.2611%
2017-09-02 | 10 | 6738 | 126.3637 | 1.875% | 17.2159 | 0.2555% | 143.5797 | 2.131% | 995 | 6720.7841 | 6594.4203 | 1.916% | 0.2611%
2017-09-19 | 24 | 6738 | 126.3637 | 1.875% | 17.2159 | 0.2555% | 143.5797 | 2.131% | 996 | 6720.7841 | 6594.4203 | 1.916% | 0.2611%
2017-11-25 | 21 | 6739 | 126.376 | 1.875% | 17.2172 | 0.2555% | 143.5933 | 2.131% | 997 | 6721.7828 | 6595.4067 | 1.916% | 0.261%
2017-10-31 | 20 | 6740 | 126.3883 | 1.875% | 17.2185 | 0.2555% | 143.6068 | 2.131% | 998 | 6722.7815 | 6596.3932 | 1.916% | 0.261%
2017-10-22 | 15 | 6744 | 126.4374 | 1.875% | 17.2237 | 0.2554% | 143.6611 | 2.13% | 999 | 6726.7763 | 6600.3389 | 1.916% | 0.261%
2017-11-16 | 1 | 6744 | 126.4374 | 1.875% | 17.2237 | 0.2554% | 143.6611 | 2.13% | 1000 | 6726.7763 | 6600.3389 | 1.916% | 0.261%
2017-11-15 | 16 | 6752 | 126.5356 | 1.874% | 17.2342 | 0.2552% | 143.7698 | 2.129% | 1001 | 6734.7658 | 6608.2302 | 1.915% | 0.2608%
2017-10-21 | 17 | 6753 | 126.5479 | 1.874% | 17.2355 | 0.2552% | 143.7833 | 2.129% | 1002 | 6735.7645 | 6609.2167 | 1.915% | 0.2608%
2017-09-25 | 8 | 6758 | 126.6093 | 1.873% | 17.242 | 0.2551% | 143.8512 | 2.129% | 1003 | 6740.758 | 6614.1488 | 1.914% | 0.2607%
2017-11-22 | 12 | 6758 | 126.6093 | 1.873% | 17.242 | 0.2551% | 143.8512 | 2.129% | 1004 | 6740.758 | 6614.1488 | 1.914% | 0.2607%
2017-10-16 | 8 | 6759 | 126.6215 | 1.873% | 17.2433 | 0.2551% | 143.8648 | 2.128% | 1005 | 6741.7567 | 6615.1352 | 1.914% | 0.2607%
2017-11-03 | 12 | 6764 | 126.6829 | 1.873% | 17.2498 | 0.255% | 143.9327 | 2.128% | 1006 | 6746.7502 | 6620.0673 | 1.914% | 0.2606%
2017-10-15 | 23 | 6765 | 126.6952 | 1.873% | 17.2511 | 0.255% | 143.9462 | 2.128% | 1007 | 6747.7489 | 6621.0538 | 1.914% | 0.2605%
2017-09-20 | 8 | 6767 | 126.7197 | 1.873% | 17.2537 | 0.255% | 143.9734 | 2.128% | 1008 | 6749.7463 | 6623.0266 | 1.913% | 0.2605%
2017-09-22 | 8 | 6767 | 126.7197 | 1.873% | 17.2537 | 0.255% | 143.9734 | 2.128% | 1009 | 6749.7463 | 6623.0266 | 1.913% | 0.2605%
2017-10-30 | 14 | 6767 | 126.7197 | 1.873% | 17.2537 | 0.255% | 143.9734 | 2.128% | 1010 | 6749.7463 | 6623.0266 | 1.913% | 0.2605%
2017-11-20 | 2 | 6768 | 126.732 | 1.873% | 17.255 | 0.2549% | 143.987 | 2.127% | 1011 | 6750.745 | 6624.013 | 1.913% | 0.2605%
2017-11-15 | 1 | 6769 | 126.7443 | 1.872% | 17.2563 | 0.2549% | 144.0005 | 2.127% | 1012 | 6751.7437 | 6624.9995 | 1.913% | 0.2605%
2017-11-12 | 13 | 6772 | 126.7811 | 1.872% | 17.2602 | 0.2549% | 144.0413 | 2.127% | 1013 | 6754.7398 | 6627.9587 | 1.913% | 0.2604%
2017-09-29 | 1 | 6773 | 126.7934 | 1.872% | 17.2615 | 0.2549% | 144.0549 | 2.127% | 1014 | 6755.7385 | 6628.9451 | 1.913% | 0.2604%
2017-09-29 | 23 | 6774 | 126.8057 | 1.872% | 17.2628 | 0.2548% | 144.0684 | 2.127% | 1015 | 6756.7372 | 6629.9316 | 1.913% | 0.2604%
2017-11-07 | 11 | 6774 | 126.8057 | 1.872% | 17.2628 | 0.2548% | 144.0684 | 2.127% | 1016 | 6756.7372 | 6629.9316 | 1.913% | 0.2604%
2017-11-13 | 14 | 6774 | 126.8057 | 1.872% | 17.2628 | 0.2548% | 144.0684 | 2.127% | 1017 | 6756.7372 | 6629.9316 | 1.913% | 0.2604%
2017-10-24 | 22 | 6775 | 126.8179 | 1.872% | 17.2641 | 0.2548% | 144.082 | 2.127% | 1018 | 6757.7359 | 6630.918 | 1.913% | 0.2604%
2017-09-06 | 23 | 6778 | 126.8548 | 1.872% | 17.268 | 0.2548% | 144.1227 | 2.126% | 1019 | 6760.732 | 6633.8773 | 1.912% | 0.2603%
2017-09-11 | 12 | 6778 | 126.8548 | 1.872% | 17.268 | 0.2548% | 144.1227 | 2.126% | 1020 | 6760.732 | 6633.8773 | 1.912% | 0.2603%
2017-09-13 | 24 | 6778 | 126.8548 | 1.872% | 17.268 | 0.2548% | 144.1227 | 2.126% | 1021 | 6760.732 | 6633.8773 | 1.912% | 0.2603%
2017-10-07 | 10 | 6778 | 126.8548 | 1.872% | 17.268 | 0.2548% | 144.1227 | 2.126% | 1022 | 6760.732 | 6633.8773 | 1.912% | 0.2603%
2017-10-30 | 18 | 6780 | 126.8793 | 1.871% | 17.2706 | 0.2547% | 144.1499 | 2.126% | 1023 | 6762.7294 | 6635.8501 | 1.912% | 0.2603%
2017-11-21 | 16 | 6781 | 126.8916 | 1.871% | 17.2719 | 0.2547% | 144.1635 | 2.126% | 1024 | 6763.7281 | 6636.8365 | 1.912% | 0.2602%
2017-10-19 | 14 | 6783 | 126.9161 | 1.871% | 17.2745 | 0.2547% | 144.1906 | 2.126% | 1025 | 6765.7255 | 6638.8094 | 1.912% | 0.2602%
2017-11-15 | 3 | 6784 | 126.9284 | 1.871% | 17.2758 | 0.2547% | 144.2042 | 2.126% | 1026 | 6766.7242 | 6639.7958 | 1.912% | 0.2602%
2017-11-21 | 15 | 6786 | 126.953 | 1.871% | 17.2784 | 0.2546% | 144.2313 | 2.125% | 1027 | 6768.7216 | 6641.7687 | 1.911% | 0.2601%
2017-10-29 | 21 | 6787 | 126.9652 | 1.871% | 17.2797 | 0.2546% | 144.2449 | 2.125% | 1028 | 6769.7203 | 6642.7551 | 1.911% | 0.2601%
2017-10-01 | 21 | 6789 | 126.9898 | 1.871% | 17.2823 | 0.2546% | 144.2721 | 2.125% | 1029 | 6771.7177 | 6644.7279 | 1.911% | 0.2601%
2017-10-11 | 6 | 6789 | 126.9898 | 1.871% | 17.2823 | 0.2546% | 144.2721 | 2.125% | 1030 | 6771.7177 | 6644.7279 | 1.911% | 0.2601%
2017-10-19 | 10 | 6790 | 127.0021 | 1.87% | 17.2836 | 0.2545% | 144.2856 | 2.125% | 1031 | 6772.7164 | 6645.7144 | 1.911% | 0.2601%
2017-10-26 | 7 | 6791 | 127.0143 | 1.87% | 17.2849 | 0.2545% | 144.2992 | 2.125% | 1032 | 6773.7151 | 6646.7008 | 1.911% | 0.2601%
2017-09-11 | 22 | 6793 | 127.0389 | 1.87% | 17.2875 | 0.2545% | 144.3264 | 2.125% | 1033 | 6775.7125 | 6648.6736 | 1.911% | 0.26%
2017-11-05 | 20 | 6793 | 127.0389 | 1.87% | 17.2875 | 0.2545% | 144.3264 | 2.125% | 1034 | 6775.7125 | 6648.6736 | 1.911% | 0.26%
2017-09-17 | 10 | 6794 | 127.0512 | 1.87% | 17.2888 | 0.2545% | 144.34 | 2.125% | 1035 | 6776.7112 | 6649.66 | 1.911% | 0.26%
2017-09-29 | 8 | 6798 | 127.1003 | 1.87% | 17.294 | 0.2544% | 144.3943 | 2.124% | 1036 | 6780.706 | 6653.6057 | 1.91% | 0.2599%
2017-11-15 | 14 | 6799 | 127.1125 | 1.87% | 17.2953 | 0.2544% | 144.4078 | 2.124% | 1037 | 6781.7047 | 6654.5922 | 1.91% | 0.2599%
2017-11-01 | 17 | 6801 | 127.1371 | 1.869% | 17.2979 | 0.2543% | 144.435 | 2.124% | 1038 | 6783.7021 | 6656.565 | 1.91% | 0.2599%
2017-11-28 | 14 | 6802 | 127.1494 | 1.869% | 17.2992 | 0.2543% | 144.4486 | 2.124% | 1039 | 6784.7008 | 6657.5514 | 1.91% | 0.2598%
2017-11-18 | 19 | 6804 | 127.1739 | 1.869% | 17.3018 | 0.2543% | 144.4757 | 2.123% | 1040 | 6786.6982 | 6659.5243 | 1.91% | 0.2598%
2017-10-31 | 21 | 6807 | 127.2107 | 1.869% | 17.3057 | 0.2542% | 144.5164 | 2.123% | 1041 | 6789.6943 | 6662.4836 | 1.909% | 0.2597%
2017-09-10 | 20 | 6809 | 127.2353 | 1.869% | 17.3083 | 0.2542% | 144.5436 | 2.123% | 1042 | 6791.6917 | 6664.4564 | 1.909% | 0.2597%
2017-10-10 | 2 | 6809 | 127.2353 | 1.869% | 17.3083 | 0.2542% | 144.5436 | 2.123% | 1043 | 6791.6917 | 6664.4564 | 1.909% | 0.2597%
2017-11-20 | 15 | 6809 | 127.2353 | 1.869% | 17.3083 | 0.2542% | 144.5436 | 2.123% | 1044 | 6791.6917 | 6664.4564 | 1.909% | 0.2597%
2017-11-20 | 16 | 6809 | 127.2353 | 1.869% | 17.3083 | 0.2542% | 144.5436 | 2.123% | 1045 | 6791.6917 | 6664.4564 | 1.909% | 0.2597%
2017-09-09 | 22 | 6811 | 127.2598 | 1.868% | 17.3109 | 0.2542% | 144.5707 | 2.123% | 1046 | 6793.6891 | 6666.4293 | 1.909% | 0.2597%
2017-09-08 | 11 | 6812 | 127.2721 | 1.868% | 17.3122 | 0.2541% | 144.5843 | 2.122% | 1047 | 6794.6878 | 6667.4157 | 1.909% | 0.2597%
2017-09-11 | 13 | 6813 | 127.2844 | 1.868% | 17.3135 | 0.2541% | 144.5979 | 2.122% | 1048 | 6795.6865 | 6668.4021 | 1.909% | 0.2596%
2017-09-21 | 7 | 6814 | 127.2967 | 1.868% | 17.3148 | 0.2541% | 144.6115 | 2.122% | 1049 | 6796.6852 | 6669.3885 | 1.909% | 0.2596%
2017-10-31 | 12 | 6814 | 127.2967 | 1.868% | 17.3148 | 0.2541% | 144.6115 | 2.122% | 1050 | 6796.6852 | 6669.3885 | 1.909% | 0.2596%
2017-10-26 | 19 | 6816 | 127.3212 | 1.868% | 17.3174 | 0.2541% | 144.6386 | 2.122% | 1051 | 6798.6826 | 6671.3614 | 1.908% | 0.2596%
2017-11-10 | 12 | 6817 | 127.3335 | 1.868% | 17.3187 | 0.2541% | 144.6522 | 2.122% | 1052 | 6799.6813 | 6672.3478 | 1.908% | 0.2596%
2017-10-27 | 11 | 6818 | 127.3458 | 1.868% | 17.32 | 0.254% | 144.6658 | 2.122% | 1053 | 6800.68 | 6673.3342 | 1.908% | 0.2595%
2017-10-18 | 19 | 6819 | 127.358 | 1.868% | 17.3213 | 0.254% | 144.6794 | 2.122% | 1054 | 6801.6787 | 6674.3206 | 1.908% | 0.2595%
2017-11-05 | 18 | 6819 | 127.358 | 1.868% | 17.3213 | 0.254% | 144.6794 | 2.122% | 1055 | 6801.6787 | 6674.3206 | 1.908% | 0.2595%
2017-11-29 | 23 | 6819 | 127.358 | 1.868% | 17.3213 | 0.254% | 144.6794 | 2.122% | 1056 | 6801.6787 | 6674.3206 | 1.908% | 0.2595%
2017-10-04 | 12 | 6821 | 127.3826 | 1.868% | 17.3239 | 0.254% | 144.7065 | 2.121% | 1057 | 6803.6761 | 6676.2935 | 1.908% | 0.2595%
2017-11-23 | 6 | 6821 | 127.3826 | 1.868% | 17.3239 | 0.254% | 144.7065 | 2.121% | 1058 | 6803.6761 | 6676.2935 | 1.908% | 0.2595%
2017-09-14 | 7 | 6823 | 127.4071 | 1.867% | 17.3265 | 0.2539% | 144.7337 | 2.121% | 1059 | 6805.6735 | 6678.2663 | 1.908% | 0.2594%
2017-11-02 | 22 | 6824 | 127.4194 | 1.867% | 17.3278 | 0.2539% | 144.7472 | 2.121% | 1060 | 6806.6722 | 6679.2528 | 1.908% | 0.2594%
2017-11-25 | 20 | 6824 | 127.4194 | 1.867% | 17.3278 | 0.2539% | 144.7472 | 2.121% | 1061 | 6806.6722 | 6679.2528 | 1.908% | 0.2594%
2017-11-25 | 19 | 6825 | 127.4317 | 1.867% | 17.3291 | 0.2539% | 144.7608 | 2.121% | 1062 | 6807.6709 | 6680.2392 | 1.908% | 0.2594%
2017-10-16 | 18 | 6826 | 127.444 | 1.867% | 17.3304 | 0.2539% | 144.7744 | 2.121% | 1063 | 6808.6696 | 6681.2256 | 1.907% | 0.2594%
2017-10-16 | 17 | 6828 | 127.4685 | 1.867% | 17.333 | 0.2539% | 144.8015 | 2.121% | 1064 | 6810.667 | 6683.1985 | 1.907% | 0.2594%
2017-10-12 | 24 | 6829 | 127.4808 | 1.867% | 17.3343 | 0.2538% | 144.8151 | 2.121% | 1065 | 6811.6657 | 6684.1849 | 1.907% | 0.2593%
2017-11-02 | 12 | 6829 | 127.4808 | 1.867% | 17.3343 | 0.2538% | 144.8151 | 2.121% | 1066 | 6811.6657 | 6684.1849 | 1.907% | 0.2593%
2017-11-30 | 5 | 6829 | 127.4808 | 1.867% | 17.3343 | 0.2538% | 144.8151 | 2.121% | 1067 | 6811.6657 | 6684.1849 | 1.907% | 0.2593%
2017-09-28 | 7 | 6831 | 127.5053 | 1.867% | 17.3369 | 0.2538% | 144.8423 | 2.12% | 1068 | 6813.6631 | 6686.1577 | 1.907% | 0.2593%
2017-10-14 | 22 | 6831 | 127.5053 | 1.867% | 17.3369 | 0.2538% | 144.8423 | 2.12% | 1069 | 6813.6631 | 6686.1577 | 1.907% | 0.2593%
2017-10-25 | 19 | 6832 | 127.5176 | 1.866% | 17.3382 | 0.2538% | 144.8558 | 2.12% | 1070 | 6814.6618 | 6687.1442 | 1.907% | 0.2593%
2017-09-11 | 16 | 6833 | 127.5299 | 1.866% | 17.3395 | 0.2538% | 144.8694 | 2.12% | 1071 | 6815.6605 | 6688.1306 | 1.907% | 0.2593%
2017-11-01 | 11 | 6834 | 127.5422 | 1.866% | 17.3408 | 0.2537% | 144.883 | 2.12% | 1072 | 6816.6592 | 6689.117 | 1.907% | 0.2592%
2017-10-23 | 10 | 6835 | 127.5544 | 1.866% | 17.3421 | 0.2537% | 144.8966 | 2.12% | 1073 | 6817.6579 | 6690.1034 | 1.907% | 0.2592%
2017-11-23 | 18 | 6837 | 127.579 | 1.866% | 17.3447 | 0.2537% | 144.9237 | 2.12% | 1074 | 6819.6553 | 6692.0763 | 1.906% | 0.2592%
2017-09-14 | 24 | 6838 | 127.5913 | 1.866% | 17.346 | 0.2537% | 144.9373 | 2.12% | 1075 | 6820.654 | 6693.0627 | 1.906% | 0.2592%
2017-11-27 | 14 | 6840 | 127.6158 | 1.866% | 17.3486 | 0.2536% | 144.9645 | 2.119% | 1076 | 6822.6514 | 6695.0355 | 1.906% | 0.2591%
2017-09-11 | 14 | 6842 | 127.6404 | 1.866% | 17.3512 | 0.2536% | 144.9916 | 2.119% | 1077 | 6824.6488 | 6697.0084 | 1.906% | 0.2591%
2017-11-14 | 14 | 6843 | 127.6526 | 1.865% | 17.3525 | 0.2536% | 145.0052 | 2.119% | 1078 | 6825.6475 | 6697.9948 | 1.906% | 0.2591%
2017-10-02 | 12 | 6844 | 127.6649 | 1.865% | 17.3538 | 0.2536% | 145.0188 | 2.119% | 1079 | 6826.6462 | 6698.9812 | 1.906% | 0.2591%
2017-11-17 | 13 | 6844 | 127.6649 | 1.865% | 17.3538 | 0.2536% | 145.0188 | 2.119% | 1080 | 6826.6462 | 6698.9812 | 1.906% | 0.2591%
2017-09-11 | 15 | 6846 | 127.6895 | 1.865% | 17.3564 | 0.2535% | 145.0459 | 2.119% | 1081 | 6828.6436 | 6700.9541 | 1.906% | 0.259%
2017-11-01 | 18 | 6846 | 127.6895 | 1.865% | 17.3564 | 0.2535% | 145.0459 | 2.119% | 1082 | 6828.6436 | 6700.9541 | 1.906% | 0.259%
2017-09-03 | 23 | 6847 | 127.7017 | 1.865% | 17.3577 | 0.2535% | 145.0595 | 2.119% | 1083 | 6829.6423 | 6701.9405 | 1.905% | 0.259%
2017-09-21 | 24 | 6850 | 127.7386 | 1.865% | 17.3616 | 0.2535% | 145.1002 | 2.118% | 1084 | 6832.6384 | 6704.8998 | 1.905% | 0.2589%
2017-10-12 | 1 | 6852 | 127.7631 | 1.865% | 17.3642 | 0.2534% | 145.1274 | 2.118% | 1085 | 6834.6358 | 6706.8726 | 1.905% | 0.2589%
2017-10-03 | 12 | 6853 | 127.7754 | 1.865% | 17.3655 | 0.2534% | 145.1409 | 2.118% | 1086 | 6835.6345 | 6707.8591 | 1.905% | 0.2589%
2017-10-20 | 15 | 6853 | 127.7754 | 1.865% | 17.3655 | 0.2534% | 145.1409 | 2.118% | 1087 | 6835.6345 | 6707.8591 | 1.905% | 0.2589%
2017-11-07 | 12 | 6853 | 127.7754 | 1.865% | 17.3655 | 0.2534% | 145.1409 | 2.118% | 1088 | 6835.6345 | 6707.8591 | 1.905% | 0.2589%
2017-09-13 | 9 | 6856 | 127.8122 | 1.864% | 17.3695 | 0.2533% | 145.1817 | 2.118% | 1089 | 6838.6305 | 6710.8183 | 1.905% | 0.2588%
2017-11-14 | 15 | 6860 | 127.8613 | 1.864% | 17.3747 | 0.2533% | 145.236 | 2.117% | 1090 | 6842.6253 | 6714.764 | 1.904% | 0.2588%
2017-09-11 | 17 | 6862 | 127.8859 | 1.864% | 17.3773 | 0.2532% | 145.2631 | 2.117% | 1091 | 6844.6227 | 6716.7369 | 1.904% | 0.2587%
2017-11-23 | 14 | 6863 | 127.8981 | 1.864% | 17.3786 | 0.2532% | 145.2767 | 2.117% | 1092 | 6845.6214 | 6717.7233 | 1.904% | 0.2587%
2017-10-30 | 23 | 6865 | 127.9227 | 1.863% | 17.3812 | 0.2532% | 145.3039 | 2.117% | 1093 | 6847.6188 | 6719.6961 | 1.904% | 0.2587%
2017-11-11 | 1 | 6865 | 127.9227 | 1.863% | 17.3812 | 0.2532% | 145.3039 | 2.117% | 1094 | 6847.6188 | 6719.6961 | 1.904% | 0.2587%
2017-10-18 | 10 | 6866 | 127.935 | 1.863% | 17.3825 | 0.2532% | 145.3174 | 2.116% | 1095 | 6848.6175 | 6720.6826 | 1.904% | 0.2586%
2017-10-29 | 20 | 6867 | 127.9472 | 1.863% | 17.3838 | 0.2531% | 145.331 | 2.116% | 1096 | 6849.6162 | 6721.669 | 1.904% | 0.2586%
2017-09-25 | 24 | 6871 | 127.9963 | 1.863% | 17.389 | 0.2531% | 145.3853 | 2.116% | 1097 | 6853.611 | 6725.6147 | 1.903% | 0.2585%
2017-09-30 | 12 | 6871 | 127.9963 | 1.863% | 17.389 | 0.2531% | 145.3853 | 2.116% | 1098 | 6853.611 | 6725.6147 | 1.903% | 0.2585%
2017-10-14 | 15 | 6871 | 127.9963 | 1.863% | 17.389 | 0.2531% | 145.3853 | 2.116% | 1099 | 6853.611 | 6725.6147 | 1.903% | 0.2585%
2017-11-22 | 8 | 6871 | 127.9963 | 1.863% | 17.389 | 0.2531% | 145.3853 | 2.116% | 1100 | 6853.611 | 6725.6147 | 1.903% | 0.2585%
2017-11-28 | 17 | 6872 | 128.0086 | 1.863% | 17.3903 | 0.2531% | 145.3989 | 2.116% | 1101 | 6854.6097 | 6726.6011 | 1.903% | 0.2585%
2017-09-10 | 21 | 6873 | 128.0209 | 1.863% | 17.3916 | 0.253% | 145.4125 | 2.116% | 1102 | 6855.6084 | 6727.5875 | 1.903% | 0.2585%
2017-11-12 | 17 | 6873 | 128.0209 | 1.863% | 17.3916 | 0.253% | 145.4125 | 2.116% | 1103 | 6855.6084 | 6727.5875 | 1.903% | 0.2585%
2017-10-18 | 7 | 6874 | 128.0332 | 1.863% | 17.3929 | 0.253% | 145.426 | 2.116% | 1104 | 6856.6071 | 6728.574 | 1.903% | 0.2585%
2017-11-22 | 11 | 6875 | 128.0454 | 1.862% | 17.3942 | 0.253% | 145.4396 | 2.115% | 1105 | 6857.6058 | 6729.5604 | 1.903% | 0.2585%
2017-10-05 | 23 | 6876 | 128.0577 | 1.862% | 17.3955 | 0.253% | 145.4532 | 2.115% | 1106 | 6858.6045 | 6730.5468 | 1.903% | 0.2585%
2017-10-16 | 9 | 6876 | 128.0577 | 1.862% | 17.3955 | 0.253% | 145.4532 | 2.115% | 1107 | 6858.6045 | 6730.5468 | 1.903% | 0.2585%
2017-11-13 | 13 | 6876 | 128.0577 | 1.862% | 17.3955 | 0.253% | 145.4532 | 2.115% | 1108 | 6858.6045 | 6730.5468 | 1.903% | 0.2585%
2017-11-13 | 23 | 6878 | 128.0823 | 1.862% | 17.3981 | 0.253% | 145.4803 | 2.115% | 1109 | 6860.6019 | 6732.5197 | 1.902% | 0.2584%
2017-10-19 | 9 | 6879 | 128.0946 | 1.862% | 17.3994 | 0.2529% | 145.4939 | 2.115% | 1110 | 6861.6006 | 6733.5061 | 1.902% | 0.2584%
2017-10-24 | 12 | 6885 | 128.1682 | 1.862% | 17.4072 | 0.2528% | 145.5754 | 2.114% | 1111 | 6867.5928 | 6739.4246 | 1.902% | 0.2583%
2017-11-11 | 2 | 6885 | 128.1682 | 1.862% | 17.4072 | 0.2528% | 145.5754 | 2.114% | 1112 | 6867.5928 | 6739.4246 | 1.902% | 0.2583%
2017-10-26 | 22 | 6886 | 128.1805 | 1.861% | 17.4085 | 0.2528% | 145.589 | 2.114% | 1113 | 6868.5915 | 6740.411 | 1.902% | 0.2583%
2017-09-15 | 8 | 6887 | 128.1928 | 1.861% | 17.4098 | 0.2528% | 145.6025 | 2.114% | 1114 | 6869.5902 | 6741.3975 | 1.902% | 0.2583%
2017-09-30 | 21 | 6887 | 128.1928 | 1.861% | 17.4098 | 0.2528% | 145.6025 | 2.114% | 1115 | 6869.5902 | 6741.3975 | 1.902% | 0.2583%
2017-11-03 | 13 | 6888 | 128.205 | 1.861% | 17.4111 | 0.2528% | 145.6161 | 2.114% | 1116 | 6870.5889 | 6742.3839 | 1.901% | 0.2582%
2017-10-19 | 15 | 6890 | 128.2296 | 1.861% | 17.4137 | 0.2527% | 145.6433 | 2.114% | 1117 | 6872.5863 | 6744.3567 | 1.901% | 0.2582%
2017-10-31 | 6 | 6893 | 128.2664 | 1.861% | 17.4176 | 0.2527% | 145.684 | 2.114% | 1118 | 6875.5824 | 6747.316 | 1.901% | 0.2581%
2017-11-06 | 12 | 6897 | 128.3155 | 1.86% | 17.4228 | 0.2526% | 145.7383 | 2.113% | 1119 | 6879.5772 | 6751.2617 | 1.901% | 0.2581%
2017-11-13 | 17 | 6899 | 128.3401 | 1.86% | 17.4254 | 0.2526% | 145.7654 | 2.113% | 1120 | 6881.5746 | 6753.2346 | 1.9% | 0.258%
2017-10-01 | 20 | 6900 | 128.3523 | 1.86% | 17.4267 | 0.2526% | 145.779 | 2.113% | 1121 | 6882.5733 | 6754.221 | 1.9% | 0.258%
2017-10-26 | 10 | 6901 | 128.3646 | 1.86% | 17.428 | 0.2525% | 145.7926 | 2.113% | 1122 | 6883.572 | 6755.2074 | 1.9% | 0.258%
2017-10-05 | 10 | 6902 | 128.3769 | 1.86% | 17.4293 | 0.2525% | 145.8062 | 2.113% | 1123 | 6884.5707 | 6756.1938 | 1.9% | 0.258%
2017-11-11 | 14 | 6903 | 128.3892 | 1.86% | 17.4306 | 0.2525% | 145.8197 | 2.112% | 1124 | 6885.5694 | 6757.1803 | 1.9% | 0.258%
2017-09-01 | 24 | 6905 | 128.4137 | 1.86% | 17.4332 | 0.2525% | 145.8469 | 2.112% | 1125 | 6887.5668 | 6759.1531 | 1.9% | 0.2579%
2017-10-20 | 19 | 6905 | 128.4137 | 1.86% | 17.4332 | 0.2525% | 145.8469 | 2.112% | 1126 | 6887.5668 | 6759.1531 | 1.9% | 0.2579%
2017-11-22 | 23 | 6913 | 128.5119 | 1.859% | 17.4436 | 0.2523% | 145.9555 | 2.111% | 1127 | 6895.5564 | 6767.0445 | 1.899% | 0.2578%
2017-11-21 | 14 | 6917 | 128.561 | 1.859% | 17.4488 | 0.2523% | 146.0098 | 2.111% | 1128 | 6899.5512 | 6770.9902 | 1.899% | 0.2577%
2017-09-07 | 11 | 6920 | 128.5978 | 1.858% | 17.4527 | 0.2522% | 146.0505 | 2.111% | 1129 | 6902.5473 | 6773.9495 | 1.898% | 0.2576%
2017-09-29 | 9 | 6920 | 128.5978 | 1.858% | 17.4527 | 0.2522% | 146.0505 | 2.111% | 1130 | 6902.5473 | 6773.9495 | 1.898% | 0.2576%
2017-10-20 | 20 | 6920 | 128.5978 | 1.858% | 17.4527 | 0.2522% | 146.0505 | 2.111% | 1131 | 6902.5473 | 6773.9495 | 1.898% | 0.2576%
2017-11-16 | 12 | 6920 | 128.5978 | 1.858% | 17.4527 | 0.2522% | 146.0505 | 2.111% | 1132 | 6902.5473 | 6773.9495 | 1.898% | 0.2576%
2017-09-12 | 9 | 6921 | 128.6101 | 1.858% | 17.454 | 0.2522% | 146.0641 | 2.11% | 1133 | 6903.546 | 6774.9359 | 1.898% | 0.2576%
2017-11-08 | 23 | 6921 | 128.6101 | 1.858% | 17.454 | 0.2522% | 146.0641 | 2.11% | 1134 | 6903.546 | 6774.9359 | 1.898% | 0.2576%
2017-10-18 | 21 | 6923 | 128.6347 | 1.858% | 17.4566 | 0.2522% | 146.0913 | 2.11% | 1135 | 6905.5434 | 6776.9087 | 1.898% | 0.2576%
2017-09-15 | 24 | 6925 | 128.6592 | 1.858% | 17.4592 | 0.2521% | 146.1184 | 2.11% | 1136 | 6907.5408 | 6778.8816 | 1.898% | 0.2576%
2017-11-30 | 12 | 6928 | 128.696 | 1.858% | 17.4631 | 0.2521% | 146.1592 | 2.11% | 1137 | 6910.5369 | 6781.8408 | 1.898% | 0.2575%
2017-09-19 | 8 | 6929 | 128.7083 | 1.858% | 17.4644 | 0.252% | 146.1727 | 2.11% | 1138 | 6911.5356 | 6782.8273 | 1.898% | 0.2575%
2017-11-08 | 8 | 6929 | 128.7083 | 1.858% | 17.4644 | 0.252% | 146.1727 | 2.11% | 1139 | 6911.5356 | 6782.8273 | 1.898% | 0.2575%
2017-11-27 | 1 | 6931 | 128.7329 | 1.857% | 17.467 | 0.252% | 146.1999 | 2.109% | 1140 | 6913.533 | 6784.8001 | 1.897% | 0.2574%
2017-10-08 | 9 | 6932 | 128.7451 | 1.857% | 17.4683 | 0.252% | 146.2135 | 2.109% | 1141 | 6914.5317 | 6785.7865 | 1.897% | 0.2574%
2017-09-09 | 13 | 6941 | 128.8556 | 1.856% | 17.48 | 0.2518% | 146.3356 | 2.108% | 1142 | 6923.52 | 6794.6644 | 1.896% | 0.2573%
2017-10-19 | 8 | 6941 | 128.8556 | 1.856% | 17.48 | 0.2518% | 146.3356 | 2.108% | 1143 | 6923.52 | 6794.6644 | 1.896% | 0.2573%
2017-11-14 | 13 | 6941 | 128.8556 | 1.856% | 17.48 | 0.2518% | 146.3356 | 2.108% | 1144 | 6923.52 | 6794.6644 | 1.896% | 0.2573%
2017-11-21 | 17 | 6946 | 128.917 | 1.856% | 17.4865 | 0.2517% | 146.4035 | 2.108% | 1145 | 6928.5135 | 6799.5965 | 1.896% | 0.2572%
2017-09-25 | 9 | 6948 | 128.9415 | 1.856% | 17.4891 | 0.2517% | 146.4307 | 2.108% | 1146 | 6930.5109 | 6801.5693 | 1.896% | 0.2571%
2017-10-16 | 19 | 6948 | 128.9415 | 1.856% | 17.4891 | 0.2517% | 146.4307 | 2.108% | 1147 | 6930.5109 | 6801.5693 | 1.896% | 0.2571%
2017-11-14 | 16 | 6948 | 128.9415 | 1.856% | 17.4891 | 0.2517% | 146.4307 | 2.108% | 1148 | 6930.5109 | 6801.5693 | 1.896% | 0.2571%
2017-10-06 | 23 | 6949 | 128.9538 | 1.856% | 17.4904 | 0.2517% | 146.4443 | 2.107% | 1149 | 6931.5096 | 6802.5557 | 1.896% | 0.2571%
2017-10-16 | 21 | 6953 | 129.0029 | 1.855% | 17.4956 | 0.2516% | 146.4986 | 2.107% | 1150 | 6935.5044 | 6806.5014 | 1.895% | 0.257%
2017-09-22 | 24 | 6954 | 129.0152 | 1.855% | 17.4969 | 0.2516% | 146.5121 | 2.107% | 1151 | 6936.5031 | 6807.4879 | 1.895% | 0.257%
2017-11-02 | 13 | 6954 | 129.0152 | 1.855% | 17.4969 | 0.2516% | 146.5121 | 2.107% | 1152 | 6936.5031 | 6807.4879 | 1.895% | 0.257%
2017-11-12 | 22 | 6954 | 129.0152 | 1.855% | 17.4969 | 0.2516% | 146.5121 | 2.107% | 1153 | 6936.5031 | 6807.4879 | 1.895% | 0.257%
2017-09-06 | 7 | 6956 | 129.0397 | 1.855% | 17.4995 | 0.2516% | 146.5393 | 2.107% | 1154 | 6938.5005 | 6809.4607 | 1.895% | 0.257%
2017-09-11 | 18 | 6956 | 129.0397 | 1.855% | 17.4995 | 0.2516% | 146.5393 | 2.107% | 1155 | 6938.5005 | 6809.4607 | 1.895% | 0.257%
2017-10-22 | 16 | 6956 | 129.0397 | 1.855% | 17.4995 | 0.2516% | 146.5393 | 2.107% | 1156 | 6938.5005 | 6809.4607 | 1.895% | 0.257%
2017-11-14 | 24 | 6961 | 129.1011 | 1.855% | 17.506 | 0.2515% | 146.6072 | 2.106% | 1157 | 6943.494 | 6814.3928 | 1.895% | 0.2569%
2017-11-26 | 18 | 6962 | 129.1134 | 1.855% | 17.5073 | 0.2515% | 146.6207 | 2.106% | 1158 | 6944.4927 | 6815.3793 | 1.894% | 0.2569%
2017-11-15 | 13 | 6963 | 129.1257 | 1.854% | 17.5086 | 0.2515% | 146.6343 | 2.106% | 1159 | 6945.4914 | 6816.3657 | 1.894% | 0.2569%
2017-11-19 | 18 | 6965 | 129.1502 | 1.854% | 17.5113 | 0.2514% | 146.6615 | 2.106% | 1160 | 6947.4887 | 6818.3385 | 1.894% | 0.2568%
2017-10-19 | 16 | 6967 | 129.1748 | 1.854% | 17.5139 | 0.2514% | 146.6886 | 2.105% | 1161 | 6949.4861 | 6820.3114 | 1.894% | 0.2568%
2017-11-20 | 14 | 6968 | 129.187 | 1.854% | 17.5152 | 0.2514% | 146.7022 | 2.105% | 1162 | 6950.4848 | 6821.2978 | 1.894% | 0.2568%
2017-11-27 | 17 | 6969 | 129.1993 | 1.854% | 17.5165 | 0.2513% | 146.7158 | 2.105% | 1163 | 6951.4835 | 6822.2842 | 1.894% | 0.2568%
2017-11-28 | 13 | 6969 | 129.1993 | 1.854% | 17.5165 | 0.2513% | 146.7158 | 2.105% | 1164 | 6951.4835 | 6822.2842 | 1.894% | 0.2568%
2017-11-08 | 9 | 6971 | 129.2239 | 1.854% | 17.5191 | 0.2513% | 146.7429 | 2.105% | 1165 | 6953.4809 | 6824.2571 | 1.894% | 0.2567%
2017-09-18 | 8 | 6975 | 129.273 | 1.853% | 17.5243 | 0.2512% | 146.7972 | 2.105% | 1166 | 6957.4757 | 6828.2028 | 1.893% | 0.2566%
2017-09-23 | 10 | 6976 | 129.2852 | 1.853% | 17.5256 | 0.2512% | 146.8108 | 2.105% | 1167 | 6958.4744 | 6829.1892 | 1.893% | 0.2566%
2017-11-03 | 21 | 6977 | 129.2975 | 1.853% | 17.5269 | 0.2512% | 146.8244 | 2.104% | 1168 | 6959.4731 | 6830.1756 | 1.893% | 0.2566%
2017-11-15 | 24 | 6978 | 129.3098 | 1.853% | 17.5282 | 0.2512% | 146.838 | 2.104% | 1169 | 6960.4718 | 6831.162 | 1.893% | 0.2566%
2017-10-16 | 16 | 6979 | 129.3221 | 1.853% | 17.5295 | 0.2512% | 146.8515 | 2.104% | 1170 | 6961.4705 | 6832.1485 | 1.893% | 0.2566%
2017-11-15 | 4 | 6979 | 129.3221 | 1.853% | 17.5295 | 0.2512% | 146.8515 | 2.104% | 1171 | 6961.4705 | 6832.1485 | 1.893% | 0.2566%
2017-11-19 | 23 | 6981 | 129.3466 | 1.853% | 17.5321 | 0.2511% | 146.8787 | 2.104% | 1172 | 6963.4679 | 6834.1213 | 1.893% | 0.2565%
2017-10-17 | 21 | 6982 | 129.3589 | 1.853% | 17.5334 | 0.2511% | 146.8923 | 2.104% | 1173 | 6964.4666 | 6835.1077 | 1.893% | 0.2565%
2017-11-20 | 3 | 6984 | 129.3834 | 1.853% | 17.536 | 0.2511% | 146.9194 | 2.104% | 1174 | 6966.464 | 6837.0806 | 1.892% | 0.2565%
2017-11-26 | 10 | 6984 | 129.3834 | 1.853% | 17.536 | 0.2511% | 146.9194 | 2.104% | 1175 | 6966.464 | 6837.0806 | 1.892% | 0.2565%
2017-10-30 | 13 | 6985 | 129.3957 | 1.852% | 17.5373 | 0.2511% | 146.933 | 2.104% | 1176 | 6967.4627 | 6838.067 | 1.892% | 0.2565%
2017-11-23 | 19 | 6989 | 129.4448 | 1.852% | 17.5425 | 0.251% | 146.9873 | 2.103% | 1177 | 6971.4575 | 6842.0127 | 1.892% | 0.2564%
2017-10-06 | 10 | 6992 | 129.4816 | 1.852% | 17.5464 | 0.2509% | 147.028 | 2.103% | 1178 | 6974.4536 | 6844.972 | 1.892% | 0.2563%
2017-10-13 | 8 | 6992 | 129.4816 | 1.852% | 17.5464 | 0.2509% | 147.028 | 2.103% | 1179 | 6974.4536 | 6844.972 | 1.892% | 0.2563%
2017-11-07 | 13 | 6993 | 129.4939 | 1.852% | 17.5477 | 0.2509% | 147.0416 | 2.103% | 1180 | 6975.4523 | 6845.9584 | 1.892% | 0.2563%
2017-09-26 | 7 | 6995 | 129.5185 | 1.852% | 17.5503 | 0.2509% | 147.0688 | 2.102% | 1181 | 6977.4497 | 6847.9312 | 1.891% | 0.2563%
2017-10-20 | 16 | 6996 | 129.5307 | 1.851% | 17.5516 | 0.2509% | 147.0823 | 2.102% | 1182 | 6978.4484 | 6848.9177 | 1.891% | 0.2563%
2017-11-05 | 19 | 6997 | 129.543 | 1.851% | 17.5529 | 0.2509% | 147.0959 | 2.102% | 1183 | 6979.4471 | 6849.9041 | 1.891% | 0.2563%
2017-11-10 | 7 | 6997 | 129.543 | 1.851% | 17.5529 | 0.2509% | 147.0959 | 2.102% | 1184 | 6979.4471 | 6849.9041 | 1.891% | 0.2563%
2017-11-10 | 24 | 7000 | 129.5798 | 1.851% | 17.5568 | 0.2508% | 147.1366 | 2.102% | 1185 | 6982.4432 | 6852.8634 | 1.891% | 0.2562%
2017-11-22 | 10 | 7000 | 129.5798 | 1.851% | 17.5568 | 0.2508% | 147.1366 | 2.102% | 1186 | 6982.4432 | 6852.8634 | 1.891% | 0.2562%
2017-11-29 | 11 | 7002 | 129.6044 | 1.851% | 17.5594 | 0.2508% | 147.1638 | 2.102% | 1187 | 6984.4406 | 6854.8362 | 1.891% | 0.2562%
2017-10-13 | 9 | 7003 | 129.6167 | 1.851% | 17.5607 | 0.2508% | 147.1774 | 2.102% | 1188 | 6985.4393 | 6855.8226 | 1.891% | 0.2561%
2017-11-11 | 3 | 7004 | 129.629 | 1.851% | 17.562 | 0.2507% | 147.1909 | 2.102% | 1189 | 6986.438 | 6856.8091 | 1.891% | 0.2561%
2017-10-02 | 13 | 7009 | 129.6903 | 1.85% | 17.5685 | 0.2507% | 147.2588 | 2.101% | 1190 | 6991.4315 | 6861.7412 | 1.89% | 0.256%
2017-10-10 | 6 | 7010 | 129.7026 | 1.85% | 17.5698 | 0.2506% | 147.2724 | 2.101% | 1191 | 6992.4302 | 6862.7276 | 1.89% | 0.256%
2017-11-16 | 23 | 7011 | 129.7149 | 1.85% | 17.5711 | 0.2506% | 147.286 | 2.101% | 1192 | 6993.4289 | 6863.714 | 1.89% | 0.256%
2017-11-22 | 9 | 7012 | 129.7272 | 1.85% | 17.5724 | 0.2506% | 147.2995 | 2.101% | 1193 | 6994.4276 | 6864.7005 | 1.89% | 0.256%
2017-11-17 | 5 | 7013 | 129.7394 | 1.85% | 17.5737 | 0.2506% | 147.3131 | 2.101% | 1194 | 6995.4263 | 6865.6869 | 1.89% | 0.256%
2017-09-08 | 12 | 7014 | 129.7517 | 1.85% | 17.575 | 0.2506% | 147.3267 | 2.1% | 1195 | 6996.425 | 6866.6733 | 1.89% | 0.2559%
2017-11-07 | 16 | 7016 | 129.7763 | 1.85% | 17.5776 | 0.2505% | 147.3539 | 2.1% | 1196 | 6998.4224 | 6868.6461 | 1.889% | 0.2559%
2017-11-26 | 24 | 7017 | 129.7885 | 1.85% | 17.5789 | 0.2505% | 147.3674 | 2.1% | 1197 | 6999.4211 | 6869.6326 | 1.889% | 0.2559%
2017-11-11 | 17 | 7024 | 129.8745 | 1.849% | 17.588 | 0.2504% | 147.4625 | 2.099% | 1198 | 7006.412 | 6876.5375 | 1.889% | 0.2558%
2017-10-02 | 22 | 7026 | 129.899 | 1.849% | 17.5906 | 0.2504% | 147.4896 | 2.099% | 1199 | 7008.4094 | 6878.5104 | 1.888% | 0.2557%
2017-10-20 | 18 | 7026 | 129.899 | 1.849% | 17.5906 | 0.2504% | 147.4896 | 2.099% | 1200 | 7008.4094 | 6878.5104 | 1.888% | 0.2557%
2017-09-03 | 11 | 7027 | 129.9113 | 1.849% | 17.5919 | 0.2503% | 147.5032 | 2.099% | 1201 | 7009.4081 | 6879.4968 | 1.888% | 0.2557%
2017-11-27 | 2 | 7027 | 129.9113 | 1.849% | 17.5919 | 0.2503% | 147.5032 | 2.099% | 1202 | 7009.4081 | 6879.4968 | 1.888% | 0.2557%
2017-09-01 | 7 | 7028 | 129.9236 | 1.849% | 17.5932 | 0.2503% | 147.5168 | 2.099% | 1203 | 7010.4068 | 6880.4832 | 1.888% | 0.2557%
2017-10-25 | 21 | 7029 | 129.9358 | 1.849% | 17.5945 | 0.2503% | 147.5303 | 2.099% | 1204 | 7011.4055 | 6881.4697 | 1.888% | 0.2557%
2017-11-08 | 10 | 7029 | 129.9358 | 1.849% | 17.5945 | 0.2503% | 147.5303 | 2.099% | 1205 | 7011.4055 | 6881.4697 | 1.888% | 0.2557%
2017-11-16 | 5 | 7029 | 129.9358 | 1.849% | 17.5945 | 0.2503% | 147.5303 | 2.099% | 1206 | 7011.4055 | 6881.4697 | 1.888% | 0.2557%
2017-09-11 | 19 | 7030 | 129.9481 | 1.848% | 17.5958 | 0.2503% | 147.5439 | 2.099% | 1207 | 7012.4042 | 6882.4561 | 1.888% | 0.2557%
2017-10-08 | 24 | 7030 | 129.9481 | 1.848% | 17.5958 | 0.2503% | 147.5439 | 2.099% | 1208 | 7012.4042 | 6882.4561 | 1.888% | 0.2557%
2017-09-08 | 22 | 7031 | 129.9604 | 1.848% | 17.5971 | 0.2503% | 147.5575 | 2.099% | 1209 | 7013.4029 | 6883.4425 | 1.888% | 0.2556%
2017-10-07 | 24 | 7032 | 129.9727 | 1.848% | 17.5984 | 0.2503% | 147.5711 | 2.099% | 1210 | 7014.4016 | 6884.4289 | 1.888% | 0.2556%
2017-11-24 | 18 | 7032 | 129.9727 | 1.848% | 17.5984 | 0.2503% | 147.5711 | 2.099% | 1211 | 7014.4016 | 6884.4289 | 1.888% | 0.2556%
2017-11-01 | 10 | 7034 | 129.9972 | 1.848% | 17.601 | 0.2502% | 147.5982 | 2.098% | 1212 | 7016.399 | 6886.4018 | 1.888% | 0.2556%
2017-10-19 | 18 | 7036 | 130.0218 | 1.848% | 17.6036 | 0.2502% | 147.6254 | 2.098% | 1213 | 7018.3964 | 6888.3746 | 1.888% | 0.2556%
2017-11-10 | 11 | 7036 | 130.0218 | 1.848% | 17.6036 | 0.2502% | 147.6254 | 2.098% | 1214 | 7018.3964 | 6888.3746 | 1.888% | 0.2556%
2017-09-28 | 8 | 7038 | 130.0463 | 1.848% | 17.6062 | 0.2502% | 147.6525 | 2.098% | 1215 | 7020.3938 | 6890.3475 | 1.887% | 0.2555%
2017-11-15 | 17 | 7038 | 130.0463 | 1.848% | 17.6062 | 0.2502% | 147.6525 | 2.098% | 1216 | 7020.3938 | 6890.3475 | 1.887% | 0.2555%
2017-10-13 | 22 | 7042 | 130.0954 | 1.847% | 17.6114 | 0.2501% | 147.7068 | 2.098% | 1217 | 7024.3886 | 6894.2932 | 1.887% | 0.2554%
2017-09-20 | 9 | 7044 | 130.12 | 1.847% | 17.614 | 0.2501% | 147.734 | 2.097% | 1218 | 7026.386 | 6896.266 | 1.887% | 0.2554%
2017-11-12 | 12 | 7045 | 130.1322 | 1.847% | 17.6153 | 0.25% | 147.7476 | 2.097% | 1219 | 7027.3847 | 6897.2524 | 1.887% | 0.2554%
2017-09-21 | 8 | 7046 | 130.1445 | 1.847% | 17.6166 | 0.25% | 147.7611 | 2.097% | 1220 | 7028.3834 | 6898.2389 | 1.887% | 0.2554%
2017-10-23 | 11 | 7046 | 130.1445 | 1.847% | 17.6166 | 0.25% | 147.7611 | 2.097% | 1221 | 7028.3834 | 6898.2389 | 1.887% | 0.2554%
2017-11-02 | 14 | 7051 | 130.2059 | 1.847% | 17.6231 | 0.2499% | 147.829 | 2.097% | 1222 | 7033.3769 | 6903.171 | 1.886% | 0.2553%
2017-10-22 | 17 | 7054 | 130.2427 | 1.846% | 17.627 | 0.2499% | 147.8697 | 2.096% | 1223 | 7036.373 | 6906.1303 | 1.886% | 0.2552%
2017-11-21 | 22 | 7055 | 130.255 | 1.846% | 17.6283 | 0.2499% | 147.8833 | 2.096% | 1224 | 7037.3717 | 6907.1167 | 1.886% | 0.2552%
2017-11-24 | 1 | 7055 | 130.255 | 1.846% | 17.6283 | 0.2499% | 147.8833 | 2.096% | 1225 | 7037.3717 | 6907.1167 | 1.886% | 0.2552%
2017-10-03 | 13 | 7057 | 130.2795 | 1.846% | 17.6309 | 0.2498% | 147.9105 | 2.096% | 1226 | 7039.3691 | 6909.0895 | 1.886% | 0.2552%
2017-10-15 | 13 | 7058 | 130.2918 | 1.846% | 17.6322 | 0.2498% | 147.924 | 2.096% | 1227 | 7040.3678 | 6910.076 | 1.886% | 0.2552%
2017-09-05 | 8 | 7059 | 130.3041 | 1.846% | 17.6335 | 0.2498% | 147.9376 | 2.096% | 1228 | 7041.3665 | 6911.0624 | 1.885% | 0.2551%
2017-10-11 | 1 | 7062 | 130.3409 | 1.846% | 17.6374 | 0.2498% | 147.9784 | 2.095% | 1229 | 7044.3626 | 6914.0216 | 1.885% | 0.2551%
2017-11-27 | 13 | 7062 | 130.3409 | 1.846% | 17.6374 | 0.2498% | 147.9784 | 2.095% | 1230 | 7044.3626 | 6914.0216 | 1.885% | 0.2551%
2017-09-19 | 9 | 7063 | 130.3532 | 1.846% | 17.6387 | 0.2497% | 147.9919 | 2.095% | 1231 | 7045.3613 | 6915.0081 | 1.885% | 0.2551%
2017-11-03 | 14 | 7065 | 130.3777 | 1.845% | 17.6413 | 0.2497% | 148.0191 | 2.095% | 1232 | 7047.3587 | 6916.9809 | 1.885% | 0.255%
2017-10-24 | 13 | 7068 | 130.4146 | 1.845% | 17.6452 | 0.2496% | 148.0598 | 2.095% | 1233 | 7050.3548 | 6919.9402 | 1.885% | 0.255%
2017-11-08 | 11 | 7068 | 130.4146 | 1.845% | 17.6452 | 0.2496% | 148.0598 | 2.095% | 1234 | 7050.3548 | 6919.9402 | 1.885% | 0.255%
2017-11-07 | 15 | 7069 | 130.4268 | 1.845% | 17.6465 | 0.2496% | 148.0734 | 2.095% | 1235 | 7051.3535 | 6920.9266 | 1.885% | 0.255%
2017-10-19 | 19 | 7070 | 130.4391 | 1.845% | 17.6478 | 0.2496% | 148.087 | 2.095% | 1236 | 7052.3522 | 6921.913 | 1.884% | 0.255%
2017-11-26 | 8 | 7071 | 130.4514 | 1.845% | 17.6491 | 0.2496% | 148.1005 | 2.094% | 1237 | 7053.3509 | 6922.8995 | 1.884% | 0.2549%
2017-09-02 | 11 | 7072 | 130.4637 | 1.845% | 17.6504 | 0.2496% | 148.1141 | 2.094% | 1238 | 7054.3496 | 6923.8859 | 1.884% | 0.2549%
2017-10-20 | 17 | 7076 | 130.5128 | 1.844% | 17.6557 | 0.2495% | 148.1684 | 2.094% | 1239 | 7058.3443 | 6927.8316 | 1.884% | 0.2549%
2017-11-08 | 12 | 7079 | 130.5496 | 1.844% | 17.6596 | 0.2495% | 148.2091 | 2.094% | 1240 | 7061.3404 | 6930.7909 | 1.884% | 0.2548%
2017-11-06 | 13 | 7080 | 130.5619 | 1.844% | 17.6609 | 0.2494% | 148.2227 | 2.094% | 1241 | 7062.3391 | 6931.7773 | 1.884% | 0.2548%
2017-10-19 | 17 | 7081 | 130.5741 | 1.844% | 17.6622 | 0.2494% | 148.2363 | 2.093% | 1242 | 7063.3378 | 6932.7637 | 1.883% | 0.2548%
2017-11-07 | 14 | 7081 | 130.5741 | 1.844% | 17.6622 | 0.2494% | 148.2363 | 2.093% | 1243 | 7063.3378 | 6932.7637 | 1.883% | 0.2548%
2017-11-25 | 2 | 7083 | 130.5987 | 1.844% | 17.6648 | 0.2494% | 148.2635 | 2.093% | 1244 | 7065.3352 | 6934.7365 | 1.883% | 0.2547%
2017-11-13 | 12 | 7087 | 130.6478 | 1.843% | 17.67 | 0.2493% | 148.3178 | 2.093% | 1245 | 7069.33 | 6938.6822 | 1.883% | 0.2547%
2017-11-18 | 11 | 7087 | 130.6478 | 1.843% | 17.67 | 0.2493% | 148.3178 | 2.093% | 1246 | 7069.33 | 6938.6822 | 1.883% | 0.2547%
2017-09-22 | 9 | 7088 | 130.6601 | 1.843% | 17.6713 | 0.2493% | 148.3313 | 2.093% | 1247 | 7070.3287 | 6939.6687 | 1.883% | 0.2546%
2017-11-28 | 23 | 7088 | 130.6601 | 1.843% | 17.6713 | 0.2493% | 148.3313 | 2.093% | 1248 | 7070.3287 | 6939.6687 | 1.883% | 0.2546%
2017-10-03 | 22 | 7089 | 130.6723 | 1.843% | 17.6726 | 0.2493% | 148.3449 | 2.093% | 1249 | 7071.3274 | 6940.6551 | 1.883% | 0.2546%
2017-09-04 | 11 | 7090 | 130.6846 | 1.843% | 17.6739 | 0.2493% | 148.3585 | 2.093% | 1250 | 7072.3261 | 6941.6415 | 1.883% | 0.2546%
2017-10-26 | 9 | 7090 | 130.6846 | 1.843% | 17.6739 | 0.2493% | 148.3585 | 2.093% | 1251 | 7072.3261 | 6941.6415 | 1.883% | 0.2546%
2017-11-30 | 22 | 7095 | 130.746 | 1.843% | 17.6804 | 0.2492% | 148.4264 | 2.092% | 1252 | 7077.3196 | 6946.5736 | 1.882% | 0.2545%
2017-11-25 | 1 | 7097 | 130.7705 | 1.843% | 17.683 | 0.2492% | 148.4535 | 2.092% | 1253 | 7079.317 | 6948.5465 | 1.882% | 0.2545%
2017-11-08 | 13 | 7100 | 130.8074 | 1.842% | 17.6869 | 0.2491% | 148.4942 | 2.091% | 1254 | 7082.3131 | 6951.5058 | 1.882% | 0.2544%
2017-10-17 | 20 | 7102 | 130.8319 | 1.842% | 17.6895 | 0.2491% | 148.5214 | 2.091% | 1255 | 7084.3105 | 6953.4786 | 1.882% | 0.2544%
2017-10-22 | 21 | 7102 | 130.8319 | 1.842% | 17.6895 | 0.2491% | 148.5214 | 2.091% | 1256 | 7084.3105 | 6953.4786 | 1.882% | 0.2544%
2017-11-21 | 13 | 7102 | 130.8319 | 1.842% | 17.6895 | 0.2491% | 148.5214 | 2.091% | 1257 | 7084.3105 | 6953.4786 | 1.882% | 0.2544%
2017-10-16 | 10 | 7103 | 130.8442 | 1.842% | 17.6908 | 0.2491% | 148.535 | 2.091% | 1258 | 7085.3092 | 6954.465 | 1.881% | 0.2544%
2017-11-10 | 18 | 7103 | 130.8442 | 1.842% | 17.6908 | 0.2491% | 148.535 | 2.091% | 1259 | 7085.3092 | 6954.465 | 1.881% | 0.2544%
2017-09-12 | 10 | 7104 | 130.8565 | 1.842% | 17.6921 | 0.249% | 148.5485 | 2.091% | 1260 | 7086.3079 | 6955.4515 | 1.881% | 0.2544%
2017-11-20 | 17 | 7106 | 130.881 | 1.842% | 17.6947 | 0.249% | 148.5757 | 2.091% | 1261 | 7088.3053 | 6957.4243 | 1.881% | 0.2543%
2017-10-18 | 20 | 7108 | 130.9056 | 1.842% | 17.6973 | 0.249% | 148.6029 | 2.091% | 1262 | 7090.3027 | 6959.3971 | 1.881% | 0.2543%
2017-11-23 | 20 | 7110 | 130.9301 | 1.841% | 17.6999 | 0.2489% | 148.63 | 2.09% | 1263 | 7092.3001 | 6961.37 | 1.881% | 0.2543%
2017-10-13 | 10 | 7112 | 130.9547 | 1.841% | 17.7025 | 0.2489% | 148.6572 | 2.09% | 1264 | 7094.2975 | 6963.3428 | 1.881% | 0.2542%
2017-09-14 | 8 | 7114 | 130.9792 | 1.841% | 17.7051 | 0.2489% | 148.6843 | 2.09% | 1265 | 7096.2949 | 6965.3157 | 1.88% | 0.2542%
2017-11-02 | 15 | 7114 | 130.9792 | 1.841% | 17.7051 | 0.2489% | 148.6843 | 2.09% | 1266 | 7096.2949 | 6965.3157 | 1.88% | 0.2542%
2017-11-01 | 7 | 7116 | 131.0038 | 1.841% | 17.7077 | 0.2488% | 148.7115 | 2.09% | 1267 | 7098.2923 | 6967.2885 | 1.88% | 0.2542%
2017-09-24 | 23 | 7117 | 131.016 | 1.841% | 17.709 | 0.2488% | 148.725 | 2.09% | 1268 | 7099.291 | 6968.275 | 1.88% | 0.2541%
2017-11-23 | 24 | 7118 | 131.0283 | 1.841% | 17.7103 | 0.2488% | 148.7386 | 2.09% | 1269 | 7100.2897 | 6969.2614 | 1.88% | 0.2541%
2017-11-24 | 12 | 7119 | 131.0406 | 1.841% | 17.7116 | 0.2488% | 148.7522 | 2.09% | 1270 | 7101.2884 | 6970.2478 | 1.88% | 0.2541%
2017-09-16 | 10 | 7120 | 131.0529 | 1.841% | 17.7129 | 0.2488% | 148.7658 | 2.089% | 1271 | 7102.2871 | 6971.2342 | 1.88% | 0.2541%
2017-09-15 | 9 | 7123 | 131.0897 | 1.84% | 17.7168 | 0.2487% | 148.8065 | 2.089% | 1272 | 7105.2832 | 6974.1935 | 1.88% | 0.254%
2017-10-19 | 21 | 7125 | 131.1142 | 1.84% | 17.7194 | 0.2487% | 148.8336 | 2.089% | 1273 | 7107.2806 | 6976.1664 | 1.879% | 0.254%
2017-11-01 | 21 | 7127 | 131.1388 | 1.84% | 17.722 | 0.2487% | 148.8608 | 2.089% | 1274 | 7109.278 | 6978.1392 | 1.879% | 0.254%
2017-09-07 | 12 | 7129 | 131.1633 | 1.84% | 17.7246 | 0.2486% | 148.888 | 2.088% | 1275 | 7111.2754 | 6980.112 | 1.879% | 0.2539%
2017-11-08 | 14 | 7129 | 131.1633 | 1.84% | 17.7246 | 0.2486% | 148.888 | 2.088% | 1276 | 7111.2754 | 6980.112 | 1.879% | 0.2539%
2017-11-09 | 22 | 7129 | 131.1633 | 1.84% | 17.7246 | 0.2486% | 148.888 | 2.088% | 1277 | 7111.2754 | 6980.112 | 1.879% | 0.2539%
2017-11-17 | 12 | 7129 | 131.1633 | 1.84% | 17.7246 | 0.2486% | 148.888 | 2.088% | 1278 | 7111.2754 | 6980.112 | 1.879% | 0.2539%
2017-09-30 | 13 | 7133 | 131.2125 | 1.84% | 17.7298 | 0.2486% | 148.9423 | 2.088% | 1279 | 7115.2702 | 6984.0577 | 1.879% | 0.2539%
2017-10-31 | 11 | 7138 | 131.2738 | 1.839% | 17.7363 | 0.2485% | 149.0101 | 2.088% | 1280 | 7120.2637 | 6988.9899 | 1.878% | 0.2538%
2017-10-22 | 19 | 7142 | 131.3229 | 1.839% | 17.7415 | 0.2484% | 149.0644 | 2.087% | 1281 | 7124.2585 | 6992.9356 | 1.878% | 0.2537%
2017-09-06 | 8 | 7143 | 131.3352 | 1.839% | 17.7428 | 0.2484% | 149.078 | 2.087% | 1282 | 7125.2572 | 6993.922 | 1.878% | 0.2537%
2017-10-18 | 9 | 7143 | 131.3352 | 1.839% | 17.7428 | 0.2484% | 149.078 | 2.087% | 1283 | 7125.2572 | 6993.922 | 1.878% | 0.2537%
2017-11-07 | 17 | 7144 | 131.3475 | 1.839% | 17.7441 | 0.2484% | 149.0916 | 2.087% | 1284 | 7126.2559 | 6994.9084 | 1.878% | 0.2537%
2017-10-26 | 21 | 7150 | 131.4211 | 1.838% | 17.7519 | 0.2483% | 149.1731 | 2.086% | 1285 | 7132.2481 | 7000.8269 | 1.877% | 0.2536%
2017-10-10 | 1 | 7152 | 131.4457 | 1.838% | 17.7545 | 0.2482% | 149.2002 | 2.086% | 1286 | 7134.2455 | 7002.7998 | 1.877% | 0.2535%
2017-10-14 | 21 | 7154 | 131.4702 | 1.838% | 17.7571 | 0.2482% | 149.2274 | 2.086% | 1287 | 7136.2429 | 7004.7726 | 1.877% | 0.2535%
2017-11-24 | 2 | 7157 | 131.5071 | 1.837% | 17.761 | 0.2482% | 149.2681 | 2.086% | 1288 | 7139.239 | 7007.7319 | 1.877% | 0.2534%
2017-09-30 | 20 | 7159 | 131.5316 | 1.837% | 17.7636 | 0.2481% | 149.2952 | 2.085% | 1289 | 7141.2364 | 7009.7048 | 1.876% | 0.2534%
2017-11-07 | 21 | 7159 | 131.5316 | 1.837% | 17.7636 | 0.2481% | 149.2952 | 2.085% | 1290 | 7141.2364 | 7009.7048 | 1.876% | 0.2534%
2017-11-09 | 15 | 7160 | 131.5439 | 1.837% | 17.7649 | 0.2481% | 149.3088 | 2.085% | 1291 | 7142.2351 | 7010.6912 | 1.876% | 0.2534%
2017-11-25 | 11 | 7161 | 131.5562 | 1.837% | 17.7662 | 0.2481% | 149.3224 | 2.085% | 1292 | 7143.2338 | 7011.6776 | 1.876% | 0.2534%
2017-10-25 | 20 | 7162 | 131.5684 | 1.837% | 17.7675 | 0.2481% | 149.336 | 2.085% | 1293 | 7144.2325 | 7012.664 | 1.876% | 0.2534%
2017-11-29 | 6 | 7165 | 131.6053 | 1.837% | 17.7714 | 0.248% | 149.3767 | 2.085% | 1294 | 7147.2286 | 7015.6233 | 1.876% | 0.2533%
2017-10-26 | 20 | 7167 | 131.6298 | 1.837% | 17.774 | 0.248% | 149.4038 | 2.085% | 1295 | 7149.226 | 7017.5962 | 1.876% | 0.2533%
2017-10-26 | 8 | 7168 | 131.6421 | 1.837% | 17.7753 | 0.248% | 149.4174 | 2.085% | 1296 | 7150.2247 | 7018.5826 | 1.876% | 0.2533%
2017-11-25 | 3 | 7168 | 131.6421 | 1.837% | 17.7753 | 0.248% | 149.4174 | 2.085% | 1297 | 7150.2247 | 7018.5826 | 1.876% | 0.2533%
2017-11-08 | 15 | 7173 | 131.7035 | 1.836% | 17.7818 | 0.2479% | 149.4853 | 2.084% | 1298 | 7155.2182 | 7023.5147 | 1.875% | 0.2532%
2017-09-18 | 9 | 7174 | 131.7157 | 1.836% | 17.7831 | 0.2479% | 149.4989 | 2.084% | 1299 | 7156.2169 | 7024.5011 | 1.875% | 0.2532%
2017-10-14 | 16 | 7174 | 131.7157 | 1.836% | 17.7831 | 0.2479% | 149.4989 | 2.084% | 1300 | 7156.2169 | 7024.5011 | 1.875% | 0.2532%
2017-11-14 | 12 | 7175 | 131.728 | 1.836% | 17.7844 | 0.2479% | 149.5125 | 2.084% | 1301 | 7157.2156 | 7025.4875 | 1.875% | 0.2531%
2017-09-27 | 7 | 7176 | 131.7403 | 1.836% | 17.7857 | 0.2479% | 149.526 | 2.084% | 1302 | 7158.2143 | 7026.474 | 1.875% | 0.2531%
2017-09-29 | 10 | 7178 | 131.7648 | 1.836% | 17.7883 | 0.2478% | 149.5532 | 2.083% | 1303 | 7160.2117 | 7028.4468 | 1.875% | 0.2531%
2017-11-22 | 18 | 7182 | 131.8139 | 1.835% | 17.7936 | 0.2478% | 149.6075 | 2.083% | 1304 | 7164.2064 | 7032.3925 | 1.874% | 0.253%
2017-09-09 | 14 | 7184 | 131.8385 | 1.835% | 17.7962 | 0.2477% | 149.6346 | 2.083% | 1305 | 7166.2038 | 7034.3654 | 1.874% | 0.253%
2017-10-16 | 15 | 7185 | 131.8508 | 1.835% | 17.7975 | 0.2477% | 149.6482 | 2.083% | 1306 | 7167.2025 | 7035.3518 | 1.874% | 0.253%
2017-11-20 | 13 | 7185 | 131.8508 | 1.835% | 17.7975 | 0.2477% | 149.6482 | 2.083% | 1307 | 7167.2025 | 7035.3518 | 1.874% | 0.253%
2017-11-24 | 24 | 7186 | 131.863 | 1.835% | 17.7988 | 0.2477% | 149.6618 | 2.083% | 1308 | 7168.2012 | 7036.3382 | 1.874% | 0.253%
2017-11-01 | 19 | 7187 | 131.8753 | 1.835% | 17.8001 | 0.2477% | 149.6754 | 2.083% | 1309 | 7169.1999 | 7037.3246 | 1.874% | 0.2529%
2017-11-02 | 16 | 7188 | 131.8876 | 1.835% | 17.8014 | 0.2477% | 149.6889 | 2.082% | 1310 | 7170.1986 | 7038.3111 | 1.874% | 0.2529%
2017-10-22 | 18 | 7189 | 131.8999 | 1.835% | 17.8027 | 0.2476% | 149.7025 | 2.082% | 1311 | 7171.1973 | 7039.2975 | 1.874% | 0.2529%
2017-10-16 | 20 | 7192 | 131.9367 | 1.834% | 17.8066 | 0.2476% | 149.7432 | 2.082% | 1312 | 7174.1934 | 7042.2568 | 1.874% | 0.2529%
2017-11-23 | 23 | 7193 | 131.949 | 1.834% | 17.8079 | 0.2476% | 149.7568 | 2.082% | 1313 | 7175.1921 | 7043.2432 | 1.873% | 0.2528%
2017-11-10 | 23 | 7198 | 132.0103 | 1.834% | 17.8144 | 0.2475% | 149.8247 | 2.081% | 1314 | 7180.1856 | 7048.1753 | 1.873% | 0.2528%
2017-11-09 | 16 | 7199 | 132.0226 | 1.834% | 17.8157 | 0.2475% | 149.8383 | 2.081% | 1315 | 7181.1843 | 7049.1617 | 1.873% | 0.2527%
2017-09-11 | 21 | 7201 | 132.0472 | 1.834% | 17.8183 | 0.2474% | 149.8654 | 2.081% | 1316 | 7183.1817 | 7051.1346 | 1.873% | 0.2527%
2017-11-26 | 9 | 7201 | 132.0472 | 1.834% | 17.8183 | 0.2474% | 149.8654 | 2.081% | 1317 | 7183.1817 | 7051.1346 | 1.873% | 0.2527%
2017-09-13 | 10 | 7205 | 132.0963 | 1.833% | 17.8235 | 0.2474% | 149.9197 | 2.081% | 1318 | 7187.1765 | 7055.0803 | 1.872% | 0.2526%
2017-11-11 | 4 | 7205 | 132.0963 | 1.833% | 17.8235 | 0.2474% | 149.9197 | 2.081% | 1319 | 7187.1765 | 7055.0803 | 1.872% | 0.2526%
2017-11-22 | 22 | 7206 | 132.1085 | 1.833% | 17.8248 | 0.2474% | 149.9333 | 2.081% | 1320 | 7188.1752 | 7056.0667 | 1.872% | 0.2526%
2017-11-09 | 14 | 7208 | 132.1331 | 1.833% | 17.8274 | 0.2473% | 149.9605 | 2.08% | 1321 | 7190.1726 | 7058.0395 | 1.872% | 0.2526%
2017-11-16 | 18 | 7212 | 132.1822 | 1.833% | 17.8326 | 0.2473% | 150.0148 | 2.08% | 1322 | 7194.1674 | 7061.9852 | 1.872% | 0.2525%
2017-09-11 | 20 | 7215 | 132.219 | 1.833% | 17.8365 | 0.2472% | 150.0555 | 2.08% | 1323 | 7197.1635 | 7064.9445 | 1.871% | 0.2525%
2017-10-18 | 8 | 7215 | 132.219 | 1.833% | 17.8365 | 0.2472% | 150.0555 | 2.08% | 1324 | 7197.1635 | 7064.9445 | 1.871% | 0.2525%
2017-11-23 | 21 | 7220 | 132.2804 | 1.832% | 17.843 | 0.2471% | 150.1234 | 2.079% | 1325 | 7202.157 | 7069.8766 | 1.871% | 0.2524%
2017-09-08 | 13 | 7222 | 132.3049 | 1.832% | 17.8456 | 0.2471% | 150.1505 | 2.079% | 1326 | 7204.1544 | 7071.8495 | 1.871% | 0.2523%
2017-10-23 | 12 | 7222 | 132.3049 | 1.832% | 17.8456 | 0.2471% | 150.1505 | 2.079% | 1327 | 7204.1544 | 7071.8495 | 1.871% | 0.2523%
2017-09-20 | 24 | 7224 | 132.3295 | 1.832% | 17.8482 | 0.2471% | 150.1777 | 2.079% | 1328 | 7206.1518 | 7073.8223 | 1.871% | 0.2523%
2017-10-13 | 11 | 7224 | 132.3295 | 1.832% | 17.8482 | 0.2471% | 150.1777 | 2.079% | 1329 | 7206.1518 | 7073.8223 | 1.871% | 0.2523%
2017-11-27 | 3 | 7225 | 132.3418 | 1.832% | 17.8495 | 0.2471% | 150.1913 | 2.079% | 1330 | 7207.1505 | 7074.8087 | 1.871% | 0.2523%
2017-11-26 | 23 | 7228 | 132.3786 | 1.831% | 17.8534 | 0.247% | 150.232 | 2.078% | 1331 | 7210.1466 | 7077.768 | 1.87% | 0.2522%
2017-11-10 | 10 | 7230 | 132.4031 | 1.831% | 17.856 | 0.247% | 150.2591 | 2.078% | 1332 | 7212.144 | 7079.7409 | 1.87% | 0.2522%
2017-09-26 | 24 | 7232 | 132.4277 | 1.831% | 17.8586 | 0.2469% | 150.2863 | 2.078% | 1333 | 7214.1414 | 7081.7137 | 1.87% | 0.2522%
2017-11-09 | 13 | 7234 | 132.4522 | 1.831% | 17.8612 | 0.2469% | 150.3134 | 2.078% | 1334 | 7216.1388 | 7083.6866 | 1.87% | 0.2521%
2017-09-09 | 20 | 7236 | 132.4768 | 1.831% | 17.8638 | 0.2469% | 150.3406 | 2.078% | 1335 | 7218.1362 | 7085.6594 | 1.87% | 0.2521%
2017-10-24 | 14 | 7238 | 132.5013 | 1.831% | 17.8664 | 0.2468% | 150.3677 | 2.077% | 1336 | 7220.1336 | 7087.6323 | 1.869% | 0.2521%
2017-09-09 | 21 | 7241 | 132.5382 | 1.83% | 17.8703 | 0.2468% | 150.4085 | 2.077% | 1337 | 7223.1297 | 7090.5915 | 1.869% | 0.252%
2017-10-24 | 21 | 7241 | 132.5382 | 1.83% | 17.8703 | 0.2468% | 150.4085 | 2.077% | 1338 | 7223.1297 | 7090.5915 | 1.869% | 0.252%
2017-11-03 | 15 | 7241 | 132.5382 | 1.83% | 17.8703 | 0.2468% | 150.4085 | 2.077% | 1339 | 7223.1297 | 7090.5915 | 1.869% | 0.252%
2017-11-06 | 21 | 7241 | 132.5382 | 1.83% | 17.8703 | 0.2468% | 150.4085 | 2.077% | 1340 | 7223.1297 | 7090.5915 | 1.869% | 0.252%
2017-09-30 | 19 | 7242 | 132.5504 | 1.83% | 17.8716 | 0.2468% | 150.4221 | 2.077% | 1341 | 7224.1284 | 7091.5779 | 1.869% | 0.252%
2017-11-11 | 13 | 7242 | 132.5504 | 1.83% | 17.8716 | 0.2468% | 150.4221 | 2.077% | 1342 | 7224.1284 | 7091.5779 | 1.869% | 0.252%
2017-11-19 | 22 | 7252 | 132.6732 | 1.829% | 17.8846 | 0.2466% | 150.5578 | 2.076% | 1343 | 7234.1154 | 7101.4422 | 1.868% | 0.2518%
2017-11-29 | 22 | 7252 | 132.6732 | 1.829% | 17.8846 | 0.2466% | 150.5578 | 2.076% | 1344 | 7234.1154 | 7101.4422 | 1.868% | 0.2518%
2017-11-09 | 7 | 7254 | 132.6977 | 1.829% | 17.8872 | 0.2466% | 150.585 | 2.076% | 1345 | 7236.1128 | 7103.415 | 1.868% | 0.2518%
2017-09-25 | 10 | 7255 | 132.71 | 1.829% | 17.8885 | 0.2466% | 150.5985 | 2.076% | 1346 | 7237.1115 | 7104.4015 | 1.868% | 0.2518%
2017-10-30 | 12 | 7255 | 132.71 | 1.829% | 17.8885 | 0.2466% | 150.5985 | 2.076% | 1347 | 7237.1115 | 7104.4015 | 1.868% | 0.2518%
2017-11-23 | 7 | 7256 | 132.7223 | 1.829% | 17.8898 | 0.2466% | 150.6121 | 2.076% | 1348 | 7238.1102 | 7105.3879 | 1.868% | 0.2518%
2017-11-14 | 6 | 7257 | 132.7346 | 1.829% | 17.8911 | 0.2465% | 150.6257 | 2.076% | 1349 | 7239.1089 | 7106.3743 | 1.868% | 0.2518%
2017-11-23 | 22 | 7258 | 132.7469 | 1.829% | 17.8924 | 0.2465% | 150.6393 | 2.075% | 1350 | 7240.1076 | 7107.3607 | 1.868% | 0.2517%
2017-11-30 | 11 | 7258 | 132.7469 | 1.829% | 17.8924 | 0.2465% | 150.6393 | 2.075% | 1351 | 7240.1076 | 7107.3607 | 1.868% | 0.2517%
2017-11-16 | 11 | 7261 | 132.7837 | 1.829% | 17.8963 | 0.2465% | 150.68 | 2.075% | 1352 | 7243.1037 | 7110.32 | 1.867% | 0.2517%
2017-11-29 | 18 | 7261 | 132.7837 | 1.829% | 17.8963 | 0.2465% | 150.68 | 2.075% | 1353 | 7243.1037 | 7110.32 | 1.867% | 0.2517%
2017-11-02 | 21 | 7267 | 132.8573 | 1.828% | 17.9041 | 0.2464% | 150.7615 | 2.075% | 1354 | 7249.0959 | 7116.2385 | 1.867% | 0.2516%
2017-11-14 | 17 | 7267 | 132.8573 | 1.828% | 17.9041 | 0.2464% | 150.7615 | 2.075% | 1355 | 7249.0959 | 7116.2385 | 1.867% | 0.2516%
2017-11-15 | 12 | 7271 | 132.9064 | 1.828% | 17.9093 | 0.2463% | 150.8158 | 2.074% | 1356 | 7253.0907 | 7120.1842 | 1.867% | 0.2515%
2017-11-29 | 10 | 7273 | 132.931 | 1.828% | 17.9119 | 0.2463% | 150.8429 | 2.074% | 1357 | 7255.0881 | 7122.1571 | 1.866% | 0.2515%
2017-11-06 | 16 | 7275 | 132.9555 | 1.828% | 17.9145 | 0.2462% | 150.8701 | 2.074% | 1358 | 7257.0855 | 7124.1299 | 1.866% | 0.2515%
2017-09-17 | 23 | 7277 | 132.9801 | 1.827% | 17.9171 | 0.2462% | 150.8972 | 2.074% | 1359 | 7259.0829 | 7126.1028 | 1.866% | 0.2514%
2017-10-05 | 11 | 7277 | 132.9801 | 1.827% | 17.9171 | 0.2462% | 150.8972 | 2.074% | 1360 | 7259.0829 | 7126.1028 | 1.866% | 0.2514%
2017-11-06 | 14 | 7278 | 132.9924 | 1.827% | 17.9184 | 0.2462% | 150.9108 | 2.074% | 1361 | 7260.0816 | 7127.0892 | 1.866% | 0.2514%
2017-10-02 | 14 | 7280 | 133.0169 | 1.827% | 17.921 | 0.2462% | 150.9379 | 2.073% | 1362 | 7262.079 | 7129.0621 | 1.866% | 0.2514%
2017-11-06 | 17 | 7284 | 133.066 | 1.827% | 17.9262 | 0.2461% | 150.9922 | 2.073% | 1363 | 7266.0738 | 7133.0078 | 1.865% | 0.2513%
2017-09-17 | 11 | 7285 | 133.0783 | 1.827% | 17.9275 | 0.2461% | 151.0058 | 2.073% | 1364 | 7267.0725 | 7133.9942 | 1.865% | 0.2513%
2017-11-01 | 9 | 7285 | 133.0783 | 1.827% | 17.9275 | 0.2461% | 151.0058 | 2.073% | 1365 | 7267.0725 | 7133.9942 | 1.865% | 0.2513%
2017-11-02 | 18 | 7287 | 133.1028 | 1.827% | 17.9301 | 0.2461% | 151.033 | 2.073% | 1366 | 7269.0699 | 7135.967 | 1.865% | 0.2513%
2017-11-24 | 3 | 7292 | 133.1642 | 1.826% | 17.9367 | 0.246% | 151.1009 | 2.072% | 1367 | 7274.0633 | 7140.8991 | 1.865% | 0.2512%
2017-11-23 | 13 | 7297 | 133.2256 | 1.826% | 17.9432 | 0.2459% | 151.1687 | 2.072% | 1368 | 7279.0568 | 7145.8313 | 1.864% | 0.2511%
2017-09-01 | 8 | 7298 | 133.2379 | 1.826% | 17.9445 | 0.2459% | 151.1823 | 2.072% | 1369 | 7280.0555 | 7146.8177 | 1.864% | 0.2511%
2017-09-29 | 22 | 7298 | 133.2379 | 1.826% | 17.9445 | 0.2459% | 151.1823 | 2.072% | 1370 | 7280.0555 | 7146.8177 | 1.864% | 0.2511%
2017-11-02 | 17 | 7298 | 133.2379 | 1.826% | 17.9445 | 0.2459% | 151.1823 | 2.072% | 1371 | 7280.0555 | 7146.8177 | 1.864% | 0.2511%
2017-11-03 | 20 | 7298 | 133.2379 | 1.826% | 17.9445 | 0.2459% | 151.1823 | 2.072% | 1372 | 7280.0555 | 7146.8177 | 1.864% | 0.2511%
2017-11-28 | 12 | 7300 | 133.2624 | 1.826% | 17.9471 | 0.2459% | 151.2095 | 2.071% | 1373 | 7282.0529 | 7148.7905 | 1.864% | 0.2511%
2017-09-23 | 23 | 7301 | 133.2747 | 1.825% | 17.9484 | 0.2458% | 151.223 | 2.071% | 1374 | 7283.0516 | 7149.777 | 1.864% | 0.251%
2017-09-27 | 24 | 7302 | 133.287 | 1.825% | 17.9497 | 0.2458% | 151.2366 | 2.071% | 1375 | 7284.0503 | 7150.7634 | 1.864% | 0.251%
2017-10-07 | 11 | 7303 | 133.2992 | 1.825% | 17.951 | 0.2458% | 151.2502 | 2.071% | 1376 | 7285.049 | 7151.7498 | 1.864% | 0.251%
2017-09-02 | 12 | 7304 | 133.3115 | 1.825% | 17.9523 | 0.2458% | 151.2638 | 2.071% | 1377 | 7286.0477 | 7152.7362 | 1.864% | 0.251%
2017-10-19 | 20 | 7307 | 133.3483 | 1.825% | 17.9562 | 0.2457% | 151.3045 | 2.071% | 1378 | 7289.0438 | 7155.6955 | 1.864% | 0.2509%
2017-11-06 | 15 | 7309 | 133.3729 | 1.825% | 17.9588 | 0.2457% | 151.3317 | 2.07% | 1379 | 7291.0412 | 7157.6683 | 1.863% | 0.2509%
2017-10-27 | 10 | 7313 | 133.422 | 1.824% | 17.964 | 0.2456% | 151.386 | 2.07% | 1380 | 7295.036 | 7161.614 | 1.863% | 0.2508%
2017-10-16 | 11 | 7314 | 133.4343 | 1.824% | 17.9653 | 0.2456% | 151.3995 | 2.07% | 1381 | 7296.0347 | 7162.6005 | 1.863% | 0.2508%
2017-09-21 | 9 | 7319 | 133.4956 | 1.824% | 17.9718 | 0.2455% | 151.4674 | 2.07% | 1382 | 7301.0282 | 7167.5326 | 1.863% | 0.2507%
2017-10-30 | 19 | 7320 | 133.5079 | 1.824% | 17.9731 | 0.2455% | 151.481 | 2.069% | 1383 | 7302.0269 | 7168.519 | 1.862% | 0.2507%
2017-11-19 | 19 | 7321 | 133.5202 | 1.824% | 17.9744 | 0.2455% | 151.4946 | 2.069% | 1384 | 7303.0256 | 7169.5054 | 1.862% | 0.2507%
2017-11-25 | 4 | 7322 | 133.5325 | 1.824% | 17.9757 | 0.2455% | 151.5081 | 2.069% | 1385 | 7304.0243 | 7170.4919 | 1.862% | 0.2507%
2017-11-30 | 18 | 7322 | 133.5325 | 1.824% | 17.9757 | 0.2455% | 151.5081 | 2.069% | 1386 | 7304.0243 | 7170.4919 | 1.862% | 0.2507%
2017-10-14 | 19 | 7325 | 133.5693 | 1.823% | 17.9796 | 0.2455% | 151.5489 | 2.069% | 1387 | 7307.0204 | 7173.4511 | 1.862% | 0.2506%
2017-11-12 | 21 | 7325 | 133.5693 | 1.823% | 17.9796 | 0.2455% | 151.5489 | 2.069% | 1388 | 7307.0204 | 7173.4511 | 1.862% | 0.2506%
2017-11-15 | 5 | 7326 | 133.5816 | 1.823% | 17.9809 | 0.2454% | 151.5624 | 2.069% | 1389 | 7308.0191 | 7174.4376 | 1.862% | 0.2506%
2017-09-07 | 22 | 7327 | 133.5938 | 1.823% | 17.9822 | 0.2454% | 151.576 | 2.069% | 1390 | 7309.0178 | 7175.424 | 1.862% | 0.2506%
2017-11-09 | 12 | 7327 | 133.5938 | 1.823% | 17.9822 | 0.2454% | 151.576 | 2.069% | 1391 | 7309.0178 | 7175.424 | 1.862% | 0.2506%
2017-09-28 | 9 | 7334 | 133.6798 | 1.823% | 17.9913 | 0.2453% | 151.6711 | 2.068% | 1392 | 7316.0087 | 7182.3289 | 1.861% | 0.2505%
2017-09-05 | 24 | 7335 | 133.692 | 1.823% | 17.9926 | 0.2453% | 151.6846 | 2.068% | 1393 | 7317.0074 | 7183.3154 | 1.861% | 0.2505%
2017-10-16 | 14 | 7336 | 133.7043 | 1.823% | 17.9939 | 0.2453% | 151.6982 | 2.068% | 1394 | 7318.0061 | 7184.3018 | 1.861% | 0.2505%
2017-09-06 | 9 | 7341 | 133.7657 | 1.822% | 18.0004 | 0.2452% | 151.7661 | 2.067% | 1395 | 7322.9996 | 7189.2339 | 1.861% | 0.2504%
2017-11-10 | 8 | 7341 | 133.7657 | 1.822% | 18.0004 | 0.2452% | 151.7661 | 2.067% | 1396 | 7322.9996 | 7189.2339 | 1.861% | 0.2504%
2017-09-02 | 23 | 7342 | 133.778 | 1.822% | 18.0017 | 0.2452% | 151.7797 | 2.067% | 1397 | 7323.9983 | 7190.2203 | 1.861% | 0.2504%
2017-09-24 | 11 | 7342 | 133.778 | 1.822% | 18.0017 | 0.2452% | 151.7797 | 2.067% | 1398 | 7323.9983 | 7190.2203 | 1.861% | 0.2504%
2017-10-22 | 20 | 7343 | 133.7902 | 1.822% | 18.003 | 0.2452% | 151.7932 | 2.067% | 1399 | 7324.997 | 7191.2068 | 1.86% | 0.2503%
2017-11-08 | 16 | 7343 | 133.7902 | 1.822% | 18.003 | 0.2452% | 151.7932 | 2.067% | 1400 | 7324.997 | 7191.2068 | 1.86% | 0.2503%
2017-09-26 | 8 | 7344 | 133.8025 | 1.822% | 18.0043 | 0.2452% | 151.8068 | 2.067% | 1401 | 7325.9957 | 7192.1932 | 1.86% | 0.2503%
2017-11-01 | 20 | 7345 | 133.8148 | 1.822% | 18.0056 | 0.2451% | 151.8204 | 2.067% | 1402 | 7326.9944 | 7193.1796 | 1.86% | 0.2503%
2017-11-03 | 18 | 7345 | 133.8148 | 1.822% | 18.0056 | 0.2451% | 151.8204 | 2.067% | 1403 | 7326.9944 | 7193.1796 | 1.86% | 0.2503%
2017-10-30 | 22 | 7346 | 133.8271 | 1.822% | 18.0069 | 0.2451% | 151.834 | 2.067% | 1404 | 7327.9931 | 7194.166 | 1.86% | 0.2503%
2017-11-20 | 4 | 7348 | 133.8516 | 1.822% | 18.0095 | 0.2451% | 151.8611 | 2.067% | 1405 | 7329.9905 | 7196.1389 | 1.86% | 0.2503%
2017-11-22 | 21 | 7350 | 133.8762 | 1.821% | 18.0121 | 0.2451% | 151.8883 | 2.067% | 1406 | 7331.9879 | 7198.1117 | 1.86% | 0.2502%
2017-11-14 | 23 | 7351 | 133.8884 | 1.821% | 18.0134 | 0.245% | 151.9018 | 2.066% | 1407 | 7332.9866 | 7199.0982 | 1.86% | 0.2502%
2017-10-24 | 15 | 7353 | 133.913 | 1.821% | 18.016 | 0.245% | 151.929 | 2.066% | 1408 | 7334.984 | 7201.071 | 1.86% | 0.2502%
2017-10-13 | 12 | 7354 | 133.9253 | 1.821% | 18.0173 | 0.245% | 151.9426 | 2.066% | 1409 | 7335.9827 | 7202.0574 | 1.86% | 0.2502%
2017-10-23 | 13 | 7356 | 133.9498 | 1.821% | 18.0199 | 0.245% | 151.9697 | 2.066% | 1410 | 7337.9801 | 7204.0303 | 1.859% | 0.2501%
2017-11-03 | 19 | 7356 | 133.9498 | 1.821% | 18.0199 | 0.245% | 151.9697 | 2.066% | 1411 | 7337.9801 | 7204.0303 | 1.859% | 0.2501%
2017-10-03 | 14 | 7358 | 133.9744 | 1.821% | 18.0225 | 0.2449% | 151.9969 | 2.066% | 1412 | 7339.9775 | 7206.0031 | 1.859% | 0.2501%
2017-09-07 | 13 | 7359 | 133.9866 | 1.821% | 18.0238 | 0.2449% | 152.0105 | 2.066% | 1413 | 7340.9762 | 7206.9895 | 1.859% | 0.2501%
2017-10-23 | 22 | 7359 | 133.9866 | 1.821% | 18.0238 | 0.2449% | 152.0105 | 2.066% | 1414 | 7340.9762 | 7206.9895 | 1.859% | 0.2501%
2017-11-09 | 17 | 7359 | 133.9866 | 1.821% | 18.0238 | 0.2449% | 152.0105 | 2.066% | 1415 | 7340.9762 | 7206.9895 | 1.859% | 0.2501%
2017-11-24 | 19 | 7359 | 133.9866 | 1.821% | 18.0238 | 0.2449% | 152.0105 | 2.066% | 1416 | 7340.9762 | 7206.9895 | 1.859% | 0.2501%
2017-11-03 | 16 | 7361 | 134.0112 | 1.821% | 18.0264 | 0.2449% | 152.0376 | 2.065% | 1417 | 7342.9736 | 7208.9624 | 1.859% | 0.2501%
2017-11-10 | 9 | 7361 | 134.0112 | 1.821% | 18.0264 | 0.2449% | 152.0376 | 2.065% | 1418 | 7342.9736 | 7208.9624 | 1.859% | 0.2501%
2017-10-16 | 12 | 7362 | 134.0235 | 1.82% | 18.0277 | 0.2449% | 152.0512 | 2.065% | 1419 | 7343.9723 | 7209.9488 | 1.859% | 0.25%
2017-09-30 | 14 | 7364 | 134.048 | 1.82% | 18.0303 | 0.2448% | 152.0783 | 2.065% | 1420 | 7345.9697 | 7211.9217 | 1.859% | 0.25%
2017-10-14 | 17 | 7366 | 134.0726 | 1.82% | 18.0329 | 0.2448% | 152.1055 | 2.065% | 1421 | 7347.9671 | 7213.8945 | 1.859% | 0.25%
2017-11-10 | 22 | 7369 | 134.1094 | 1.82% | 18.0368 | 0.2448% | 152.1462 | 2.065% | 1422 | 7350.9632 | 7216.8538 | 1.858% | 0.2499%
2017-11-22 | 20 | 7369 | 134.1094 | 1.82% | 18.0368 | 0.2448% | 152.1462 | 2.065% | 1423 | 7350.9632 | 7216.8538 | 1.858% | 0.2499%
2017-10-12 | 7 | 7370 | 134.1217 | 1.82% | 18.0381 | 0.2448% | 152.1598 | 2.065% | 1424 | 7351.9619 | 7217.8402 | 1.858% | 0.2499%
2017-11-22 | 19 | 7371 | 134.1339 | 1.82% | 18.0394 | 0.2447% | 152.1734 | 2.064% | 1425 | 7352.9606 | 7218.8266 | 1.858% | 0.2499%
2017-09-14 | 9 | 7373 | 134.1585 | 1.82% | 18.042 | 0.2447% | 152.2005 | 2.064% | 1426 | 7354.958 | 7220.7995 | 1.858% | 0.2499%
2017-11-15 | 23 | 7374 | 134.1708 | 1.82% | 18.0433 | 0.2447% | 152.2141 | 2.064% | 1427 | 7355.9567 | 7221.7859 | 1.858% | 0.2498%
2017-11-21 | 21 | 7375 | 134.183 | 1.819% | 18.0446 | 0.2447% | 152.2277 | 2.064% | 1428 | 7356.9554 | 7222.7723 | 1.858% | 0.2498%
2017-11-26 | 19 | 7385 | 134.3058 | 1.819% | 18.0576 | 0.2445% | 152.3634 | 2.063% | 1429 | 7366.9424 | 7232.6366 | 1.857% | 0.2497%
2017-09-12 | 23 | 7386 | 134.3181 | 1.819% | 18.0589 | 0.2445% | 152.377 | 2.063% | 1430 | 7367.9411 | 7233.623 | 1.857% | 0.2497%
2017-10-04 | 22 | 7387 | 134.3304 | 1.818% | 18.0602 | 0.2445% | 152.3906 | 2.063% | 1431 | 7368.9398 | 7234.6094 | 1.857% | 0.2496%
2017-11-16 | 22 | 7388 | 134.3426 | 1.818% | 18.0615 | 0.2445% | 152.4042 | 2.063% | 1432 | 7369.9385 | 7235.5958 | 1.857% | 0.2496%
2017-09-09 | 15 | 7391 | 134.3795 | 1.818% | 18.0654 | 0.2444% | 152.4449 | 2.063% | 1433 | 7372.9346 | 7238.5551 | 1.856% | 0.2496%
2017-10-04 | 13 | 7391 | 134.3795 | 1.818% | 18.0654 | 0.2444% | 152.4449 | 2.063% | 1434 | 7372.9346 | 7238.5551 | 1.856% | 0.2496%
2017-11-13 | 11 | 7391 | 134.3795 | 1.818% | 18.0654 | 0.2444% | 152.4449 | 2.063% | 1435 | 7372.9346 | 7238.5551 | 1.856% | 0.2496%
2017-11-18 | 2 | 7391 | 134.3795 | 1.818% | 18.0654 | 0.2444% | 152.4449 | 2.063% | 1436 | 7372.9346 | 7238.5551 | 1.856% | 0.2496%
2017-09-16 | 23 | 7392 | 134.3917 | 1.818% | 18.0667 | 0.2444% | 152.4585 | 2.062% | 1437 | 7373.9333 | 7239.5415 | 1.856% | 0.2496%
2017-10-06 | 11 | 7392 | 134.3917 | 1.818% | 18.0667 | 0.2444% | 152.4585 | 2.062% | 1438 | 7373.9333 | 7239.5415 | 1.856% | 0.2496%
2017-11-13 | 22 | 7392 | 134.3917 | 1.818% | 18.0667 | 0.2444% | 152.4585 | 2.062% | 1439 | 7373.9333 | 7239.5415 | 1.856% | 0.2496%
2017-11-17 | 18 | 7399 | 134.4777 | 1.818% | 18.0759 | 0.2443% | 152.5535 | 2.062% | 1440 | 7380.9241 | 7246.4465 | 1.856% | 0.2494%
2017-09-12 | 11 | 7400 | 134.4899 | 1.817% | 18.0772 | 0.2443% | 152.5671 | 2.062% | 1441 | 7381.9228 | 7247.4329 | 1.856% | 0.2494%
2017-11-02 | 19 | 7403 | 134.5268 | 1.817% | 18.0811 | 0.2442% | 152.6078 | 2.061% | 1442 | 7384.9189 | 7250.3922 | 1.855% | 0.2494%
2017-11-18 | 1 | 7403 | 134.5268 | 1.817% | 18.0811 | 0.2442% | 152.6078 | 2.061% | 1443 | 7384.9189 | 7250.3922 | 1.855% | 0.2494%
2017-10-13 | 21 | 7405 | 134.5513 | 1.817% | 18.0837 | 0.2442% | 152.635 | 2.061% | 1444 | 7386.9163 | 7252.365 | 1.855% | 0.2493%
2017-10-14 | 18 | 7406 | 134.5636 | 1.817% | 18.085 | 0.2442% | 152.6485 | 2.061% | 1445 | 7387.915 | 7253.3515 | 1.855% | 0.2493%
2017-10-16 | 13 | 7408 | 134.5881 | 1.817% | 18.0876 | 0.2442% | 152.6757 | 2.061% | 1446 | 7389.9124 | 7255.3243 | 1.855% | 0.2493%
2017-10-27 | 7 | 7408 | 134.5881 | 1.817% | 18.0876 | 0.2442% | 152.6757 | 2.061% | 1447 | 7389.9124 | 7255.3243 | 1.855% | 0.2493%
2017-11-14 | 11 | 7409 | 134.6004 | 1.817% | 18.0889 | 0.2441% | 152.6893 | 2.061% | 1448 | 7390.9111 | 7256.3107 | 1.855% | 0.2493%
2017-10-15 | 22 | 7414 | 134.6618 | 1.816% | 18.0954 | 0.2441% | 152.7571 | 2.06% | 1449 | 7395.9046 | 7261.2429 | 1.855% | 0.2492%
2017-11-12 | 18 | 7414 | 134.6618 | 1.816% | 18.0954 | 0.2441% | 152.7571 | 2.06% | 1450 | 7395.9046 | 7261.2429 | 1.855% | 0.2492%
2017-11-24 | 23 | 7414 | 134.6618 | 1.816% | 18.0954 | 0.2441% | 152.7571 | 2.06% | 1451 | 7395.9046 | 7261.2429 | 1.855% | 0.2492%
2017-09-05 | 9 | 7417 | 134.6986 | 1.816% | 18.0993 | 0.244% | 152.7979 | 2.06% | 1452 | 7398.9007 | 7264.2021 | 1.854% | 0.2492%
2017-10-24 | 18 | 7417 | 134.6986 | 1.816% | 18.0993 | 0.244% | 152.7979 | 2.06% | 1453 | 7398.9007 | 7264.2021 | 1.854% | 0.2492%
2017-11-10 | 19 | 7422 | 134.76 | 1.816% | 18.1058 | 0.2439% | 152.8658 | 2.06% | 1454 | 7403.8942 | 7269.1342 | 1.854% | 0.2491%
2017-10-09 | 7 | 7424 | 134.7845 | 1.816% | 18.1084 | 0.2439% | 152.8929 | 2.059% | 1455 | 7405.8916 | 7271.1071 | 1.854% | 0.249%
2017-11-10 | 21 | 7427 | 134.8214 | 1.815% | 18.1123 | 0.2439% | 152.9336 | 2.059% | 1456 | 7408.8877 | 7274.0664 | 1.853% | 0.249%
2017-09-03 | 12 | 7428 | 134.8336 | 1.815% | 18.1136 | 0.2439% | 152.9472 | 2.059% | 1457 | 7409.8864 | 7275.0528 | 1.853% | 0.249%
2017-10-24 | 19 | 7428 | 134.8336 | 1.815% | 18.1136 | 0.2439% | 152.9472 | 2.059% | 1458 | 7409.8864 | 7275.0528 | 1.853% | 0.249%
2017-11-09 | 11 | 7430 | 134.8582 | 1.815% | 18.1162 | 0.2438% | 152.9744 | 2.059% | 1459 | 7411.8838 | 7277.0256 | 1.853% | 0.249%
2017-09-26 | 9 | 7433 | 134.895 | 1.815% | 18.1201 | 0.2438% | 153.0151 | 2.059% | 1460 | 7414.8799 | 7279.9849 | 1.853% | 0.2489%
2017-11-01 | 8 | 7434 | 134.9073 | 1.815% | 18.1214 | 0.2438% | 153.0287 | 2.058% | 1461 | 7415.8786 | 7280.9713 | 1.853% | 0.2489%
2017-09-09 | 19 | 7435 | 134.9196 | 1.815% | 18.1227 | 0.2437% | 153.0422 | 2.058% | 1462 | 7416.8773 | 7281.9578 | 1.853% | 0.2489%
2017-11-21 | 12 | 7436 | 134.9318 | 1.815% | 18.124 | 0.2437% | 153.0558 | 2.058% | 1463 | 7417.876 | 7282.9442 | 1.853% | 0.2489%
2017-11-30 | 21 | 7436 | 134.9318 | 1.815% | 18.124 | 0.2437% | 153.0558 | 2.058% | 1464 | 7417.876 | 7282.9442 | 1.853% | 0.2489%
2017-10-11 | 24 | 7442 | 135.0055 | 1.814% | 18.1318 | 0.2436% | 153.1373 | 2.058% | 1465 | 7423.8682 | 7288.8627 | 1.852% | 0.2488%
2017-11-18 | 3 | 7442 | 135.0055 | 1.814% | 18.1318 | 0.2436% | 153.1373 | 2.058% | 1466 | 7423.8682 | 7288.8627 | 1.852% | 0.2488%
2017-11-19 | 21 | 7442 | 135.0055 | 1.814% | 18.1318 | 0.2436% | 153.1373 | 2.058% | 1467 | 7423.8682 | 7288.8627 | 1.852% | 0.2488%
2017-11-09 | 8 | 7444 | 135.03 | 1.814% | 18.1344 | 0.2436% | 153.1644 | 2.058% | 1468 | 7425.8656 | 7290.8356 | 1.852% | 0.2487%
2017-11-27 | 12 | 7445 | 135.0423 | 1.814% | 18.1357 | 0.2436% | 153.178 | 2.057% | 1469 | 7426.8643 | 7291.822 | 1.852% | 0.2487%
2017-11-03 | 17 | 7448 | 135.0791 | 1.814% | 18.1396 | 0.2435% | 153.2187 | 2.057% | 1470 | 7429.8604 | 7294.7813 | 1.852% | 0.2487%
2017-10-14 | 20 | 7449 | 135.0914 | 1.814% | 18.1409 | 0.2435% | 153.2323 | 2.057% | 1471 | 7430.8591 | 7295.7677 | 1.852% | 0.2486%
2017-09-19 | 10 | 7450 | 135.1037 | 1.813% | 18.1422 | 0.2435% | 153.2459 | 2.057% | 1472 | 7431.8578 | 7296.7541 | 1.852% | 0.2486%
2017-11-19 | 20 | 7450 | 135.1037 | 1.813% | 18.1422 | 0.2435% | 153.2459 | 2.057% | 1473 | 7431.8578 | 7296.7541 | 1.852% | 0.2486%
2017-11-09 | 10 | 7452 | 135.1282 | 1.813% | 18.1448 | 0.2435% | 153.273 | 2.057% | 1474 | 7433.8552 | 7298.727 | 1.851% | 0.2486%
2017-11-10 | 20 | 7454 | 135.1528 | 1.813% | 18.1474 | 0.2435% | 153.3002 | 2.057% | 1475 | 7435.8526 | 7300.6998 | 1.851% | 0.2486%
2017-11-09 | 21 | 7456 | 135.1773 | 1.813% | 18.15 | 0.2434% | 153.3273 | 2.056% | 1476 | 7437.85 | 7302.6727 | 1.851% | 0.2485%
2017-11-26 | 22 | 7461 | 135.2387 | 1.813% | 18.1565 | 0.2434% | 153.3952 | 2.056% | 1477 | 7442.8435 | 7307.6048 | 1.851% | 0.2485%
2017-11-09 | 9 | 7462 | 135.251 | 1.813% | 18.1578 | 0.2433% | 153.4088 | 2.056% | 1478 | 7443.8422 | 7308.5912 | 1.851% | 0.2484%
2017-11-07 | 20 | 7465 | 135.2878 | 1.812% | 18.1617 | 0.2433% | 153.4495 | 2.056% | 1479 | 7446.8383 | 7311.5505 | 1.85% | 0.2484%
2017-10-24 | 16 | 7466 | 135.3001 | 1.812% | 18.163 | 0.2433% | 153.4631 | 2.055% | 1480 | 7447.837 | 7312.5369 | 1.85% | 0.2484%
2017-09-27 | 8 | 7471 | 135.3615 | 1.812% | 18.1695 | 0.2432% | 153.531 | 2.055% | 1481 | 7452.8305 | 7317.469 | 1.85% | 0.2483%
2017-10-03 | 15 | 7474 | 135.3983 | 1.812% | 18.1734 | 0.2432% | 153.5717 | 2.055% | 1482 | 7455.8266 | 7320.4283 | 1.85% | 0.2483%
2017-10-23 | 17 | 7476 | 135.4228 | 1.811% | 18.176 | 0.2431% | 153.5989 | 2.055% | 1483 | 7457.824 | 7322.4011 | 1.849% | 0.2482%
2017-11-13 | 7 | 7476 | 135.4228 | 1.811% | 18.176 | 0.2431% | 153.5989 | 2.055% | 1484 | 7457.824 | 7322.4011 | 1.849% | 0.2482%
2017-09-06 | 22 | 7477 | 135.4351 | 1.811% | 18.1773 | 0.2431% | 153.6124 | 2.054% | 1485 | 7458.8227 | 7323.3876 | 1.849% | 0.2482%
2017-11-07 | 18 | 7479 | 135.4597 | 1.811% | 18.1799 | 0.2431% | 153.6396 | 2.054% | 1486 | 7460.8201 | 7325.3604 | 1.849% | 0.2482%
2017-11-12 | 11 | 7480 | 135.4719 | 1.811% | 18.1812 | 0.2431% | 153.6532 | 2.054% | 1487 | 7461.8188 | 7326.3468 | 1.849% | 0.2482%
2017-10-23 | 16 | 7481 | 135.4842 | 1.811% | 18.1825 | 0.243% | 153.6667 | 2.054% | 1488 | 7462.8175 | 7327.3333 | 1.849% | 0.2481%
2017-09-18 | 10 | 7482 | 135.4965 | 1.811% | 18.1838 | 0.243% | 153.6803 | 2.054% | 1489 | 7463.8162 | 7328.3197 | 1.849% | 0.2481%
2017-11-08 | 22 | 7486 | 135.5456 | 1.811% | 18.189 | 0.243% | 153.7346 | 2.054% | 1490 | 7467.811 | 7332.2654 | 1.849% | 0.2481%
2017-11-29 | 21 | 7486 | 135.5456 | 1.811% | 18.189 | 0.243% | 153.7346 | 2.054% | 1491 | 7467.811 | 7332.2654 | 1.849% | 0.2481%
2017-11-27 | 4 | 7488 | 135.5701 | 1.81% | 18.1916 | 0.2429% | 153.7618 | 2.053% | 1492 | 7469.8084 | 7334.2382 | 1.848% | 0.248%
2017-10-13 | 13 | 7490 | 135.5947 | 1.81% | 18.1942 | 0.2429% | 153.7889 | 2.053% | 1493 | 7471.8058 | 7336.2111 | 1.848% | 0.248%
2017-11-24 | 20 | 7492 | 135.6192 | 1.81% | 18.1968 | 0.2429% | 153.8161 | 2.053% | 1494 | 7473.8032 | 7338.1839 | 1.848% | 0.248%
2017-09-29 | 11 | 7495 | 135.6561 | 1.81% | 18.2007 | 0.2428% | 153.8568 | 2.053% | 1495 | 7476.7993 | 7341.1432 | 1.848% | 0.2479%
2017-11-11 | 5 | 7499 | 135.7052 | 1.81% | 18.2059 | 0.2428% | 153.9111 | 2.052% | 1496 | 7480.7941 | 7345.0889 | 1.848% | 0.2479%
2017-11-12 | 2 | 7502 | 135.742 | 1.809% | 18.2098 | 0.2427% | 153.9518 | 2.052% | 1497 | 7483.7902 | 7348.0482 | 1.847% | 0.2478%
2017-11-21 | 18 | 7502 | 135.742 | 1.809% | 18.2098 | 0.2427% | 153.9518 | 2.052% | 1498 | 7483.7902 | 7348.0482 | 1.847% | 0.2478%
2017-09-08 | 21 | 7505 | 135.7788 | 1.809% | 18.2137 | 0.2427% | 153.9926 | 2.052% | 1499 | 7486.7863 | 7351.0074 | 1.847% | 0.2478%
2017-10-02 | 15 | 7505 | 135.7788 | 1.809% | 18.2137 | 0.2427% | 153.9926 | 2.052% | 1500 | 7486.7863 | 7351.0074 | 1.847% | 0.2478%
2017-09-03 | 22 | 7506 | 135.7911 | 1.809% | 18.215 | 0.2427% | 154.0061 | 2.052% | 1501 | 7487.785 | 7351.9939 | 1.847% | 0.2478%
2017-09-08 | 14 | 7506 | 135.7911 | 1.809% | 18.215 | 0.2427% | 154.0061 | 2.052% | 1502 | 7487.785 | 7351.9939 | 1.847% | 0.2478%
2017-11-30 | 19 | 7508 | 135.8156 | 1.809% | 18.2177 | 0.2426% | 154.0333 | 2.052% | 1503 | 7489.7823 | 7353.9667 | 1.847% | 0.2477%
2017-11-12 | 3 | 7509 | 135.8279 | 1.809% | 18.219 | 0.2426% | 154.0469 | 2.051% | 1504 | 7490.781 | 7354.9531 | 1.847% | 0.2477%
2017-09-04 | 23 | 7510 | 135.8402 | 1.809% | 18.2203 | 0.2426% | 154.0605 | 2.051% | 1505 | 7491.7797 | 7355.9395 | 1.847% | 0.2477%
2017-09-28 | 24 | 7513 | 135.877 | 1.809% | 18.2242 | 0.2426% | 154.1012 | 2.051% | 1506 | 7494.7758 | 7358.8988 | 1.846% | 0.2476%
2017-11-18 | 4 | 7514 | 135.8893 | 1.808% | 18.2255 | 0.2426% | 154.1148 | 2.051% | 1507 | 7495.7745 | 7359.8852 | 1.846% | 0.2476%
2017-10-07 | 23 | 7517 | 135.9261 | 1.808% | 18.2294 | 0.2425% | 154.1555 | 2.051% | 1508 | 7498.7706 | 7362.8445 | 1.846% | 0.2476%
2017-09-01 | 23 | 7518 | 135.9384 | 1.808% | 18.2307 | 0.2425% | 154.1691 | 2.051% | 1509 | 7499.7693 | 7363.8309 | 1.846% | 0.2476%
2017-11-24 | 4 | 7518 | 135.9384 | 1.808% | 18.2307 | 0.2425% | 154.1691 | 2.051% | 1510 | 7499.7693 | 7363.8309 | 1.846% | 0.2476%
2017-10-31 | 10 | 7520 | 135.963 | 1.808% | 18.2333 | 0.2425% | 154.1962 | 2.05% | 1511 | 7501.7667 | 7365.8038 | 1.846% | 0.2475%
2017-11-30 | 6 | 7522 | 135.9875 | 1.808% | 18.2359 | 0.2424% | 154.2234 | 2.05% | 1512 | 7503.7641 | 7367.7766 | 1.846% | 0.2475%
2017-09-13 | 23 | 7527 | 136.0489 | 1.807% | 18.2424 | 0.2424% | 154.2912 | 2.05% | 1513 | 7508.7576 | 7372.7088 | 1.845% | 0.2474%
2017-11-13 | 18 | 7527 | 136.0489 | 1.807% | 18.2424 | 0.2424% | 154.2912 | 2.05% | 1514 | 7508.7576 | 7372.7088 | 1.845% | 0.2474%
2017-10-04 | 14 | 7528 | 136.0612 | 1.807% | 18.2437 | 0.2423% | 154.3048 | 2.05% | 1515 | 7509.7563 | 7373.6952 | 1.845% | 0.2474%
2017-11-12 | 20 | 7528 | 136.0612 | 1.807% | 18.2437 | 0.2423% | 154.3048 | 2.05% | 1516 | 7509.7563 | 7373.6952 | 1.845% | 0.2474%
2017-10-23 | 18 | 7529 | 136.0734 | 1.807% | 18.245 | 0.2423% | 154.3184 | 2.05% | 1517 | 7510.755 | 7374.6816 | 1.845% | 0.2474%
2017-11-17 | 24 | 7534 | 136.1348 | 1.807% | 18.2515 | 0.2423% | 154.3863 | 2.049% | 1518 | 7515.7485 | 7379.6137 | 1.845% | 0.2473%
2017-11-25 | 5 | 7534 | 136.1348 | 1.807% | 18.2515 | 0.2423% | 154.3863 | 2.049% | 1519 | 7515.7485 | 7379.6137 | 1.845% | 0.2473%
2017-09-19 | 23 | 7535 | 136.1471 | 1.807% | 18.2528 | 0.2422% | 154.3999 | 2.049% | 1520 | 7516.7472 | 7380.6001 | 1.845% | 0.2473%
2017-10-24 | 20 | 7535 | 136.1471 | 1.807% | 18.2528 | 0.2422% | 154.3999 | 2.049% | 1521 | 7516.7472 | 7380.6001 | 1.845% | 0.2473%
2017-09-20 | 10 | 7537 | 136.1716 | 1.807% | 18.2554 | 0.2422% | 154.427 | 2.049% | 1522 | 7518.7446 | 7382.573 | 1.845% | 0.2473%
2017-10-23 | 14 | 7537 | 136.1716 | 1.807% | 18.2554 | 0.2422% | 154.427 | 2.049% | 1523 | 7518.7446 | 7382.573 | 1.845% | 0.2473%
2017-11-06 | 18 | 7537 | 136.1716 | 1.807% | 18.2554 | 0.2422% | 154.427 | 2.049% | 1524 | 7518.7446 | 7382.573 | 1.845% | 0.2473%
2017-11-20 | 12 | 7537 | 136.1716 | 1.807% | 18.2554 | 0.2422% | 154.427 | 2.049% | 1525 | 7518.7446 | 7382.573 | 1.845% | 0.2473%
2017-09-09 | 16 | 7538 | 136.1839 | 1.807% | 18.2567 | 0.2422% | 154.4406 | 2.049% | 1526 | 7519.7433 | 7383.5594 | 1.844% | 0.2473%
2017-11-02 | 20 | 7538 | 136.1839 | 1.807% | 18.2567 | 0.2422% | 154.4406 | 2.049% | 1527 | 7519.7433 | 7383.5594 | 1.844% | 0.2473%
2017-11-17 | 11 | 7538 | 136.1839 | 1.807% | 18.2567 | 0.2422% | 154.4406 | 2.049% | 1528 | 7519.7433 | 7383.5594 | 1.844% | 0.2473%
2017-10-06 | 22 | 7540 | 136.2085 | 1.806% | 18.2593 | 0.2422% | 154.4677 | 2.049% | 1529 | 7521.7407 | 7385.5323 | 1.844% | 0.2472%
2017-11-26 | 20 | 7541 | 136.2207 | 1.806% | 18.2606 | 0.2422% | 154.4813 | 2.049% | 1530 | 7522.7394 | 7386.5187 | 1.844% | 0.2472%
2017-09-15 | 10 | 7543 | 136.2453 | 1.806% | 18.2632 | 0.2421% | 154.5085 | 2.048% | 1531 | 7524.7368 | 7388.4915 | 1.844% | 0.2472%
2017-10-23 | 15 | 7544 | 136.2576 | 1.806% | 18.2645 | 0.2421% | 154.522 | 2.048% | 1532 | 7525.7355 | 7389.478 | 1.844% | 0.2472%
2017-09-18 | 23 | 7546 | 136.2821 | 1.806% | 18.2671 | 0.2421% | 154.5492 | 2.048% | 1533 | 7527.7329 | 7391.4508 | 1.844% | 0.2471%
2017-10-12 | 23 | 7546 | 136.2821 | 1.806% | 18.2671 | 0.2421% | 154.5492 | 2.048% | 1534 | 7527.7329 | 7391.4508 | 1.844% | 0.2471%
2017-11-12 | 1 | 7547 | 136.2944 | 1.806% | 18.2684 | 0.2421% | 154.5628 | 2.048% | 1535 | 7528.7316 | 7392.4372 | 1.844% | 0.2471%
2017-11-24 | 22 | 7547 | 136.2944 | 1.806% | 18.2684 | 0.2421% | 154.5628 | 2.048% | 1536 | 7528.7316 | 7392.4372 | 1.844% | 0.2471%
2017-09-25 | 23 | 7552 | 136.3558 | 1.806% | 18.2749 | 0.242% | 154.6306 | 2.048% | 1537 | 7533.7251 | 7397.3694 | 1.843% | 0.247%
2017-09-12 | 12 | 7553 | 136.368 | 1.805% | 18.2762 | 0.242% | 154.6442 | 2.047% | 1538 | 7534.7238 | 7398.3558 | 1.843% | 0.247%
2017-09-22 | 10 | 7557 | 136.4171 | 1.805% | 18.2814 | 0.2419% | 154.6985 | 2.047% | 1539 | 7538.7186 | 7402.3015 | 1.843% | 0.247%
2017-09-02 | 13 | 7561 | 136.4662 | 1.805% | 18.2866 | 0.2419% | 154.7528 | 2.047% | 1540 | 7542.7134 | 7406.2472 | 1.843% | 0.2469%
2017-09-01 | 9 | 7562 | 136.4785 | 1.805% | 18.2879 | 0.2418% | 154.7664 | 2.047% | 1541 | 7543.7121 | 7407.2336 | 1.843% | 0.2469%
2017-11-13 | 10 | 7563 | 136.4908 | 1.805% | 18.2892 | 0.2418% | 154.78 | 2.047% | 1542 | 7544.7108 | 7408.22 | 1.842% | 0.2469%
2017-11-29 | 19 | 7565 | 136.5153 | 1.805% | 18.2918 | 0.2418% | 154.8071 | 2.046% | 1543 | 7546.7082 | 7410.1929 | 1.842% | 0.2468%
2017-09-21 | 23 | 7568 | 136.5522 | 1.804% | 18.2957 | 0.2418% | 154.8479 | 2.046% | 1544 | 7549.7043 | 7413.1521 | 1.842% | 0.2468%
2017-11-21 | 20 | 7568 | 136.5522 | 1.804% | 18.2957 | 0.2418% | 154.8479 | 2.046% | 1545 | 7549.7043 | 7413.1521 | 1.842% | 0.2468%
2017-11-06 | 20 | 7569 | 136.5644 | 1.804% | 18.297 | 0.2417% | 154.8614 | 2.046% | 1546 | 7550.703 | 7414.1386 | 1.842% | 0.2468%
2017-10-02 | 21 | 7576 | 136.6504 | 1.804% | 18.3061 | 0.2416% | 154.9565 | 2.045% | 1547 | 7557.6939 | 7421.0435 | 1.841% | 0.2467%
2017-11-12 | 4 | 7577 | 136.6626 | 1.804% | 18.3074 | 0.2416% | 154.9701 | 2.045% | 1548 | 7558.6926 | 7422.0299 | 1.841% | 0.2467%
2017-09-30 | 15 | 7581 | 136.7117 | 1.803% | 18.3126 | 0.2416% | 155.0244 | 2.045% | 1549 | 7562.6874 | 7425.9756 | 1.841% | 0.2466%
2017-09-15 | 23 | 7584 | 136.7486 | 1.803% | 18.3165 | 0.2415% | 155.0651 | 2.045% | 1550 | 7565.6835 | 7428.9349 | 1.841% | 0.2466%
2017-11-16 | 19 | 7584 | 136.7486 | 1.803% | 18.3165 | 0.2415% | 155.0651 | 2.045% | 1551 | 7565.6835 | 7428.9349 | 1.841% | 0.2466%
2017-11-29 | 20 | 7584 | 136.7486 | 1.803% | 18.3165 | 0.2415% | 155.0651 | 2.045% | 1552 | 7565.6835 | 7428.9349 | 1.841% | 0.2466%
2017-11-24 | 21 | 7586 | 136.7731 | 1.803% | 18.3191 | 0.2415% | 155.0922 | 2.044% | 1553 | 7567.6809 | 7430.9078 | 1.841% | 0.2465%
2017-11-16 | 20 | 7587 | 136.7854 | 1.803% | 18.3204 | 0.2415% | 155.1058 | 2.044% | 1554 | 7568.6796 | 7431.8942 | 1.841% | 0.2465%
2017-11-30 | 20 | 7589 | 136.8099 | 1.803% | 18.323 | 0.2414% | 155.133 | 2.044% | 1555 | 7570.677 | 7433.867 | 1.84% | 0.2465%
2017-10-11 | 7 | 7590 | 136.8222 | 1.803% | 18.3243 | 0.2414% | 155.1465 | 2.044% | 1556 | 7571.6757 | 7434.8535 | 1.84% | 0.2465%
2017-11-28 | 22 | 7591 | 136.8345 | 1.803% | 18.3256 | 0.2414% | 155.1601 | 2.044% | 1557 | 7572.6744 | 7435.8399 | 1.84% | 0.2464%
2017-10-13 | 19 | 7592 | 136.8468 | 1.803% | 18.3269 | 0.2414% | 155.1737 | 2.044% | 1558 | 7573.6731 | 7436.8263 | 1.84% | 0.2464%
2017-10-15 | 14 | 7594 | 136.8713 | 1.802% | 18.3295 | 0.2414% | 155.2008 | 2.044% | 1559 | 7575.6705 | 7438.7992 | 1.84% | 0.2464%
2017-10-03 | 21 | 7596 | 136.8959 | 1.802% | 18.3321 | 0.2413% | 155.228 | 2.044% | 1560 | 7577.6679 | 7440.772 | 1.84% | 0.2464%
2017-10-08 | 10 | 7601 | 136.9572 | 1.802% | 18.3386 | 0.2413% | 155.2959 | 2.043% | 1561 | 7582.6614 | 7445.7041 | 1.839% | 0.2463%
2017-09-08 | 20 | 7602 | 136.9695 | 1.802% | 18.3399 | 0.2413% | 155.3095 | 2.043% | 1562 | 7583.6601 | 7446.6905 | 1.839% | 0.2463%
2017-11-12 | 19 | 7604 | 136.9941 | 1.802% | 18.3425 | 0.2412% | 155.3366 | 2.043% | 1563 | 7585.6575 | 7448.6634 | 1.839% | 0.2463%
2017-11-28 | 1 | 7606 | 137.0186 | 1.801% | 18.3451 | 0.2412% | 155.3638 | 2.043% | 1564 | 7587.6549 | 7450.6362 | 1.839% | 0.2462%
2017-11-26 | 21 | 7607 | 137.0309 | 1.801% | 18.3464 | 0.2412% | 155.3773 | 2.043% | 1565 | 7588.6536 | 7451.6227 | 1.839% | 0.2462%
2017-11-28 | 18 | 7607 | 137.0309 | 1.801% | 18.3464 | 0.2412% | 155.3773 | 2.043% | 1566 | 7588.6536 | 7451.6227 | 1.839% | 0.2462%
2017-09-14 | 23 | 7610 | 137.0677 | 1.801% | 18.3503 | 0.2411% | 155.4181 | 2.042% | 1567 | 7591.6497 | 7454.5819 | 1.839% | 0.2462%
2017-11-16 | 21 | 7610 | 137.0677 | 1.801% | 18.3503 | 0.2411% | 155.4181 | 2.042% | 1568 | 7591.6497 | 7454.5819 | 1.839% | 0.2462%
2017-09-25 | 11 | 7611 | 137.08 | 1.801% | 18.3516 | 0.2411% | 155.4316 | 2.042% | 1569 | 7592.6484 | 7455.5684 | 1.839% | 0.2461%
2017-11-21 | 1 | 7614 | 137.1168 | 1.801% | 18.3555 | 0.2411% | 155.4724 | 2.042% | 1570 | 7595.6445 | 7458.5276 | 1.838% | 0.2461%
2017-10-24 | 17 | 7616 | 137.1414 | 1.801% | 18.3582 | 0.241% | 155.4995 | 2.042% | 1571 | 7597.6418 | 7460.5005 | 1.838% | 0.2461%
2017-11-18 | 10 | 7620 | 137.1905 | 1.8% | 18.3634 | 0.241% | 155.5538 | 2.041% | 1572 | 7601.6366 | 7464.4462 | 1.838% | 0.246%
2017-10-30 | 21 | 7621 | 137.2027 | 1.8% | 18.3647 | 0.241% | 155.5674 | 2.041% | 1573 | 7602.6353 | 7465.4326 | 1.838% | 0.246%
2017-09-30 | 18 | 7623 | 137.2273 | 1.8% | 18.3673 | 0.2409% | 155.5946 | 2.041% | 1574 | 7604.6327 | 7467.4054 | 1.838% | 0.246%
2017-10-08 | 23 | 7623 | 137.2273 | 1.8% | 18.3673 | 0.2409% | 155.5946 | 2.041% | 1575 | 7604.6327 | 7467.4054 | 1.838% | 0.246%
2017-10-30 | 11 | 7629 | 137.3009 | 1.8% | 18.3751 | 0.2409% | 155.676 | 2.041% | 1576 | 7610.6249 | 7473.324 | 1.837% | 0.2459%
2017-11-24 | 11 | 7632 | 137.3378 | 1.799% | 18.379 | 0.2408% | 155.7167 | 2.04% | 1577 | 7613.621 | 7476.2833 | 1.837% | 0.2458%
2017-10-05 | 22 | 7634 | 137.3623 | 1.799% | 18.3816 | 0.2408% | 155.7439 | 2.04% | 1578 | 7615.6184 | 7478.2561 | 1.837% | 0.2458%
2017-09-09 | 18 | 7637 | 137.3991 | 1.799% | 18.3855 | 0.2407% | 155.7846 | 2.04% | 1579 | 7618.6145 | 7481.2154 | 1.837% | 0.2458%
2017-11-07 | 19 | 7638 | 137.4114 | 1.799% | 18.3868 | 0.2407% | 155.7982 | 2.04% | 1580 | 7619.6132 | 7482.2018 | 1.837% | 0.2457%
2017-10-10 | 24 | 7640 | 137.436 | 1.799% | 18.3894 | 0.2407% | 155.8253 | 2.04% | 1581 | 7621.6106 | 7484.1747 | 1.836% | 0.2457%
2017-09-09 | 17 | 7641 | 137.4483 | 1.799% | 18.3907 | 0.2407% | 155.8389 | 2.04% | 1582 | 7622.6093 | 7485.1611 | 1.836% | 0.2457%
2017-09-26 | 10 | 7646 | 137.5096 | 1.798% | 18.3972 | 0.2406% | 155.9068 | 2.039% | 1583 | 7627.6028 | 7490.0932 | 1.836% | 0.2456%
2017-09-13 | 11 | 7649 | 137.5465 | 1.798% | 18.4011 | 0.2406% | 155.9475 | 2.039% | 1584 | 7630.5989 | 7493.0525 | 1.836% | 0.2456%
2017-11-21 | 2 | 7652 | 137.5833 | 1.798% | 18.405 | 0.2405% | 155.9883 | 2.039% | 1585 | 7633.595 | 7496.0117 | 1.835% | 0.2455%
2017-09-07 | 14 | 7656 | 137.6324 | 1.798% | 18.4102 | 0.2405% | 156.0426 | 2.038% | 1586 | 7637.5898 | 7499.9574 | 1.835% | 0.2455%
2017-10-05 | 12 | 7656 | 137.6324 | 1.798% | 18.4102 | 0.2405% | 156.0426 | 2.038% | 1587 | 7637.5898 | 7499.9574 | 1.835% | 0.2455%
2017-10-13 | 20 | 7657 | 137.6447 | 1.798% | 18.4115 | 0.2405% | 156.0561 | 2.038% | 1588 | 7638.5885 | 7500.9439 | 1.835% | 0.2455%
2017-11-21 | 19 | 7657 | 137.6447 | 1.798% | 18.4115 | 0.2405% | 156.0561 | 2.038% | 1589 | 7638.5885 | 7500.9439 | 1.835% | 0.2455%
2017-11-15 | 11 | 7659 | 137.6692 | 1.797% | 18.4141 | 0.2404% | 156.0833 | 2.038% | 1590 | 7640.5859 | 7502.9167 | 1.835% | 0.2454%
2017-11-18 | 5 | 7665 | 137.7429 | 1.797% | 18.4219 | 0.2403% | 156.1648 | 2.037% | 1591 | 7646.5781 | 7508.8352 | 1.834% | 0.2453%
2017-09-23 | 11 | 7672 | 137.8288 | 1.797% | 18.431 | 0.2402% | 156.2598 | 2.037% | 1592 | 7653.569 | 7515.7402 | 1.834% | 0.2452%
2017-10-27 | 9 | 7674 | 137.8533 | 1.796% | 18.4336 | 0.2402% | 156.2869 | 2.037% | 1593 | 7655.5664 | 7517.7131 | 1.834% | 0.2452%
2017-11-11 | 12 | 7679 | 137.9147 | 1.796% | 18.4401 | 0.2401% | 156.3548 | 2.036% | 1594 | 7660.5599 | 7522.6452 | 1.833% | 0.2451%
2017-10-13 | 14 | 7680 | 137.927 | 1.796% | 18.4414 | 0.2401% | 156.3684 | 2.036% | 1595 | 7661.5586 | 7523.6316 | 1.833% | 0.2451%
2017-11-12 | 5 | 7680 | 137.927 | 1.796% | 18.4414 | 0.2401% | 156.3684 | 2.036% | 1596 | 7661.5586 | 7523.6316 | 1.833% | 0.2451%
2017-11-11 | 24 | 7683 | 137.9638 | 1.796% | 18.4453 | 0.2401% | 156.4091 | 2.036% | 1597 | 7664.5547 | 7526.5909 | 1.833% | 0.2451%
2017-11-13 | 9 | 7685 | 137.9884 | 1.796% | 18.4479 | 0.2401% | 156.4363 | 2.036% | 1598 | 7666.5521 | 7528.5637 | 1.833% | 0.245%
2017-11-14 | 10 | 7688 | 138.0252 | 1.795% | 18.4518 | 0.24% | 156.477 | 2.035% | 1599 | 7669.5482 | 7531.523 | 1.833% | 0.245%
2017-09-29 | 12 | 7690 | 138.0497 | 1.795% | 18.4544 | 0.24% | 156.5042 | 2.035% | 1600 | 7671.5456 | 7533.4958 | 1.832% | 0.245%
2017-10-13 | 18 | 7692 | 138.0743 | 1.795% | 18.457 | 0.24% | 156.5313 | 2.035% | 1601 | 7673.543 | 7535.4687 | 1.832% | 0.2449%
2017-09-06 | 10 | 7694 | 138.0988 | 1.795% | 18.4596 | 0.2399% | 156.5585 | 2.035% | 1602 | 7675.5404 | 7537.4415 | 1.832% | 0.2449%
2017-09-27 | 9 | 7694 | 138.0988 | 1.795% | 18.4596 | 0.2399% | 156.5585 | 2.035% | 1603 | 7675.5404 | 7537.4415 | 1.832% | 0.2449%
2017-11-28 | 2 | 7695 | 138.1111 | 1.795% | 18.4609 | 0.2399% | 156.572 | 2.035% | 1604 | 7676.5391 | 7538.428 | 1.832% | 0.2449%
2017-10-30 | 20 | 7696 | 138.1234 | 1.795% | 18.4622 | 0.2399% | 156.5856 | 2.035% | 1605 | 7677.5378 | 7539.4144 | 1.832% | 0.2449%
2017-09-22 | 23 | 7697 | 138.1357 | 1.795% | 18.4635 | 0.2399% | 156.5992 | 2.035% | 1606 | 7678.5365 | 7540.4008 | 1.832% | 0.2449%
2017-10-02 | 19 | 7697 | 138.1357 | 1.795% | 18.4635 | 0.2399% | 156.5992 | 2.035% | 1607 | 7678.5365 | 7540.4008 | 1.832% | 0.2449%
2017-11-13 | 21 | 7697 | 138.1357 | 1.795% | 18.4635 | 0.2399% | 156.5992 | 2.035% | 1608 | 7678.5365 | 7540.4008 | 1.832% | 0.2449%
2017-09-29 | 21 | 7698 | 138.1479 | 1.795% | 18.4648 | 0.2399% | 156.6128 | 2.034% | 1609 | 7679.5352 | 7541.3872 | 1.832% | 0.2448%
2017-11-16 | 10 | 7699 | 138.1602 | 1.795% | 18.4661 | 0.2399% | 156.6263 | 2.034% | 1610 | 7680.5339 | 7542.3737 | 1.832% | 0.2448%
2017-10-02 | 16 | 7701 | 138.1848 | 1.794% | 18.4687 | 0.2398% | 156.6535 | 2.034% | 1611 | 7682.5313 | 7544.3465 | 1.832% | 0.2448%
2017-11-08 | 17 | 7701 | 138.1848 | 1.794% | 18.4687 | 0.2398% | 156.6535 | 2.034% | 1612 | 7682.5313 | 7544.3465 | 1.832% | 0.2448%
2017-09-14 | 10 | 7704 | 138.2216 | 1.794% | 18.4726 | 0.2398% | 156.6942 | 2.034% | 1613 | 7685.5274 | 7547.3058 | 1.831% | 0.2448%
2017-09-30 | 16 | 7704 | 138.2216 | 1.794% | 18.4726 | 0.2398% | 156.6942 | 2.034% | 1614 | 7685.5274 | 7547.3058 | 1.831% | 0.2448%
2017-10-09 | 24 | 7712 | 138.3198 | 1.794% | 18.483 | 0.2397% | 156.8028 | 2.033% | 1615 | 7693.517 | 7555.1972 | 1.831% | 0.2446%
2017-10-12 | 8 | 7713 | 138.3321 | 1.793% | 18.4843 | 0.2397% | 156.8164 | 2.033% | 1616 | 7694.5157 | 7556.1836 | 1.831% | 0.2446%
2017-11-09 | 20 | 7715 | 138.3566 | 1.793% | 18.4869 | 0.2396% | 156.8436 | 2.033% | 1617 | 7696.5131 | 7558.1564 | 1.831% | 0.2446%
2017-11-13 | 8 | 7716 | 138.3689 | 1.793% | 18.4882 | 0.2396% | 156.8571 | 2.033% | 1618 | 7697.5118 | 7559.1429 | 1.83% | 0.2446%
2017-11-16 | 6 | 7720 | 138.418 | 1.793% | 18.4934 | 0.2396% | 156.9114 | 2.033% | 1619 | 7701.5066 | 7563.0886 | 1.83% | 0.2445%
2017-11-27 | 24 | 7720 | 138.418 | 1.793% | 18.4934 | 0.2396% | 156.9114 | 2.033% | 1620 | 7701.5066 | 7563.0886 | 1.83% | 0.2445%
2017-11-11 | 18 | 7722 | 138.4425 | 1.793% | 18.496 | 0.2395% | 156.9386 | 2.032% | 1621 | 7703.504 | 7565.0614 | 1.83% | 0.2445%
2017-11-17 | 6 | 7729 | 138.5285 | 1.792% | 18.5052 | 0.2394% | 157.0336 | 2.032% | 1622 | 7710.4948 | 7571.9664 | 1.829% | 0.2444%
2017-11-17 | 23 | 7729 | 138.5285 | 1.792% | 18.5052 | 0.2394% | 157.0336 | 2.032% | 1623 | 7710.4948 | 7571.9664 | 1.829% | 0.2444%
2017-11-25 | 10 | 7732 | 138.5653 | 1.792% | 18.5091 | 0.2394% | 157.0744 | 2.031% | 1624 | 7713.4909 | 7574.9256 | 1.829% | 0.2443%
2017-10-23 | 19 | 7736 | 138.6144 | 1.792% | 18.5143 | 0.2393% | 157.1287 | 2.031% | 1625 | 7717.4857 | 7578.8713 | 1.829% | 0.2443%
2017-09-30 | 17 | 7744 | 138.7126 | 1.791% | 18.5247 | 0.2392% | 157.2373 | 2.03% | 1626 | 7725.4753 | 7586.7627 | 1.828% | 0.2442%
2017-11-23 | 12 | 7744 | 138.7126 | 1.791% | 18.5247 | 0.2392% | 157.2373 | 2.03% | 1627 | 7725.4753 | 7586.7627 | 1.828% | 0.2442%
2017-11-15 | 18 | 7752 | 138.8108 | 1.791% | 18.5351 | 0.2391% | 157.3459 | 2.03% | 1628 | 7733.4649 | 7594.6541 | 1.828% | 0.2441%
2017-11-23 | 8 | 7752 | 138.8108 | 1.791% | 18.5351 | 0.2391% | 157.3459 | 2.03% | 1629 | 7733.4649 | 7594.6541 | 1.828% | 0.2441%
2017-11-17 | 19 | 7754 | 138.8353 | 1.79% | 18.5377 | 0.2391% | 157.373 | 2.03% | 1630 | 7735.4623 | 7596.627 | 1.828% | 0.244%
2017-09-12 | 13 | 7760 | 138.909 | 1.79% | 18.5455 | 0.239% | 157.4545 | 2.029% | 1631 | 7741.4545 | 7602.5455 | 1.827% | 0.2439%
2017-11-30 | 10 | 7763 | 138.9458 | 1.79% | 18.5494 | 0.2389% | 157.4952 | 2.029% | 1632 | 7744.4506 | 7605.5048 | 1.827% | 0.2439%
2017-10-13 | 15 | 7770 | 139.0318 | 1.789% | 18.5585 | 0.2388% | 157.5902 | 2.028% | 1633 | 7751.4415 | 7612.4098 | 1.826% | 0.2438%
2017-11-06 | 19 | 7771 | 139.044 | 1.789% | 18.5598 | 0.2388% | 157.6038 | 2.028% | 1634 | 7752.4402 | 7613.3962 | 1.826% | 0.2438%
2017-11-25 | 6 | 7776 | 139.1054 | 1.789% | 18.5663 | 0.2388% | 157.6717 | 2.028% | 1635 | 7757.4337 | 7618.3283 | 1.826% | 0.2437%
2017-09-17 | 12 | 7779 | 139.1422 | 1.789% | 18.5702 | 0.2387% | 157.7124 | 2.027% | 1636 | 7760.4298 | 7621.2876 | 1.826% | 0.2437%
2017-11-09 | 18 | 7780 | 139.1545 | 1.789% | 18.5715 | 0.2387% | 157.726 | 2.027% | 1637 | 7761.4285 | 7622.274 | 1.826% | 0.2436%
2017-10-03 | 19 | 7783 | 139.1913 | 1.788% | 18.5754 | 0.2387% | 157.7667 | 2.027% | 1638 | 7764.4246 | 7625.2333 | 1.825% | 0.2436%
2017-11-27 | 18 | 7785 | 139.2159 | 1.788% | 18.578 | 0.2386% | 157.7939 | 2.027% | 1639 | 7766.422 | 7627.2061 | 1.825% | 0.2436%
2017-10-04 | 15 | 7786 | 139.2282 | 1.788% | 18.5793 | 0.2386% | 157.8075 | 2.027% | 1640 | 7767.4207 | 7628.1925 | 1.825% | 0.2436%
2017-10-03 | 16 | 7787 | 139.2404 | 1.788% | 18.5806 | 0.2386% | 157.821 | 2.027% | 1641 | 7768.4194 | 7629.179 | 1.825% | 0.2435%
2017-11-11 | 6 | 7791 | 139.2895 | 1.788% | 18.5858 | 0.2386% | 157.8753 | 2.026% | 1642 | 7772.4142 | 7633.1247 | 1.825% | 0.2435%
2017-09-16 | 11 | 7798 | 139.3755 | 1.787% | 18.5949 | 0.2385% | 157.9704 | 2.026% | 1643 | 7779.4051 | 7640.0296 | 1.824% | 0.2434%
2017-10-07 | 12 | 7798 | 139.3755 | 1.787% | 18.5949 | 0.2385% | 157.9704 | 2.026% | 1644 | 7779.4051 | 7640.0296 | 1.824% | 0.2434%
2017-11-21 | 3 | 7798 | 139.3755 | 1.787% | 18.5949 | 0.2385% | 157.9704 | 2.026% | 1645 | 7779.4051 | 7640.0296 | 1.824% | 0.2434%
2017-11-15 | 22 | 7799 | 139.3877 | 1.787% | 18.5962 | 0.2384% | 157.984 | 2.026% | 1646 | 7780.4038 | 7641.016 | 1.824% | 0.2434%
2017-09-04 | 12 | 7800 | 139.4 | 1.787% | 18.5975 | 0.2384% | 157.9975 | 2.026% | 1647 | 7781.4025 | 7642.0025 | 1.824% | 0.2434%
2017-11-20 | 24 | 7800 | 139.4 | 1.787% | 18.5975 | 0.2384% | 157.9975 | 2.026% | 1648 | 7781.4025 | 7642.0025 | 1.824% | 0.2434%
2017-10-12 | 9 | 7802 | 139.4246 | 1.787% | 18.6001 | 0.2384% | 158.0247 | 2.025% | 1649 | 7783.3999 | 7643.9753 | 1.824% | 0.2433%
2017-10-10 | 7 | 7806 | 139.4737 | 1.787% | 18.6053 | 0.2383% | 158.079 | 2.025% | 1650 | 7787.3947 | 7647.921 | 1.824% | 0.2433%
2017-10-31 | 7 | 7807 | 139.4859 | 1.787% | 18.6066 | 0.2383% | 158.0926 | 2.025% | 1651 | 7788.3934 | 7648.9074 | 1.824% | 0.2433%
2017-10-06 | 12 | 7808 | 139.4982 | 1.787% | 18.6079 | 0.2383% | 158.1061 | 2.025% | 1652 | 7789.3921 | 7649.8939 | 1.824% | 0.2432%
2017-10-23 | 21 | 7808 | 139.4982 | 1.787% | 18.6079 | 0.2383% | 158.1061 | 2.025% | 1653 | 7789.3921 | 7649.8939 | 1.824% | 0.2432%
2017-09-08 | 15 | 7815 | 139.5841 | 1.786% | 18.617 | 0.2382% | 158.2012 | 2.024% | 1654 | 7796.383 | 7656.7988 | 1.823% | 0.2431%
2017-11-14 | 22 | 7818 | 139.621 | 1.786% | 18.6209 | 0.2382% | 158.2419 | 2.024% | 1655 | 7799.3791 | 7659.7581 | 1.823% | 0.2431%
2017-11-24 | 5 | 7824 | 139.6946 | 1.785% | 18.6287 | 0.2381% | 158.3234 | 2.024% | 1656 | 7805.3713 | 7665.6766 | 1.822% | 0.243%
2017-10-13 | 17 | 7829 | 139.756 | 1.785% | 18.6352 | 0.238% | 158.3912 | 2.023% | 1657 | 7810.3648 | 7670.6088 | 1.822% | 0.2429%
2017-10-27 | 8 | 7830 | 139.7683 | 1.785% | 18.6365 | 0.238% | 158.4048 | 2.023% | 1658 | 7811.3635 | 7671.5952 | 1.822% | 0.2429%
2017-11-28 | 11 | 7838 | 139.8665 | 1.784% | 18.647 | 0.2379% | 158.5134 | 2.022% | 1659 | 7819.353 | 7679.4866 | 1.821% | 0.2428%
2017-10-02 | 17 | 7839 | 139.8787 | 1.784% | 18.6483 | 0.2379% | 158.527 | 2.022% | 1660 | 7820.3517 | 7680.473 | 1.821% | 0.2428%
2017-10-02 | 20 | 7844 | 139.9401 | 1.784% | 18.6548 | 0.2378% | 158.5949 | 2.022% | 1661 | 7825.3452 | 7685.4051 | 1.821% | 0.2427%
2017-11-18 | 6 | 7845 | 139.9524 | 1.784% | 18.6561 | 0.2378% | 158.6085 | 2.022% | 1662 | 7826.3439 | 7686.3915 | 1.821% | 0.2427%
2017-11-17 | 20 | 7848 | 139.9892 | 1.784% | 18.66 | 0.2378% | 158.6492 | 2.022% | 1663 | 7829.34 | 7689.3508 | 1.821% | 0.2427%
2017-09-19 | 11 | 7849 | 140.0015 | 1.784% | 18.6613 | 0.2378% | 158.6628 | 2.021% | 1664 | 7830.3387 | 7690.3372 | 1.82% | 0.2427%
2017-09-21 | 10 | 7854 | 140.0629 | 1.783% | 18.6678 | 0.2377% | 158.7306 | 2.021% | 1665 | 7835.3322 | 7695.2694 | 1.82% | 0.2426%
2017-10-02 | 18 | 7854 | 140.0629 | 1.783% | 18.6678 | 0.2377% | 158.7306 | 2.021% | 1666 | 7835.3322 | 7695.2694 | 1.82% | 0.2426%
2017-10-13 | 16 | 7854 | 140.0629 | 1.783% | 18.6678 | 0.2377% | 158.7306 | 2.021% | 1667 | 7835.3322 | 7695.2694 | 1.82% | 0.2426%
2017-11-09 | 19 | 7856 | 140.0874 | 1.783% | 18.6704 | 0.2377% | 158.7578 | 2.021% | 1668 | 7837.3296 | 7697.2422 | 1.82% | 0.2426%
2017-11-20 | 5 | 7856 | 140.0874 | 1.783% | 18.6704 | 0.2377% | 158.7578 | 2.021% | 1669 | 7837.3296 | 7697.2422 | 1.82% | 0.2426%
2017-11-13 | 20 | 7857 | 140.0997 | 1.783% | 18.6717 | 0.2376% | 158.7714 | 2.021% | 1670 | 7838.3283 | 7698.2286 | 1.82% | 0.2425%
2017-11-13 | 19 | 7859 | 140.1242 | 1.783% | 18.6743 | 0.2376% | 158.7985 | 2.021% | 1671 | 7840.3257 | 7700.2015 | 1.82% | 0.2425%
2017-10-03 | 20 | 7860 | 140.1365 | 1.783% | 18.6756 | 0.2376% | 158.8121 | 2.021% | 1672 | 7841.3244 | 7701.1879 | 1.82% | 0.2425%
2017-11-28 | 3 | 7867 | 140.2224 | 1.782% | 18.6847 | 0.2375% | 158.9071 | 2.02% | 1673 | 7848.3153 | 7708.0929 | 1.819% | 0.2424%
2017-09-18 | 11 | 7869 | 140.247 | 1.782% | 18.6873 | 0.2375% | 158.9343 | 2.02% | 1674 | 7850.3127 | 7710.0657 | 1.819% | 0.2424%
2017-09-07 | 21 | 7871 | 140.2715 | 1.782% | 18.6899 | 0.2375% | 158.9614 | 2.02% | 1675 | 7852.3101 | 7712.0386 | 1.819% | 0.2423%
2017-09-03 | 13 | 7873 | 140.2961 | 1.782% | 18.6925 | 0.2374% | 158.9886 | 2.019% | 1676 | 7854.3075 | 7714.0114 | 1.819% | 0.2423%
2017-11-29 | 9 | 7875 | 140.3206 | 1.782% | 18.6951 | 0.2374% | 159.0157 | 2.019% | 1677 | 7856.3049 | 7715.9843 | 1.819% | 0.2423%
2017-09-02 | 14 | 7876 | 140.3329 | 1.782% | 18.6964 | 0.2374% | 159.0293 | 2.019% | 1678 | 7857.3036 | 7716.9707 | 1.818% | 0.2423%
2017-11-12 | 6 | 7879 | 140.3697 | 1.782% | 18.7003 | 0.2373% | 159.07 | 2.019% | 1679 | 7860.2997 | 7719.93 | 1.818% | 0.2422%
2017-11-27 | 11 | 7883 | 140.4188 | 1.781% | 18.7055 | 0.2373% | 159.1243 | 2.019% | 1680 | 7864.2945 | 7723.8757 | 1.818% | 0.2422%
2017-09-29 | 19 | 7888 | 140.4802 | 1.781% | 18.712 | 0.2372% | 159.1922 | 2.018% | 1681 | 7869.288 | 7728.8078 | 1.818% | 0.2421%
2017-10-09 | 8 | 7889 | 140.4925 | 1.781% | 18.7133 | 0.2372% | 159.2058 | 2.018% | 1682 | 7870.2867 | 7729.7942 | 1.818% | 0.2421%
2017-09-02 | 22 | 7893 | 140.5416 | 1.781% | 18.7185 | 0.2372% | 159.2601 | 2.018% | 1683 | 7874.2815 | 7733.7399 | 1.817% | 0.242%
2017-09-28 | 10 | 7895 | 140.5662 | 1.78% | 18.7211 | 0.2371% | 159.2873 | 2.018% | 1684 | 7876.2789 | 7735.7127 | 1.817% | 0.242%
2017-10-30 | 7 | 7895 | 140.5662 | 1.78% | 18.7211 | 0.2371% | 159.2873 | 2.018% | 1685 | 7876.2789 | 7735.7127 | 1.817% | 0.242%
2017-11-28 | 21 | 7897 | 140.5907 | 1.78% | 18.7237 | 0.2371% | 159.3144 | 2.017% | 1686 | 7878.2763 | 7737.6856 | 1.817% | 0.242%
2017-11-17 | 22 | 7898 | 140.603 | 1.78% | 18.725 | 0.2371% | 159.328 | 2.017% | 1687 | 7879.275 | 7738.672 | 1.817% | 0.242%
2017-09-29 | 20 | 7899 | 140.6153 | 1.78% | 18.7263 | 0.2371% | 159.3416 | 2.017% | 1688 | 7880.2737 | 7739.6584 | 1.817% | 0.242%
2017-09-06 | 21 | 7906 | 140.7012 | 1.78% | 18.7354 | 0.237% | 159.4366 | 2.017% | 1689 | 7887.2646 | 7746.5634 | 1.816% | 0.2419%
2017-10-04 | 21 | 7908 | 140.7257 | 1.78% | 18.738 | 0.237% | 159.4637 | 2.016% | 1690 | 7889.262 | 7748.5363 | 1.816% | 0.2418%
2017-11-28 | 19 | 7910 | 140.7503 | 1.779% | 18.7406 | 0.2369% | 159.4909 | 2.016% | 1691 | 7891.2594 | 7750.5091 | 1.816% | 0.2418%
2017-09-24 | 22 | 7913 | 140.7871 | 1.779% | 18.7445 | 0.2369% | 159.5316 | 2.016% | 1692 | 7894.2555 | 7753.4684 | 1.816% | 0.2418%
2017-11-08 | 21 | 7913 | 140.7871 | 1.779% | 18.7445 | 0.2369% | 159.5316 | 2.016% | 1693 | 7894.2555 | 7753.4684 | 1.816% | 0.2418%
2017-09-24 | 12 | 7919 | 140.8608 | 1.779% | 18.7523 | 0.2368% | 159.6131 | 2.016% | 1694 | 7900.2477 | 7759.3869 | 1.815% | 0.2417%
2017-09-07 | 20 | 7926 | 140.9464 | 1.778% | 18.7615 | 0.2367% | 159.7079 | 2.015% | 1695 | 7907.2385 | 7766.2921 | 1.815% | 0.2416% | 7925.5105
2017-09-29 | 13 | 7927 | 140.9539 | 1.778% | 18.764 | 0.2367% | 159.7179 | 2.015% | 1696 | 7908.236 | 7767.2821 | 1.815% | 0.2416%
2017-10-11 | 8 | 7927 | 140.9539 | 1.778% | 18.764 | 0.2367% | 159.7179 | 2.015% | 1697 | 7908.236 | 7767.2821 | 1.815% | 0.2416%
2017-09-23 | 22 | 7931 | 140.9838 | 1.778% | 18.7739 | 0.2367% | 159.7577 | 2.014% | 1698 | 7912.2261 | 7771.2423 | 1.814% | 0.2416%
2017-10-31 | 9 | 7933 | 140.9988 | 1.777% | 18.7788 | 0.2367% | 159.7776 | 2.014% | 1699 | 7914.2212 | 7773.2224 | 1.814% | 0.2416%
2017-11-21 | 11 | 7933 | 140.9988 | 1.777% | 18.7788 | 0.2367% | 159.7776 | 2.014% | 1700 | 7914.2212 | 7773.2224 | 1.814% | 0.2416%
2017-09-26 | 11 | 7935 | 141.0138 | 1.777% | 18.7838 | 0.2367% | 159.7975 | 2.014% | 1701 | 7916.2162 | 7775.2025 | 1.814% | 0.2416%
2017-09-07 | 15 | 7936 | 141.0212 | 1.777% | 18.7863 | 0.2367% | 159.8075 | 2.014% | 1702 | 7917.2137 | 7776.1925 | 1.813% | 0.2416%
2017-09-05 | 10 | 7937 | 141.0287 | 1.777% | 18.7887 | 0.2367% | 159.8175 | 2.014% | 1703 | 7918.2113 | 7777.1825 | 1.813% | 0.2416%
2017-11-17 | 21 | 7938 | 141.0362 | 1.777% | 18.7912 | 0.2367% | 159.8274 | 2.013% | 1704 | 7919.2088 | 7778.1726 | 1.813% | 0.2416%
2017-11-20 | 18 | 7940 | 141.0512 | 1.776% | 18.7962 | 0.2367% | 159.8473 | 2.013% | 1705 | 7921.2038 | 7780.1527 | 1.813% | 0.2416%
2017-11-11 | 23 | 7941 | 141.0586 | 1.776% | 18.7986 | 0.2367% | 159.8573 | 2.013% | 1706 | 7922.2014 | 7781.1427 | 1.813% | 0.2416%
2017-10-23 | 20 | 7951 | 141.1335 | 1.775% | 18.8234 | 0.2367% | 159.9569 | 2.012% | 1707 | 7932.1766 | 7791.0431 | 1.811% | 0.2416%
2017-11-27 | 5 | 7960 | 141.2008 | 1.774% | 18.8457 | 0.2368% | 160.0465 | 2.011% | 1708 | 7941.1543 | 7799.9535 | 1.81% | 0.2416%
2017-09-08 | 19 | 7962 | 141.2158 | 1.774% | 18.8506 | 0.2368% | 160.0664 | 2.01% | 1709 | 7943.1494 | 7801.9336 | 1.81% | 0.2416%
2017-09-26 | 23 | 7964 | 141.2307 | 1.773% | 18.8556 | 0.2368% | 160.0863 | 2.01% | 1710 | 7945.1444 | 7803.9137 | 1.81% | 0.2416%
2017-11-21 | 4 | 7965 | 141.2382 | 1.773% | 18.8581 | 0.2368% | 160.0963 | 2.01% | 1711 | 7946.1419 | 7804.9037 | 1.81% | 0.2416%
2017-11-14 | 18 | 7969 | 141.2681 | 1.773% | 18.868 | 0.2368% | 160.1361 | 2.009% | 1712 | 7950.132 | 7808.8639 | 1.809% | 0.2416%
2017-10-03 | 17 | 7972 | 141.2906 | 1.772% | 18.8754 | 0.2368% | 160.166 | 2.009% | 1713 | 7953.1246 | 7811.834 | 1.809% | 0.2416%
2017-09-06 | 20 | 7977 | 141.328 | 1.772% | 18.8878 | 0.2368% | 160.2158 | 2.008% | 1714 | 7958.1122 | 7816.7842 | 1.808% | 0.2416%
2017-10-03 | 18 | 7982 | 141.3654 | 1.771% | 18.9001 | 0.2368% | 160.2656 | 2.008% | 1715 | 7963.0999 | 7821.7344 | 1.807% | 0.2416%
2017-11-12 | 10 | 7982 | 141.3654 | 1.771% | 18.9001 | 0.2368% | 160.2656 | 2.008% | 1716 | 7963.0999 | 7821.7344 | 1.807% | 0.2416%
2017-09-25 | 12 | 7986 | 141.3953 | 1.771% | 18.91 | 0.2368% | 160.3054 | 2.007% | 1717 | 7967.09 | 7825.6946 | 1.807% | 0.2416%
2017-10-07 | 22 | 7988 | 141.4103 | 1.77% | 18.915 | 0.2368% | 160.3253 | 2.007% | 1718 | 7969.085 | 7827.6747 | 1.807% | 0.2416%
2017-11-28 | 20 | 7989 | 141.4178 | 1.77% | 18.9175 | 0.2368% | 160.3353 | 2.007% | 1719 | 7970.0825 | 7828.6647 | 1.806% | 0.2416%
2017-09-01 | 10 | 7995 | 141.4627 | 1.769% | 18.9323 | 0.2368% | 160.395 | 2.006% | 1720 | 7976.0677 | 7834.605 | 1.806% | 0.2417%
2017-09-12 | 14 | 7998 | 141.4851 | 1.769% | 18.9398 | 0.2368% | 160.4249 | 2.006% | 1721 | 7979.0602 | 7837.5751 | 1.805% | 0.2417%
2017-10-15 | 15 | 8005 | 141.5375 | 1.768% | 18.9571 | 0.2368% | 160.4946 | 2.005% | 1722 | 7986.0429 | 7844.5054 | 1.804% | 0.2417%
2017-09-16 | 22 | 8014 | 141.6048 | 1.767% | 18.9794 | 0.2368% | 160.5842 | 2.004% | 1723 | 7995.0206 | 7853.4158 | 1.803% | 0.2417%
2017-10-05 | 13 | 8018 | 141.6348 | 1.766% | 18.9893 | 0.2368% | 160.624 | 2.003% | 1724 | 7999.0107 | 7857.376 | 1.803% | 0.2417%
2017-09-08 | 16 | 8024 | 141.6797 | 1.766% | 19.0041 | 0.2368% | 160.6838 | 2.003% | 1725 | 8004.9959 | 7863.3162 | 1.802% | 0.2417%
2017-10-08 | 11 | 8024 | 141.6797 | 1.766% | 19.0041 | 0.2368% | 160.6838 | 2.003% | 1726 | 8004.9959 | 7863.3162 | 1.802% | 0.2417%
2017-09-06 | 19 | 8028 | 141.7096 | 1.765% | 19.014 | 0.2368% | 160.7236 | 2.002% | 1727 | 8008.986 | 7867.2764 | 1.801% | 0.2417%
2017-09-01 | 22 | 8029 | 141.7171 | 1.765% | 19.0165 | 0.2368% | 160.7336 | 2.002% | 1728 | 8009.9835 | 7868.2664 | 1.801% | 0.2417%
2017-10-11 | 9 | 8029 | 141.7171 | 1.765% | 19.0165 | 0.2368% | 160.7336 | 2.002% | 1729 | 8009.9835 | 7868.2664 | 1.801% | 0.2417%
2017-11-20 | 11 | 8030 | 141.7246 | 1.765% | 19.019 | 0.2368% | 160.7435 | 2.002% | 1730 | 8010.981 | 7869.2565 | 1.801% | 0.2417%
2017-11-27 | 23 | 8032 | 141.7395 | 1.765% | 19.0239 | 0.2369% | 160.7635 | 2.002% | 1731 | 8012.9761 | 7871.2365 | 1.801% | 0.2417%
2017-10-15 | 21 | 8035 | 141.762 | 1.764% | 19.0314 | 0.2369% | 160.7933 | 2.001% | 1732 | 8015.9686 | 7874.2067 | 1.8% | 0.2417%
2017-09-20 | 23 | 8036 | 141.7695 | 1.764% | 19.0338 | 0.2369% | 160.8033 | 2.001% | 1733 | 8016.9662 | 7875.1967 | 1.8% | 0.2417%
2017-10-06 | 21 | 8037 | 141.7769 | 1.764% | 19.0363 | 0.2369% | 160.8132 | 2.001% | 1734 | 8017.9637 | 7876.1868 | 1.8% | 0.2417%
2017-10-04 | 16 | 8038 | 141.7844 | 1.764% | 19.0388 | 0.2369% | 160.8232 | 2.001% | 1735 | 8018.9612 | 7877.1768 | 1.8% | 0.2417%
2017-11-14 | 9 | 8049 | 141.8667 | 1.763% | 19.066 | 0.2369% | 160.9327 | 1.999% | 1736 | 8029.934 | 7888.0673 | 1.798% | 0.2417%
2017-11-17 | 10 | 8052 | 141.8892 | 1.762% | 19.0734 | 0.2369% | 160.9626 | 1.999% | 1737 | 8032.9266 | 7891.0374 | 1.798% | 0.2417%
2017-10-30 | 10 | 8053 | 141.8967 | 1.762% | 19.0759 | 0.2369% | 160.9726 | 1.999% | 1738 | 8033.9241 | 7892.0274 | 1.798% | 0.2417%
2017-09-17 | 22 | 8055 | 141.9116 | 1.762% | 19.0809 | 0.2369% | 160.9925 | 1.999% | 1739 | 8035.9191 | 7894.0075 | 1.798% | 0.2417%
2017-11-15 | 21 | 8058 | 141.9341 | 1.761% | 19.0883 | 0.2369% | 161.0224 | 1.998% | 1740 | 8038.9117 | 7896.9776 | 1.797% | 0.2417%
2017-11-20 | 23 | 8058 | 141.9341 | 1.761% | 19.0883 | 0.2369% | 161.0224 | 1.998% | 1741 | 8038.9117 | 7896.9776 | 1.797% | 0.2417%
2017-11-23 | 11 | 8064 | 141.979 | 1.761% | 19.1032 | 0.2369% | 161.0821 | 1.998% | 1742 | 8044.8968 | 7902.9179 | 1.797% | 0.2417%
2017-10-12 | 10 | 8067 | 142.0014 | 1.76% | 19.1106 | 0.2369% | 161.112 | 1.997% | 1743 | 8047.8894 | 7905.888 | 1.796% | 0.2417%
2017-09-03 | 21 | 8069 | 142.0164 | 1.76% | 19.1155 | 0.2369% | 161.1319 | 1.997% | 1744 | 8049.8845 | 7907.8681 | 1.796% | 0.2417%
2017-11-29 | 7 | 8074 | 142.0538 | 1.759% | 19.1279 | 0.2369% | 161.1817 | 1.996% | 1745 | 8054.8721 | 7912.8183 | 1.795% | 0.2417%
2017-10-04 | 19 | 8106 | 142.2932 | 1.755% | 19.2071 | 0.2369% | 161.5003 | 1.992% | 1746 | 8086.7929 | 7944.4997 | 1.791% | 0.2418%
2017-10-09 | 9 | 8106 | 142.2932 | 1.755% | 19.2071 | 0.2369% | 161.5003 | 1.992% | 1747 | 8086.7929 | 7944.4997 | 1.791% | 0.2418%
2017-11-15 | 6 | 8106 | 142.2932 | 1.755% | 19.2071 | 0.2369% | 161.5003 | 1.992% | 1748 | 8086.7929 | 7944.4997 | 1.791% | 0.2418%
2017-09-13 | 12 | 8108 | 142.3082 | 1.755% | 19.2121 | 0.237% | 161.5203 | 1.992% | 1749 | 8088.7879 | 7946.4797 | 1.791% | 0.2418%
2017-11-11 | 19 | 8111 | 142.3306 | 1.755% | 19.2195 | 0.237% | 161.5501 | 1.992% | 1750 | 8091.7805 | 7949.4499 | 1.79% | 0.2418%
2017-09-15 | 11 | 8114 | 142.3531 | 1.754% | 19.2269 | 0.237% | 161.58 | 1.991% | 1751 | 8094.7731 | 7952.42 | 1.79% | 0.2418%
2017-11-11 | 22 | 8120 | 142.398 | 1.754% | 19.2418 | 0.237% | 161.6398 | 1.991% | 1752 | 8100.7582 | 7958.3602 | 1.789% | 0.2418%
2017-09-14 | 11 | 8123 | 142.4204 | 1.753% | 19.2492 | 0.237% | 161.6696 | 1.99% | 1753 | 8103.7508 | 7961.3304 | 1.789% | 0.2418%
2017-10-10 | 8 | 8123 | 142.4204 | 1.753% | 19.2492 | 0.237% | 161.6696 | 1.99% | 1754 | 8103.7508 | 7961.3304 | 1.789% | 0.2418%
2017-11-28 | 4 | 8125 | 142.4354 | 1.753% | 19.2542 | 0.237% | 161.6895 | 1.99% | 1755 | 8105.7458 | 7963.3105 | 1.789% | 0.2418%
2017-09-27 | 10 | 8129 | 142.4653 | 1.753% | 19.2641 | 0.237% | 161.7294 | 1.99% | 1756 | 8109.7359 | 7967.2706 | 1.788% | 0.2418%
2017-11-15 | 19 | 8129 | 142.4653 | 1.753% | 19.2641 | 0.237% | 161.7294 | 1.99% | 1757 | 8109.7359 | 7967.2706 | 1.788% | 0.2418%
2017-11-18 | 7 | 8129 | 142.4653 | 1.753% | 19.2641 | 0.237% | 161.7294 | 1.99% | 1758 | 8109.7359 | 7967.2706 | 1.788% | 0.2418%
2017-10-31 | 8 | 8132 | 142.4878 | 1.752% | 19.2715 | 0.237% | 161.7593 | 1.989% | 1759 | 8112.7285 | 7970.2407 | 1.788% | 0.2418%
2017-09-29 | 18 | 8134 | 142.5027 | 1.752% | 19.2765 | 0.237% | 161.7792 | 1.989% | 1760 | 8114.7235 | 7972.2208 | 1.787% | 0.2418%
2017-11-11 | 11 | 8135 | 142.5102 | 1.752% | 19.2789 | 0.237% | 161.7891 | 1.989% | 1761 | 8115.7211 | 7973.2109 | 1.787% | 0.2418%
2017-11-23 | 9 | 8141 | 142.5551 | 1.751% | 19.2938 | 0.237% | 161.8489 | 1.988% | 1762 | 8121.7062 | 7979.1511 | 1.787% | 0.2418%
2017-11-15 | 10 | 8143 | 142.5701 | 1.751% | 19.2987 | 0.237% | 161.8688 | 1.988% | 1763 | 8123.7013 | 7981.1312 | 1.786% | 0.2418%
2017-09-06 | 11 | 8144 | 142.5775 | 1.751% | 19.3012 | 0.237% | 161.8787 | 1.988% | 1764 | 8124.6988 | 7982.1213 | 1.786% | 0.2418%
2017-11-15 | 20 | 8149 | 142.6149 | 1.75% | 19.3136 | 0.237% | 161.9285 | 1.987% | 1765 | 8129.6864 | 7987.0715 | 1.786% | 0.2418%
2017-09-27 | 23 | 8151 | 142.6299 | 1.75% | 19.3185 | 0.237% | 161.9485 | 1.987% | 1766 | 8131.6815 | 7989.0515 | 1.785% | 0.2418%
2017-11-08 | 20 | 8159 | 142.6898 | 1.749% | 19.3383 | 0.237% | 162.0281 | 1.986% | 1767 | 8139.6617 | 7996.9719 | 1.784% | 0.2418%
2017-11-18 | 9 | 8159 | 142.6898 | 1.749% | 19.3383 | 0.237% | 162.0281 | 1.986% | 1768 | 8139.6617 | 7996.9719 | 1.784% | 0.2418%
2017-10-11 | 23 | 8160 | 142.6973 | 1.749% | 19.3408 | 0.237% | 162.0381 | 1.986% | 1769 | 8140.6592 | 7997.9619 | 1.784% | 0.2418%
2017-11-08 | 18 | 8164 | 142.7272 | 1.748% | 19.3507 | 0.237% | 162.0779 | 1.985% | 1770 | 8144.6493 | 8001.9221 | 1.784% | 0.2418%
2017-09-12 | 22 | 8165 | 142.7347 | 1.748% | 19.3532 | 0.237% | 162.0879 | 1.985% | 1771 | 8145.6468 | 8002.9121 | 1.784% | 0.2418%
2017-11-14 | 21 | 8165 | 142.7347 | 1.748% | 19.3532 | 0.237% | 162.0879 | 1.985% | 1772 | 8145.6468 | 8002.9121 | 1.784% | 0.2418%
2017-09-07 | 19 | 8168 | 142.7571 | 1.748% | 19.3606 | 0.237% | 162.1177 | 1.985% | 1773 | 8148.6394 | 8005.8823 | 1.783% | 0.2418%
2017-11-14 | 7 | 8169 | 142.7646 | 1.748% | 19.3631 | 0.237% | 162.1277 | 1.985% | 1774 | 8149.6369 | 8006.8723 | 1.783% | 0.2418%
2017-09-07 | 16 | 8171 | 142.7796 | 1.747% | 19.3681 | 0.237% | 162.1476 | 1.984% | 1775 | 8151.6319 | 8008.8524 | 1.783% | 0.2418%
2017-10-08 | 22 | 8173 | 142.7945 | 1.747% | 19.373 | 0.237% | 162.1675 | 1.984% | 1776 | 8153.627 | 8010.8325 | 1.783% | 0.2418%
2017-11-12 | 7 | 8174 | 142.802 | 1.747% | 19.3755 | 0.237% | 162.1775 | 1.984% | 1777 | 8154.6245 | 8011.8225 | 1.782% | 0.2418%
2017-09-20 | 11 | 8175 | 142.8095 | 1.747% | 19.378 | 0.237% | 162.1874 | 1.984% | 1778 | 8155.622 | 8012.8126 | 1.782% | 0.2418%
2017-09-22 | 11 | 8192 | 142.9367 | 1.745% | 19.42 | 0.2371% | 162.3567 | 1.982% | 1779 | 8172.58 | 8029.6433 | 1.78% | 0.2419%
2017-09-05 | 23 | 8193 | 142.9442 | 1.745% | 19.4225 | 0.2371% | 162.3667 | 1.982% | 1780 | 8173.5775 | 8030.6333 | 1.78% | 0.2419%
2017-11-25 | 7 | 8200 | 142.9965 | 1.744% | 19.4399 | 0.2371% | 162.4364 | 1.981% | 1781 | 8180.5601 | 8037.5636 | 1.779% | 0.2419%
2017-09-29 | 14 | 8201 | 143.004 | 1.744% | 19.4423 | 0.2371% | 162.4464 | 1.981% | 1782 | 8181.5577 | 8038.5536 | 1.779% | 0.2419%
2017-10-06 | 13 | 8202 | 143.0115 | 1.744% | 19.4448 | 0.2371% | 162.4563 | 1.981% | 1783 | 8182.5552 | 8039.5437 | 1.779% | 0.2419%
2017-10-04 | 20 | 8203 | 143.019 | 1.743% | 19.4473 | 0.2371% | 162.4663 | 1.981% | 1784 | 8183.5527 | 8040.5337 | 1.779% | 0.2419%
2017-11-11 | 20 | 8203 | 143.019 | 1.743% | 19.4473 | 0.2371% | 162.4663 | 1.981% | 1785 | 8183.5527 | 8040.5337 | 1.779% | 0.2419%
2017-10-04 | 18 | 8205 | 143.034 | 1.743% | 19.4522 | 0.2371% | 162.4862 | 1.98% | 1786 | 8185.5478 | 8042.5138 | 1.778% | 0.2419%
2017-11-23 | 10 | 8216 | 143.1163 | 1.742% | 19.4795 | 0.2371% | 162.5957 | 1.979% | 1787 | 8196.5205 | 8053.4043 | 1.777% | 0.2419%
2017-10-07 | 13 | 8218 | 143.1312 | 1.742% | 19.4844 | 0.2371% | 162.6156 | 1.979% | 1788 | 8198.5156 | 8055.3844 | 1.777% | 0.2419%
2017-09-06 | 18 | 8221 | 143.1537 | 1.741% | 19.4918 | 0.2371% | 162.6455 | 1.978% | 1789 | 8201.5082 | 8058.3545 | 1.776% | 0.2419%
2017-11-11 | 21 | 8227 | 143.1986 | 1.741% | 19.5067 | 0.2371% | 162.7053 | 1.978% | 1790 | 8207.4933 | 8064.2947 | 1.776% | 0.2419%
2017-09-08 | 17 | 8234 | 143.2509 | 1.74% | 19.524 | 0.2371% | 162.775 | 1.977% | 1791 | 8214.476 | 8071.225 | 1.775% | 0.2419%
2017-10-04 | 17 | 8235 | 143.2584 | 1.74% | 19.5265 | 0.2371% | 162.7849 | 1.977% | 1792 | 8215.4735 | 8072.2151 | 1.775% | 0.2419%
2017-11-16 | 9 | 8236 | 143.2659 | 1.74% | 19.529 | 0.2371% | 162.7949 | 1.977% | 1793 | 8216.471 | 8073.2051 | 1.775% | 0.2419%
2017-11-29 | 8 | 8240 | 143.2958 | 1.739% | 19.5389 | 0.2371% | 162.8347 | 1.976% | 1794 | 8220.4611 | 8077.1653 | 1.774% | 0.2419%
2017-09-08 | 18 | 8241 | 143.3033 | 1.739% | 19.5414 | 0.2371% | 162.8447 | 1.976% | 1795 | 8221.4586 | 8078.1553 | 1.774% | 0.2419%
2017-10-10 | 9 | 8245 | 143.3332 | 1.738% | 19.5513 | 0.2371% | 162.8845 | 1.976% | 1796 | 8225.4487 | 8082.1155 | 1.773% | 0.2419%
2017-09-15 | 22 | 8246 | 143.3407 | 1.738% | 19.5537 | 0.2371% | 162.8945 | 1.975% | 1797 | 8226.4463 | 8083.1055 | 1.773% | 0.2419%
2017-09-12 | 15 | 8247 | 143.3482 | 1.738% | 19.5562 | 0.2371% | 162.9044 | 1.975% | 1798 | 8227.4438 | 8084.0956 | 1.773% | 0.2419%
2017-09-02 | 15 | 8250 | 143.3707 | 1.738% | 19.5636 | 0.2371% | 162.9343 | 1.975% | 1799 | 8230.4364 | 8087.0657 | 1.773% | 0.2419%
2017-11-24 | 10 | 8257 | 143.423 | 1.737% | 19.581 | 0.2371% | 163.004 | 1.974% | 1800 | 8237.419 | 8093.996 | 1.772% | 0.2419%
2017-10-05 | 21 | 8260 | 143.4455 | 1.737% | 19.5884 | 0.2371% | 163.0339 | 1.974% | 1801 | 8240.4116 | 8096.9661 | 1.772% | 0.2419%
2017-11-14 | 8 | 8261 | 143.453 | 1.737% | 19.5909 | 0.2371% | 163.0438 | 1.974% | 1802 | 8241.4091 | 8097.9562 | 1.771% | 0.2419%
2017-10-12 | 22 | 8273 | 143.5427 | 1.735% | 19.6206 | 0.2372% | 163.1633 | 1.972% | 1803 | 8253.3794 | 8109.8367 | 1.77% | 0.2419%
2017-09-03 | 14 | 8274 | 143.5502 | 1.735% | 19.6231 | 0.2372% | 163.1733 | 1.972% | 1804 | 8254.3769 | 8110.8267 | 1.77% | 0.2419%
2017-11-24 | 6 | 8277 | 143.5727 | 1.735% | 19.6305 | 0.2372% | 163.2032 | 1.972% | 1805 | 8257.3695 | 8113.7968 | 1.769% | 0.2419%
2017-10-15 | 19 | 8295 | 143.7074 | 1.732% | 19.675 | 0.2372% | 163.3824 | 1.97% | 1806 | 8275.325 | 8131.6176 | 1.767% | 0.242%
2017-10-07 | 21 | 8297 | 143.7223 | 1.732% | 19.68 | 0.2372% | 163.4023 | 1.969% | 1807 | 8277.32 | 8133.5977 | 1.767% | 0.242%
2017-10-11 | 10 | 8303 | 143.7672 | 1.732% | 19.6949 | 0.2372% | 163.4621 | 1.969% | 1808 | 8283.3051 | 8139.5379 | 1.766% | 0.242%
2017-11-14 | 20 | 8303 | 143.7672 | 1.732% | 19.6949 | 0.2372% | 163.4621 | 1.969% | 1809 | 8283.3051 | 8139.5379 | 1.766% | 0.242%
2017-11-25 | 9 | 8308 | 143.8046 | 1.731% | 19.7072 | 0.2372% | 163.5119 | 1.968% | 1810 | 8288.2928 | 8144.4881 | 1.766% | 0.242%
2017-11-14 | 19 | 8310 | 143.8196 | 1.731% | 19.7122 | 0.2372% | 163.5318 | 1.968% | 1811 | 8290.2878 | 8146.4682 | 1.765% | 0.242%
2017-09-03 | 20 | 8311 | 143.8271 | 1.731% | 19.7147 | 0.2372% | 163.5417 | 1.968% | 1812 | 8291.2853 | 8147.4583 | 1.765% | 0.242%
2017-11-21 | 5 | 8313 | 143.842 | 1.73% | 19.7196 | 0.2372% | 163.5616 | 1.968% | 1813 | 8293.2804 | 8149.4384 | 1.765% | 0.242%
2017-09-23 | 12 | 8314 | 143.8495 | 1.73% | 19.7221 | 0.2372% | 163.5716 | 1.967% | 1814 | 8294.2779 | 8150.4284 | 1.765% | 0.242%
2017-09-17 | 13 | 8321 | 143.9019 | 1.729% | 19.7394 | 0.2372% | 163.6413 | 1.967% | 1815 | 8301.2606 | 8157.3587 | 1.764% | 0.242%
2017-10-15 | 20 | 8321 | 143.9019 | 1.729% | 19.7394 | 0.2372% | 163.6413 | 1.967% | 1816 | 8301.2606 | 8157.3587 | 1.764% | 0.242%
2017-09-29 | 17 | 8324 | 143.9243 | 1.729% | 19.7468 | 0.2372% | 163.6712 | 1.966% | 1817 | 8304.2532 | 8160.3288 | 1.764% | 0.242%
2017-09-19 | 12 | 8327 | 143.9468 | 1.729% | 19.7543 | 0.2372% | 163.7011 | 1.966% | 1818 | 8307.2457 | 8163.2989 | 1.763% | 0.242%
2017-10-15 | 16 | 8330 | 143.9692 | 1.728% | 19.7617 | 0.2372% | 163.7309 | 1.966% | 1819 | 8310.2383 | 8166.2691 | 1.763% | 0.242%
2017-09-02 | 21 | 8334 | 143.9992 | 1.728% | 19.7716 | 0.2372% | 163.7708 | 1.965% | 1820 | 8314.2284 | 8170.2292 | 1.762% | 0.242%
2017-09-22 | 22 | 8335 | 144.0066 | 1.728% | 19.7741 | 0.2372% | 163.7807 | 1.965% | 1821 | 8315.2259 | 8171.2193 | 1.762% | 0.242%
2017-11-08 | 19 | 8336 | 144.0141 | 1.728% | 19.7766 | 0.2372% | 163.7907 | 1.965% | 1822 | 8316.2234 | 8172.2093 | 1.762% | 0.242%
2017-11-27 | 19 | 8336 | 144.0141 | 1.728% | 19.7766 | 0.2372% | 163.7907 | 1.965% | 1823 | 8316.2234 | 8172.2093 | 1.762% | 0.242%
2017-09-26 | 12 | 8338 | 144.0291 | 1.727% | 19.7815 | 0.2372% | 163.8106 | 1.965% | 1824 | 8318.2185 | 8174.1894 | 1.762% | 0.242%
2017-09-04 | 22 | 8340 | 144.0441 | 1.727% | 19.7865 | 0.2372% | 163.8305 | 1.964% | 1825 | 8320.2135 | 8176.1695 | 1.762% | 0.242%
2017-10-08 | 12 | 8340 | 144.0441 | 1.727% | 19.7865 | 0.2372% | 163.8305 | 1.964% | 1826 | 8320.2135 | 8176.1695 | 1.762% | 0.242%
2017-09-18 | 12 | 8343 | 144.0665 | 1.727% | 19.7939 | 0.2373% | 163.8604 | 1.964% | 1827 | 8323.2061 | 8179.1396 | 1.761% | 0.242%
2017-09-18 | 22 | 8346 | 144.0889 | 1.726% | 19.8013 | 0.2373% | 163.8903 | 1.964% | 1828 | 8326.1987 | 8182.1097 | 1.761% | 0.242%
2017-09-07 | 17 | 8357 | 144.1712 | 1.725% | 19.8285 | 0.2373% | 163.9998 | 1.962% | 1829 | 8337.1715 | 8193.0002 | 1.76% | 0.242%
2017-09-13 | 22 | 8361 | 144.2012 | 1.725% | 19.8384 | 0.2373% | 164.0396 | 1.962% | 1830 | 8341.1616 | 8196.9604 | 1.759% | 0.242%
2017-10-30 | 9 | 8361 | 144.2012 | 1.725% | 19.8384 | 0.2373% | 164.0396 | 1.962% | 1831 | 8341.1616 | 8196.9604 | 1.759% | 0.242%
2017-09-29 | 15 | 8368 | 144.2536 | 1.724% | 19.8558 | 0.2373% | 164.1093 | 1.961% | 1832 | 8348.1442 | 8203.8907 | 1.758% | 0.242%
2017-11-20 | 19 | 8375 | 144.3059 | 1.723% | 19.8731 | 0.2373% | 164.179 | 1.96% | 1833 | 8355.1269 | 8210.821 | 1.758% | 0.242%
2017-10-12 | 11 | 8378 | 144.3284 | 1.723% | 19.8805 | 0.2373% | 164.2089 | 1.96% | 1834 | 8358.1195 | 8213.7911 | 1.757% | 0.242%
2017-09-07 | 18 | 8380 | 144.3433 | 1.722% | 19.8855 | 0.2373% | 164.2288 | 1.96% | 1835 | 8360.1145 | 8215.7712 | 1.757% | 0.242%
2017-10-10 | 23 | 8381 | 144.3508 | 1.722% | 19.888 | 0.2373% | 164.2388 | 1.96% | 1836 | 8361.112 | 8216.7612 | 1.757% | 0.242%
2017-11-28 | 10 | 8381 | 144.3508 | 1.722% | 19.888 | 0.2373% | 164.2388 | 1.96% | 1837 | 8361.112 | 8216.7612 | 1.757% | 0.242%
2017-11-12 | 9 | 8388 | 144.4032 | 1.722% | 19.9053 | 0.2373% | 164.3085 | 1.959% | 1838 | 8368.0947 | 8223.6915 | 1.756% | 0.242%
2017-09-25 | 13 | 8390 | 144.4182 | 1.721% | 19.9102 | 0.2373% | 164.3284 | 1.959% | 1839 | 8370.0898 | 8225.6716 | 1.756% | 0.2421%
2017-11-11 | 7 | 8390 | 144.4182 | 1.721% | 19.9102 | 0.2373% | 164.3284 | 1.959% | 1840 | 8370.0898 | 8225.6716 | 1.756% | 0.2421%
2017-09-21 | 22 | 8393 | 144.4406 | 1.721% | 19.9177 | 0.2373% | 164.3583 | 1.958% | 1841 | 8373.0823 | 8228.6417 | 1.755% | 0.2421%
2017-11-27 | 22 | 8394 | 144.4481 | 1.721% | 19.9201 | 0.2373% | 164.3682 | 1.958% | 1842 | 8374.0799 | 8229.6318 | 1.755% | 0.2421%
2017-09-04 | 13 | 8396 | 144.4631 | 1.721% | 19.9251 | 0.2373% | 164.3882 | 1.958% | 1843 | 8376.0749 | 8231.6118 | 1.755% | 0.2421%
2017-09-16 | 12 | 8396 | 144.4631 | 1.721% | 19.9251 | 0.2373% | 164.3882 | 1.958% | 1844 | 8376.0749 | 8231.6118 | 1.755% | 0.2421%
2017-09-28 | 23 | 8396 | 144.4631 | 1.721% | 19.9251 | 0.2373% | 164.3882 | 1.958% | 1845 | 8376.0749 | 8231.6118 | 1.755% | 0.2421%
2017-10-30 | 8 | 8396 | 144.4631 | 1.721% | 19.9251 | 0.2373% | 164.3882 | 1.958% | 1846 | 8376.0749 | 8231.6118 | 1.755% | 0.2421%
2017-11-18 | 8 | 8396 | 144.4631 | 1.721% | 19.9251 | 0.2373% | 164.3882 | 1.958% | 1847 | 8376.0749 | 8231.6118 | 1.755% | 0.2421%
2017-09-29 | 16 | 8397 | 144.4705 | 1.721% | 19.9276 | 0.2373% | 164.3981 | 1.958% | 1848 | 8377.0724 | 8232.6019 | 1.755% | 0.2421%
2017-11-30 | 9 | 8399 | 144.4855 | 1.72% | 19.9325 | 0.2373% | 164.418 | 1.958% | 1849 | 8379.0675 | 8234.582 | 1.755% | 0.2421%
2017-10-09 | 23 | 8400 | 144.493 | 1.72% | 19.935 | 0.2373% | 164.428 | 1.957% | 1850 | 8380.065 | 8235.572 | 1.754% | 0.2421%
2017-09-19 | 22 | 8403 | 144.5154 | 1.72% | 19.9424 | 0.2373% | 164.4579 | 1.957% | 1851 | 8383.0576 | 8238.5421 | 1.754% | 0.2421%
2017-09-25 | 22 | 8406 | 144.5379 | 1.719% | 19.9499 | 0.2373% | 164.4877 | 1.957% | 1852 | 8386.0501 | 8241.5123 | 1.754% | 0.2421%
2017-10-07 | 19 | 8417 | 144.6202 | 1.718% | 19.9771 | 0.2373% | 164.5973 | 1.956% | 1853 | 8397.0229 | 8252.4027 | 1.752% | 0.2421%
2017-10-06 | 20 | 8422 | 144.6576 | 1.718% | 19.9895 | 0.2373% | 164.6471 | 1.955% | 1854 | 8402.0105 | 8257.3529 | 1.752% | 0.2421%
2017-09-14 | 22 | 8430 | 144.7175 | 1.717% | 20.0093 | 0.2374% | 164.7267 | 1.954% | 1855 | 8409.9907 | 8265.2733 | 1.751% | 0.2421%
2017-11-12 | 8 | 8431 | 144.7249 | 1.717% | 20.0117 | 0.2374% | 164.7367 | 1.954% | 1856 | 8410.9883 | 8266.2633 | 1.751% | 0.2421%
2017-10-05 | 14 | 8434 | 144.7474 | 1.716% | 20.0192 | 0.2374% | 164.7666 | 1.954% | 1857 | 8413.9808 | 8269.2334 | 1.75% | 0.2421%
2017-11-20 | 22 | 8434 | 144.7474 | 1.716% | 20.0192 | 0.2374% | 164.7666 | 1.954% | 1858 | 8413.9808 | 8269.2334 | 1.75% | 0.2421%
2017-09-02 | 20 | 8437 | 144.7698 | 1.716% | 20.0266 | 0.2374% | 164.7964 | 1.953% | 1859 | 8416.9734 | 8272.2036 | 1.75% | 0.2421%
2017-10-09 | 10 | 8445 | 144.8297 | 1.715% | 20.0464 | 0.2374% | 164.8761 | 1.952% | 1860 | 8424.9536 | 8280.1239 | 1.749% | 0.2421%
2017-09-01 | 21 | 8450 | 144.8671 | 1.714% | 20.0588 | 0.2374% | 164.9259 | 1.952% | 1861 | 8429.9412 | 8285.0741 | 1.749% | 0.2421%
2017-11-25 | 8 | 8452 | 144.8821 | 1.714% | 20.0637 | 0.2374% | 164.9458 | 1.952% | 1862 | 8431.9363 | 8287.0542 | 1.748% | 0.2421%
2017-09-06 | 17 | 8454 | 144.897 | 1.714% | 20.0687 | 0.2374% | 164.9657 | 1.951% | 1863 | 8433.9313 | 8289.0343 | 1.748% | 0.2421%
2017-10-07 | 14 | 8456 | 144.912 | 1.714% | 20.0736 | 0.2374% | 164.9856 | 1.951% | 1864 | 8435.9264 | 8291.0144 | 1.748% | 0.2421%
2017-09-12 | 16 | 8481 | 145.099 | 1.711% | 20.1355 | 0.2374% | 165.2346 | 1.948% | 1865 | 8460.8645 | 8315.7654 | 1.745% | 0.2421%
2017-11-27 | 20 | 8500 | 145.2412 | 1.709% | 20.1826 | 0.2374% | 165.4238 | 1.946% | 1866 | 8479.8174 | 8334.5762 | 1.743% | 0.2422%
2017-09-21 | 11 | 8509 | 145.3085 | 1.708% | 20.2049 | 0.2375% | 165.5134 | 1.945% | 1867 | 8488.7951 | 8343.4866 | 1.742% | 0.2422%
2017-10-07 | 18 | 8510 | 145.316 | 1.708% | 20.2073 | 0.2375% | 165.5234 | 1.945% | 1868 | 8489.7927 | 8344.4766 | 1.741% | 0.2422%
2017-10-07 | 20 | 8511 | 145.3235 | 1.707% | 20.2098 | 0.2375% | 165.5333 | 1.945% | 1869 | 8490.7902 | 8345.4667 | 1.741% | 0.2422%
2017-10-15 | 18 | 8516 | 145.3609 | 1.707% | 20.2222 | 0.2375% | 165.5831 | 1.944% | 1870 | 8495.7778 | 8350.4169 | 1.741% | 0.2422%
2017-09-24 | 13 | 8521 | 145.3983 | 1.706% | 20.2346 | 0.2375% | 165.6329 | 1.944% | 1871 | 8500.7654 | 8355.3671 | 1.74% | 0.2422%
2017-11-17 | 9 | 8524 | 145.4208 | 1.706% | 20.242 | 0.2375% | 165.6628 | 1.943% | 1872 | 8503.758 | 8358.3372 | 1.74% | 0.2422%
2017-09-01 | 11 | 8525 | 145.4283 | 1.706% | 20.2445 | 0.2375% | 165.6727 | 1.943% | 1873 | 8504.7555 | 8359.3273 | 1.74% | 0.2422%
2017-10-15 | 17 | 8539 | 145.533 | 1.704% | 20.2791 | 0.2375% | 165.8121 | 1.942% | 1874 | 8518.7209 | 8373.1879 | 1.738% | 0.2422%
2017-09-23 | 21 | 8542 | 145.5555 | 1.704% | 20.2866 | 0.2375% | 165.842 | 1.941% | 1875 | 8521.7134 | 8376.158 | 1.738% | 0.2422%
2017-09-05 | 11 | 8546 | 145.5854 | 1.704% | 20.2965 | 0.2375% | 165.8818 | 1.941% | 1876 | 8525.7035 | 8380.1182 | 1.737% | 0.2422%
2017-09-13 | 13 | 8553 | 145.6378 | 1.703% | 20.3138 | 0.2375% | 165.9516 | 1.94% | 1877 | 8532.6862 | 8387.0484 | 1.736% | 0.2422%
2017-11-28 | 5 | 8553 | 145.6378 | 1.703% | 20.3138 | 0.2375% | 165.9516 | 1.94% | 1878 | 8532.6862 | 8387.0484 | 1.736% | 0.2422%
2017-11-30 | 7 | 8555 | 145.6527 | 1.703% | 20.3187 | 0.2375% | 165.9715 | 1.94% | 1879 | 8534.6813 | 8389.0285 | 1.736% | 0.2422%
2017-09-14 | 12 | 8560 | 145.6901 | 1.702% | 20.3311 | 0.2375% | 166.0213 | 1.94% | 1880 | 8539.6689 | 8393.9787 | 1.736% | 0.2422%
2017-09-06 | 12 | 8566 | 145.735 | 1.701% | 20.346 | 0.2375% | 166.081 | 1.939% | 1881 | 8545.654 | 8399.919 | 1.735% | 0.2422%
2017-11-27 | 10 | 8572 | 145.7799 | 1.701% | 20.3608 | 0.2375% | 166.1408 | 1.938% | 1882 | 8551.6392 | 8405.8592 | 1.734% | 0.2422%
2017-11-27 | 21 | 8574 | 145.7949 | 1.7% | 20.3658 | 0.2375% | 166.1607 | 1.938% | 1883 | 8553.6342 | 8407.8393 | 1.734% | 0.2422%
2017-11-20 | 20 | 8581 | 145.8473 | 1.7% | 20.3831 | 0.2375% | 166.2304 | 1.937% | 1884 | 8560.6169 | 8414.7696 | 1.733% | 0.2422%
2017-10-10 | 10 | 8582 | 145.8547 | 1.7% | 20.3856 | 0.2375% | 166.2403 | 1.937% | 1885 | 8561.6144 | 8415.7597 | 1.733% | 0.2422%
2017-11-11 | 10 | 8584 | 145.8697 | 1.699% | 20.3905 | 0.2375% | 166.2602 | 1.937% | 1886 | 8563.6095 | 8417.7398 | 1.733% | 0.2422%
2017-10-07 | 17 | 8595 | 145.952 | 1.698% | 20.4178 | 0.2376% | 166.3698 | 1.936% | 1887 | 8574.5822 | 8428.6302 | 1.732% | 0.2422%
2017-10-11 | 11 | 8600 | 145.9894 | 1.698% | 20.4301 | 0.2376% | 166.4196 | 1.935% | 1888 | 8579.5699 | 8433.5804 | 1.731% | 0.2422%
2017-09-02 | 16 | 8602 | 146.0044 | 1.697% | 20.4351 | 0.2376% | 166.4395 | 1.935% | 1889 | 8581.5649 | 8435.5605 | 1.731% | 0.2422%
2017-09-16 | 21 | 8603 | 146.0119 | 1.697% | 20.4376 | 0.2376% | 166.4494 | 1.935% | 1890 | 8582.5624 | 8436.5506 | 1.731% | 0.2423%
2017-11-20 | 21 | 8606 | 146.0343 | 1.697% | 20.445 | 0.2376% | 166.4793 | 1.934% | 1891 | 8585.555 | 8439.5207 | 1.73% | 0.2423%
2017-10-05 | 19 | 8607 | 146.0418 | 1.697% | 20.4475 | 0.2376% | 166.4893 | 1.934% | 1892 | 8586.5525 | 8440.5107 | 1.73% | 0.2423%
2017-10-07 | 15 | 8607 | 146.0418 | 1.697% | 20.4475 | 0.2376% | 166.4893 | 1.934% | 1893 | 8586.5525 | 8440.5107 | 1.73% | 0.2423%
2017-09-24 | 21 | 8608 | 146.0493 | 1.697% | 20.45 | 0.2376% | 166.4992 | 1.934% | 1894 | 8587.55 | 8441.5008 | 1.73% | 0.2423%
2017-10-08 | 21 | 8618 | 146.1241 | 1.696% | 20.4747 | 0.2376% | 166.5988 | 1.933% | 1895 | 8597.5253 | 8451.4012 | 1.729% | 0.2423%
2017-11-21 | 10 | 8619 | 146.1316 | 1.695% | 20.4772 | 0.2376% | 166.6088 | 1.933% | 1896 | 8598.5228 | 8452.3912 | 1.729% | 0.2423%
2017-11-20 | 6 | 8621 | 146.1466 | 1.695% | 20.4821 | 0.2376% | 166.6287 | 1.933% | 1897 | 8600.5179 | 8454.3713 | 1.729% | 0.2423%
2017-11-20 | 10 | 8621 | 146.1466 | 1.695% | 20.4821 | 0.2376% | 166.6287 | 1.933% | 1898 | 8600.5179 | 8454.3713 | 1.729% | 0.2423%
2017-09-03 | 15 | 8632 | 146.2289 | 1.694% | 20.5094 | 0.2376% | 166.7382 | 1.932% | 1899 | 8611.4906 | 8465.2618 | 1.727% | 0.2423%
2017-10-06 | 14 | 8635 | 146.2513 | 1.694% | 20.5168 | 0.2376% | 166.7681 | 1.931% | 1900 | 8614.4832 | 8468.2319 | 1.727% | 0.2423%
2017-10-05 | 20 | 8636 | 146.2588 | 1.694% | 20.5193 | 0.2376% | 166.7781 | 1.931% | 1901 | 8615.4807 | 8469.2219 | 1.727% | 0.2423%
2017-09-27 | 11 | 8639 | 146.2812 | 1.693% | 20.5267 | 0.2376% | 166.8079 | 1.931% | 1902 | 8618.4733 | 8472.1921 | 1.727% | 0.2423%
2017-10-08 | 13 | 8644 | 146.3186 | 1.693% | 20.5391 | 0.2376% | 166.8577 | 1.93% | 1903 | 8623.4609 | 8477.1423 | 1.726% | 0.2423%
2017-09-28 | 11 | 8654 | 146.3935 | 1.692% | 20.5638 | 0.2376% | 166.9573 | 1.929% | 1904 | 8633.4362 | 8487.0427 | 1.725% | 0.2423%
2017-09-01 | 20 | 8659 | 146.4309 | 1.691% | 20.5762 | 0.2376% | 167.0071 | 1.929% | 1905 | 8638.4238 | 8491.9929 | 1.724% | 0.2423%
2017-10-06 | 19 | 8662 | 146.4533 | 1.691% | 20.5836 | 0.2376% | 167.037 | 1.928% | 1906 | 8641.4164 | 8494.963 | 1.724% | 0.2423%
2017-10-07 | 16 | 8666 | 146.4833 | 1.69% | 20.5935 | 0.2376% | 167.0768 | 1.928% | 1907 | 8645.4065 | 8498.9232 | 1.724% | 0.2423%
2017-11-16 | 7 | 8668 | 146.4982 | 1.69% | 20.5985 | 0.2376% | 167.0967 | 1.928% | 1908 | 8647.4015 | 8500.9033 | 1.723% | 0.2423%
2017-09-02 | 19 | 8669 | 146.5057 | 1.69% | 20.601 | 0.2376% | 167.1067 | 1.928% | 1909 | 8648.399 | 8501.8933 | 1.723% | 0.2423%
2017-11-17 | 7 | 8669 | 146.5057 | 1.69% | 20.601 | 0.2376% | 167.1067 | 1.928% | 1910 | 8648.399 | 8501.8933 | 1.723% | 0.2423%
2017-11-15 | 9 | 8687 | 146.6404 | 1.688% | 20.6455 | 0.2377% | 167.2859 | 1.926% | 1911 | 8666.3545 | 8519.7141 | 1.721% | 0.2423%
2017-09-15 | 12 | 8690 | 146.6628 | 1.688% | 20.653 | 0.2377% | 167.3158 | 1.925% | 1912 | 8669.347 | 8522.6842 | 1.721% | 0.2423%
2017-10-12 | 12 | 8691 | 146.6703 | 1.688% | 20.6554 | 0.2377% | 167.3257 | 1.925% | 1913 | 8670.3446 | 8523.6743 | 1.721% | 0.2423%
2017-09-12 | 17 | 8706 | 146.7825 | 1.686% | 20.6926 | 0.2377% | 167.4751 | 1.924% | 1914 | 8685.3074 | 8538.5249 | 1.719% | 0.2423%
2017-11-24 | 7 | 8723 | 146.9097 | 1.684% | 20.7347 | 0.2377% | 167.6444 | 1.922% | 1915 | 8702.2653 | 8555.3556 | 1.717% | 0.2424%
2017-09-12 | 21 | 8726 | 146.9322 | 1.684% | 20.7421 | 0.2377% | 167.6743 | 1.922% | 1916 | 8705.2579 | 8558.3257 | 1.717% | 0.2424%
2017-11-11 | 8 | 8731 | 146.9696 | 1.683% | 20.7545 | 0.2377% | 167.7241 | 1.921% | 1917 | 8710.2455 | 8563.2759 | 1.716% | 0.2424%
2017-09-17 | 21 | 8743 | 147.0594 | 1.682% | 20.7842 | 0.2377% | 167.8436 | 1.92% | 1918 | 8722.2158 | 8575.1564 | 1.715% | 0.2424%
2017-10-05 | 15 | 8745 | 147.0743 | 1.682% | 20.7891 | 0.2377% | 167.8635 | 1.92% | 1919 | 8724.2109 | 8577.1365 | 1.715% | 0.2424%
2017-10-05 | 18 | 8749 | 147.1043 | 1.681% | 20.799 | 0.2377% | 167.9033 | 1.919% | 1920 | 8728.201 | 8581.0967 | 1.714% | 0.2424%
2017-11-11 | 9 | 8753 | 147.1342 | 1.681% | 20.8089 | 0.2377% | 167.9431 | 1.919% | 1921 | 8732.1911 | 8585.0569 | 1.714% | 0.2424%
2017-09-18 | 13 | 8768 | 147.2464 | 1.679% | 20.8461 | 0.2378% | 168.0925 | 1.917% | 1922 | 8747.1539 | 8599.9075 | 1.712% | 0.2424%
2017-09-12 | 19 | 8774 | 147.2913 | 1.679% | 20.8609 | 0.2378% | 168.1523 | 1.916% | 1923 | 8753.1391 | 8605.8477 | 1.712% | 0.2424%
2017-10-08 | 15 | 8783 | 147.3587 | 1.678% | 20.8832 | 0.2378% | 168.2419 | 1.916% | 1924 | 8762.1168 | 8614.7581 | 1.711% | 0.2424%
2017-09-26 | 13 | 8785 | 147.3736 | 1.678% | 20.8882 | 0.2378% | 168.2618 | 1.915% | 1925 | 8764.1118 | 8616.7382 | 1.71% | 0.2424%
2017-10-05 | 16 | 8785 | 147.3736 | 1.678% | 20.8882 | 0.2378% | 168.2618 | 1.915% | 1926 | 8764.1118 | 8616.7382 | 1.71% | 0.2424%
2017-11-27 | 6 | 8787 | 147.3886 | 1.677% | 20.8931 | 0.2378% | 168.2817 | 1.915% | 1927 | 8766.1069 | 8618.7183 | 1.71% | 0.2424%
2017-10-08 | 19 | 8791 | 147.4185 | 1.677% | 20.903 | 0.2378% | 168.3215 | 1.915% | 1928 | 8770.097 | 8622.6785 | 1.71% | 0.2424%
2017-09-12 | 20 | 8792 | 147.426 | 1.677% | 20.9055 | 0.2378% | 168.3315 | 1.915% | 1929 | 8771.0945 | 8623.6685 | 1.71% | 0.2424%
2017-11-16 | 8 | 8795 | 147.4485 | 1.677% | 20.9129 | 0.2378% | 168.3614 | 1.914% | 1930 | 8774.0871 | 8626.6386 | 1.709% | 0.2424%
2017-09-25 | 14 | 8797 | 147.4634 | 1.676% | 20.9179 | 0.2378% | 168.3813 | 1.914% | 1931 | 8776.0821 | 8628.6187 | 1.709% | 0.2424%
2017-09-26 | 22 | 8797 | 147.4634 | 1.676% | 20.9179 | 0.2378% | 168.3813 | 1.914% | 1932 | 8776.0821 | 8628.6187 | 1.709% | 0.2424%
2017-09-06 | 16 | 8801 | 147.4934 | 1.676% | 20.9278 | 0.2378% | 168.4211 | 1.914% | 1933 | 8780.0722 | 8632.5789 | 1.709% | 0.2424%
2017-09-12 | 18 | 8805 | 147.5233 | 1.675% | 20.9377 | 0.2378% | 168.461 | 1.913% | 1934 | 8784.0623 | 8636.539 | 1.708% | 0.2424%
2017-09-02 | 17 | 8806 | 147.5308 | 1.675% | 20.9402 | 0.2378% | 168.4709 | 1.913% | 1935 | 8785.0598 | 8637.5291 | 1.708% | 0.2424%
2017-11-30 | 8 | 8816 | 147.6056 | 1.674% | 20.9649 | 0.2378% | 168.5705 | 1.912% | 1936 | 8795.0351 | 8647.4295 | 1.707% | 0.2424%
2017-10-08 | 18 | 8817 | 147.6131 | 1.674% | 20.9674 | 0.2378% | 168.5805 | 1.912% | 1937 | 8796.0326 | 8648.4195 | 1.707% | 0.2424%
2017-10-08 | 20 | 8821 | 147.643 | 1.674% | 20.9773 | 0.2378% | 168.6203 | 1.912% | 1938 | 8800.0227 | 8652.3797 | 1.706% | 0.2424%
2017-10-08 | 16 | 8822 | 147.6505 | 1.674% | 20.9798 | 0.2378% | 168.6302 | 1.911% | 1939 | 8801.0202 | 8653.3698 | 1.706% | 0.2424%
2017-10-08 | 14 | 8826 | 147.6804 | 1.673% | 20.9897 | 0.2378% | 168.6701 | 1.911% | 1940 | 8805.0103 | 8657.3299 | 1.706% | 0.2424%
2017-09-22 | 12 | 8831 | 147.7178 | 1.673% | 21.002 | 0.2378% | 168.7199 | 1.911% | 1941 | 8809.998 | 8662.2801 | 1.705% | 0.2425%
2017-10-12 | 21 | 8834 | 147.7403 | 1.672% | 21.0095 | 0.2378% | 168.7497 | 1.91% | 1942 | 8812.9905 | 8665.2503 | 1.705% | 0.2425%
2017-10-05 | 17 | 8843 | 147.8076 | 1.671% | 21.0318 | 0.2378% | 168.8394 | 1.909% | 1943 | 8821.9682 | 8674.1606 | 1.704% | 0.2425%
2017-10-08 | 17 | 8844 | 147.8151 | 1.671% | 21.0342 | 0.2378% | 168.8493 | 1.909% | 1944 | 8822.9658 | 8675.1507 | 1.704% | 0.2425%
2017-09-15 | 21 | 8848 | 147.845 | 1.671% | 21.0441 | 0.2378% | 168.8891 | 1.909% | 1945 | 8826.9559 | 8679.1109 | 1.703% | 0.2425%
2017-09-03 | 19 | 8855 | 147.8974 | 1.67% | 21.0615 | 0.2378% | 168.9589 | 1.908% | 1946 | 8833.9385 | 8686.0411 | 1.703% | 0.2425%
2017-09-02 | 18 | 8861 | 147.9423 | 1.67% | 21.0763 | 0.2379% | 169.0186 | 1.907% | 1947 | 8839.9237 | 8691.9814 | 1.702% | 0.2425%
2017-09-17 | 14 | 8872 | 148.0246 | 1.668% | 21.1035 | 0.2379% | 169.1281 | 1.906% | 1948 | 8850.8965 | 8702.8719 | 1.701% | 0.2425%
2017-10-09 | 11 | 8874 | 148.0396 | 1.668% | 21.1085 | 0.2379% | 169.1481 | 1.906% | 1949 | 8852.8915 | 8704.8519 | 1.701% | 0.2425%
2017-11-24 | 9 | 8878 | 148.0695 | 1.668% | 21.1184 | 0.2379% | 169.1879 | 1.906% | 1950 | 8856.8816 | 8708.8121 | 1.7% | 0.2425%
2017-09-16 | 20 | 8879 | 148.077 | 1.668% | 21.1209 | 0.2379% | 169.1978 | 1.906% | 1951 | 8857.8791 | 8709.8022 | 1.7% | 0.2425%
2017-09-20 | 12 | 8883 | 148.1069 | 1.667% | 21.1308 | 0.2379% | 169.2377 | 1.905% | 1952 | 8861.8692 | 8713.7623 | 1.7% | 0.2425%
2017-09-06 | 13 | 8886 | 148.1293 | 1.667% | 21.1382 | 0.2379% | 169.2676 | 1.905% | 1953 | 8864.8618 | 8716.7324 | 1.699% | 0.2425%
2017-09-14 | 13 | 8886 | 148.1293 | 1.667% | 21.1382 | 0.2379% | 169.2676 | 1.905% | 1954 | 8864.8618 | 8716.7324 | 1.699% | 0.2425%
2017-09-19 | 13 | 8886 | 148.1293 | 1.667% | 21.1382 | 0.2379% | 169.2676 | 1.905% | 1955 | 8864.8618 | 8716.7324 | 1.699% | 0.2425%
2017-09-23 | 13 | 8890 | 148.1593 | 1.667% | 21.1481 | 0.2379% | 169.3074 | 1.904% | 1956 | 8868.8519 | 8720.6926 | 1.699% | 0.2425%
2017-10-06 | 15 | 8918 | 148.3688 | 1.664% | 21.2174 | 0.2379% | 169.5862 | 1.902% | 1957 | 8896.7826 | 8748.4138 | 1.696% | 0.2425%
2017-09-03 | 16 | 8924 | 148.4137 | 1.663% | 21.2323 | 0.2379% | 169.646 | 1.901% | 1958 | 8902.7677 | 8754.354 | 1.695% | 0.2425%
2017-09-20 | 22 | 8934 | 148.4885 | 1.662% | 21.257 | 0.2379% | 169.7455 | 1.9% | 1959 | 8912.743 | 8764.2545 | 1.694% | 0.2425%
2017-10-11 | 12 | 8934 | 148.4885 | 1.662% | 21.257 | 0.2379% | 169.7455 | 1.9% | 1960 | 8912.743 | 8764.2545 | 1.694% | 0.2425%
2017-09-23 | 20 | 8939 | 148.5259 | 1.662% | 21.2694 | 0.2379% | 169.7953 | 1.899% | 1961 | 8917.7306 | 8769.2047 | 1.694% | 0.2425%
2017-11-17 | 8 | 8942 | 148.5483 | 1.661% | 21.2769 | 0.2379% | 169.8252 | 1.899% | 1962 | 8920.7231 | 8772.1748 | 1.693% | 0.2425%
2017-09-04 | 14 | 8946 | 148.5783 | 1.661% | 21.2868 | 0.2379% | 169.865 | 1.899% | 1963 | 8924.7132 | 8776.135 | 1.693% | 0.2426%
2017-11-21 | 6 | 8950 | 148.6082 | 1.66% | 21.2967 | 0.238% | 169.9049 | 1.898% | 1964 | 8928.7033 | 8780.0951 | 1.693% | 0.2426%
2017-11-15 | 7 | 8955 | 148.6456 | 1.66% | 21.309 | 0.238% | 169.9546 | 1.898% | 1965 | 8933.691 | 8785.0454 | 1.692% | 0.2426%
2017-10-12 | 19 | 8959 | 148.6755 | 1.66% | 21.3189 | 0.238% | 169.9945 | 1.897% | 1966 | 8937.6811 | 8789.0055 | 1.692% | 0.2426%
2017-09-24 | 20 | 8965 | 148.7204 | 1.659% | 21.3338 | 0.238% | 170.0542 | 1.897% | 1967 | 8943.6662 | 8794.9458 | 1.691% | 0.2426%
2017-10-06 | 18 | 8967 | 148.7354 | 1.659% | 21.3387 | 0.238% | 170.0741 | 1.897% | 1968 | 8945.6613 | 8796.9259 | 1.691% | 0.2426%
2017-09-17 | 20 | 8978 | 148.8177 | 1.658% | 21.366 | 0.238% | 170.1837 | 1.896% | 1969 | 8956.634 | 8807.8163 | 1.69% | 0.2426%
2017-10-12 | 13 | 8989 | 148.9 | 1.656% | 21.3932 | 0.238% | 170.2932 | 1.894% | 1970 | 8967.6068 | 8818.7068 | 1.688% | 0.2426%
2017-09-16 | 13 | 8992 | 148.9225 | 1.656% | 21.4006 | 0.238% | 170.3231 | 1.894% | 1971 | 8970.5994 | 8821.6769 | 1.688% | 0.2426%
2017-09-25 | 15 | 8997 | 148.9599 | 1.656% | 21.413 | 0.238% | 170.3729 | 1.894% | 1972 | 8975.587 | 8826.6271 | 1.688% | 0.2426%
2017-09-01 | 19 | 9003 | 149.0048 | 1.655% | 21.4279 | 0.238% | 170.4326 | 1.893% | 1973 | 8981.5721 | 8832.5674 | 1.687% | 0.2426%
2017-10-11 | 22 | 9003 | 149.0048 | 1.655% | 21.4279 | 0.238% | 170.4326 | 1.893% | 1974 | 8981.5721 | 8832.5674 | 1.687% | 0.2426%
2017-10-06 | 16 | 9009 | 149.0497 | 1.654% | 21.4427 | 0.238% | 170.4924 | 1.892% | 1975 | 8987.5573 | 8838.5076 | 1.686% | 0.2426%
2017-09-24 | 14 | 9013 | 149.0796 | 1.654% | 21.4526 | 0.238% | 170.5322 | 1.892% | 1976 | 8991.5474 | 8842.4678 | 1.686% | 0.2426%
2017-09-22 | 21 | 9020 | 149.132 | 1.653% | 21.47 | 0.238% | 170.6019 | 1.891% | 1977 | 8998.53 | 8849.3981 | 1.685% | 0.2426%
2017-09-01 | 12 | 9024 | 149.1619 | 1.653% | 21.4799 | 0.238% | 170.6417 | 1.891% | 1978 | 9002.5201 | 8853.3583 | 1.685% | 0.2426%
2017-10-12 | 18 | 9028 | 149.1918 | 1.653% | 21.4898 | 0.238% | 170.6816 | 1.891% | 1979 | 9006.5102 | 8857.3184 | 1.684% | 0.2426%
2017-09-13 | 21 | 9035 | 149.2442 | 1.652% | 21.5071 | 0.238% | 170.7513 | 1.89% | 1980 | 9013.4929 | 8864.2487 | 1.684% | 0.2426%
2017-09-13 | 14 | 9038 | 149.2666 | 1.652% | 21.5145 | 0.238% | 170.7812 | 1.89% | 1981 | 9016.4855 | 8867.2188 | 1.683% | 0.2426%
2017-09-25 | 21 | 9039 | 149.2741 | 1.651% | 21.517 | 0.238% | 170.7911 | 1.889% | 1982 | 9017.483 | 8868.2089 | 1.683% | 0.2426%
2017-11-24 | 8 | 9044 | 149.3115 | 1.651% | 21.5294 | 0.2381% | 170.8409 | 1.889% | 1983 | 9022.4706 | 8873.1591 | 1.683% | 0.2426%
2017-09-06 | 14 | 9051 | 149.3639 | 1.65% | 21.5467 | 0.2381% | 170.9106 | 1.888% | 1984 | 9029.4533 | 8880.0894 | 1.682% | 0.2426%
2017-11-15 | 8 | 9065 | 149.4687 | 1.649% | 21.5814 | 0.2381% | 171.05 | 1.887% | 1985 | 9043.4186 | 8893.95 | 1.681% | 0.2427%
2017-09-06 | 15 | 9067 | 149.4836 | 1.649% | 21.5863 | 0.2381% | 171.0699 | 1.887% | 1986 | 9045.4137 | 8895.9301 | 1.68% | 0.2427%
2017-09-04 | 21 | 9071 | 149.5136 | 1.648% | 21.5962 | 0.2381% | 171.1098 | 1.886% | 1987 | 9049.4038 | 8899.8902 | 1.68% | 0.2427%
2017-09-18 | 21 | 9072 | 149.521 | 1.648% | 21.5987 | 0.2381% | 171.1197 | 1.886% | 1988 | 9050.4013 | 8900.8803 | 1.68% | 0.2427%
2017-09-14 | 21 | 9078 | 149.5659 | 1.648% | 21.6136 | 0.2381% | 171.1795 | 1.886% | 1989 | 9056.3864 | 8906.8205 | 1.679% | 0.2427%
2017-10-06 | 17 | 9079 | 149.5734 | 1.647% | 21.616 | 0.2381% | 171.1894 | 1.886% | 1990 | 9057.384 | 8907.8106 | 1.679% | 0.2427%
2017-09-24 | 19 | 9097 | 149.7081 | 1.646% | 21.6606 | 0.2381% | 171.3687 | 1.884% | 1991 | 9075.3394 | 8925.6313 | 1.677% | 0.2427%
2017-10-12 | 20 | 9104 | 149.7605 | 1.645% | 21.6779 | 0.2381% | 171.4384 | 1.883% | 1992 | 9082.3221 | 8932.5616 | 1.677% | 0.2427%
2017-09-21 | 21 | 9105 | 149.7679 | 1.645% | 21.6804 | 0.2381% | 171.4483 | 1.883% | 1993 | 9083.3196 | 8933.5517 | 1.676% | 0.2427%
2017-09-27 | 22 | 9107 | 149.7829 | 1.645% | 21.6853 | 0.2381% | 171.4683 | 1.883% | 1994 | 9085.3147 | 8935.5317 | 1.676% | 0.2427%
2017-09-05 | 22 | 9108 | 149.7904 | 1.645% | 21.6878 | 0.2381% | 171.4782 | 1.883% | 1995 | 9086.3122 | 8936.5218 | 1.676% | 0.2427%
2017-10-10 | 11 | 9122 | 149.8951 | 1.643% | 21.7225 | 0.2381% | 171.6176 | 1.881% | 1996 | 9100.2775 | 8950.3824 | 1.675% | 0.2427%
2017-09-03 | 17 | 9129 | 149.9475 | 1.643% | 21.7398 | 0.2381% | 171.6873 | 1.881% | 1997 | 9107.2602 | 8957.3127 | 1.674% | 0.2427%
2017-10-10 | 22 | 9144 | 150.0598 | 1.641% | 21.7769 | 0.2382% | 171.8367 | 1.879% | 1998 | 9122.2231 | 8972.1633 | 1.673% | 0.2427%
2017-09-03 | 18 | 9149 | 150.0972 | 1.641% | 21.7893 | 0.2382% | 171.8865 | 1.879% | 1999 | 9127.2107 | 8977.1135 | 1.672% | 0.2427%
2017-10-09 | 22 | 9152 | 150.1196 | 1.64% | 21.7968 | 0.2382% | 171.9164 | 1.878% | 2000 | 9130.2032 | 8980.0836 | 1.672% | 0.2427%
2017-09-18 | 14 | 9164 | 150.2094 | 1.639% | 21.8265 | 0.2382% | 172.0359 | 1.877% | 2001 | 9142.1735 | 8991.9641 | 1.67% | 0.2427%
2017-09-16 | 19 | 9172 | 150.2693 | 1.638% | 21.8463 | 0.2382% | 172.1155 | 1.877% | 2002 | 9150.1537 | 8999.8845 | 1.67% | 0.2427%
2017-09-05 | 12 | 9185 | 150.3665 | 1.637% | 21.8785 | 0.2382% | 172.245 | 1.875% | 2003 | 9163.1215 | 9012.755 | 1.668% | 0.2427%
2017-09-27 | 12 | 9188 | 150.389 | 1.637% | 21.8859 | 0.2382% | 172.2749 | 1.875% | 2004 | 9166.1141 | 9015.7251 | 1.668% | 0.2428%
2017-09-19 | 21 | 9198 | 150.4638 | 1.636% | 21.9106 | 0.2382% | 172.3744 | 1.874% | 2005 | 9176.0894 | 9025.6256 | 1.667% | 0.2428%
2017-09-25 | 16 | 9205 | 150.5162 | 1.635% | 21.928 | 0.2382% | 172.4441 | 1.873% | 2006 | 9183.072 | 9032.5559 | 1.666% | 0.2428%
2017-10-09 | 12 | 9205 | 150.5162 | 1.635% | 21.928 | 0.2382% | 172.4441 | 1.873% | 2007 | 9183.072 | 9032.5559 | 1.666% | 0.2428%
2017-09-15 | 20 | 9212 | 150.5685 | 1.634% | 21.9453 | 0.2382% | 172.5138 | 1.873% | 2008 | 9190.0547 | 9039.4862 | 1.666% | 0.2428%
2017-09-15 | 13 | 9218 | 150.6134 | 1.634% | 21.9602 | 0.2382% | 172.5736 | 1.872% | 2009 | 9196.0398 | 9045.4264 | 1.665% | 0.2428%
2017-09-13 | 20 | 9229 | 150.6957 | 1.633% | 21.9874 | 0.2382% | 172.6831 | 1.871% | 2010 | 9207.0126 | 9056.3169 | 1.664% | 0.2428%
2017-09-17 | 19 | 9229 | 150.6957 | 1.633% | 21.9874 | 0.2382% | 172.6831 | 1.871% | 2011 | 9207.0126 | 9056.3169 | 1.664% | 0.2428%
2017-09-17 | 15 | 9232 | 150.7182 | 1.633% | 21.9948 | 0.2382% | 172.713 | 1.871% | 2012 | 9210.0052 | 9059.287 | 1.664% | 0.2428%
2017-09-14 | 20 | 9238 | 150.7631 | 1.632% | 22.0097 | 0.2383% | 172.7727 | 1.87% | 2013 | 9215.9903 | 9065.2273 | 1.663% | 0.2428%
2017-09-26 | 14 | 9261 | 150.9352 | 1.63% | 22.0666 | 0.2383% | 173.0018 | 1.868% | 2014 | 9238.9334 | 9087.9982 | 1.661% | 0.2428%
2017-09-25 | 19 | 9263 | 150.9501 | 1.63% | 22.0716 | 0.2383% | 173.0217 | 1.868% | 2015 | 9240.9284 | 9089.9783 | 1.661% | 0.2428%
2017-10-12 | 14 | 9275 | 151.0399 | 1.628% | 22.1013 | 0.2383% | 173.1412 | 1.867% | 2016 | 9252.8987 | 9101.8588 | 1.659% | 0.2428%
2017-11-28 | 6 | 9275 | 151.0399 | 1.628% | 22.1013 | 0.2383% | 173.1412 | 1.867% | 2017 | 9252.8987 | 9101.8588 | 1.659% | 0.2428%
2017-09-23 | 19 | 9276 | 151.0474 | 1.628% | 22.1037 | 0.2383% | 173.1512 | 1.867% | 2018 | 9253.8963 | 9102.8488 | 1.659% | 0.2428%
2017-09-14 | 14 | 9277 | 151.0549 | 1.628% | 22.1062 | 0.2383% | 173.1611 | 1.867% | 2019 | 9254.8938 | 9103.8389 | 1.659% | 0.2428%
2017-09-16 | 14 | 9277 | 151.0549 | 1.628% | 22.1062 | 0.2383% | 173.1611 | 1.867% | 2020 | 9254.8938 | 9103.8389 | 1.659% | 0.2428%
2017-10-12 | 17 | 9290 | 151.1522 | 1.627% | 22.1384 | 0.2383% | 173.2906 | 1.865% | 2021 | 9267.8616 | 9116.7094 | 1.658% | 0.2428%
2017-09-21 | 12 | 9307 | 151.2794 | 1.625% | 22.1805 | 0.2383% | 173.4598 | 1.864% | 2022 | 9284.8195 | 9133.5402 | 1.656% | 0.2428%
2017-09-25 | 20 | 9312 | 151.3168 | 1.625% | 22.1929 | 0.2383% | 173.5096 | 1.863% | 2023 | 9289.8071 | 9138.4904 | 1.656% | 0.2429%
2017-10-11 | 13 | 9313 | 151.3242 | 1.625% | 22.1953 | 0.2383% | 173.5196 | 1.863% | 2024 | 9290.8047 | 9139.4804 | 1.656% | 0.2429%
2017-11-21 | 9 | 9320 | 151.3766 | 1.624% | 22.2127 | 0.2383% | 173.5893 | 1.863% | 2025 | 9297.7873 | 9146.4107 | 1.655% | 0.2429%
2017-09-04 | 20 | 9326 | 151.4215 | 1.624% | 22.2275 | 0.2383% | 173.649 | 1.862% | 2026 | 9303.7725 | 9152.351 | 1.654% | 0.2429%
2017-09-28 | 22 | 9326 | 151.4215 | 1.624% | 22.2275 | 0.2383% | 173.649 | 1.862% | 2027 | 9303.7725 | 9152.351 | 1.654% | 0.2429%
2017-09-01 | 18 | 9330 | 151.4514 | 1.623% | 22.2374 | 0.2383% | 173.6889 | 1.862% | 2028 | 9307.7626 | 9156.3111 | 1.654% | 0.2429%
2017-09-23 | 14 | 9331 | 151.4589 | 1.623% | 22.2399 | 0.2383% | 173.6988 | 1.862% | 2029 | 9308.7601 | 9157.3012 | 1.654% | 0.2429%
2017-09-18 | 20 | 9353 | 151.6235 | 1.621% | 22.2944 | 0.2384% | 173.9179 | 1.859% | 2030 | 9330.7056 | 9179.0821 | 1.652% | 0.2429%
2017-09-25 | 17 | 9373 | 151.7732 | 1.619% | 22.3439 | 0.2384% | 174.1171 | 1.858% | 2031 | 9350.6561 | 9198.8829 | 1.65% | 0.2429%
2017-09-04 | 15 | 9376 | 151.7956 | 1.619% | 22.3513 | 0.2384% | 174.1469 | 1.857% | 2032 | 9353.6487 | 9201.8531 | 1.65% | 0.2429%
2017-09-24 | 15 | 9384 | 151.8555 | 1.618% | 22.3711 | 0.2384% | 174.2266 | 1.857% | 2033 | 9361.6289 | 9209.7734 | 1.649% | 0.2429%
2017-09-28 | 12 | 9389 | 151.8929 | 1.618% | 22.3835 | 0.2384% | 174.2764 | 1.856% | 2034 | 9366.6165 | 9214.7236 | 1.648% | 0.2429%
2017-09-19 | 14 | 9393 | 151.9228 | 1.617% | 22.3934 | 0.2384% | 174.3162 | 1.856% | 2035 | 9370.6066 | 9218.6838 | 1.648% | 0.2429%
2017-09-25 | 18 | 9406 | 152.0201 | 1.616% | 22.4256 | 0.2384% | 174.4457 | 1.855% | 2036 | 9383.5744 | 9231.5543 | 1.647% | 0.2429%
2017-09-13 | 15 | 9408 | 152.0351 | 1.616% | 22.4305 | 0.2384% | 174.4656 | 1.854% | 2037 | 9385.5695 | 9233.5344 | 1.647% | 0.2429%
2017-09-14 | 19 | 9423 | 152.1473 | 1.615% | 22.4677 | 0.2384% | 174.615 | 1.853% | 2038 | 9400.5323 | 9248.385 | 1.645% | 0.2429%
2017-09-22 | 13 | 9430 | 152.1997 | 1.614% | 22.485 | 0.2384% | 174.6847 | 1.852% | 2039 | 9407.515 | 9255.3153 | 1.644% | 0.2429%
2017-09-21 | 20 | 9439 | 152.267 | 1.613% | 22.5073 | 0.2384% | 174.7743 | 1.852% | 2040 | 9416.4927 | 9264.2257 | 1.644% | 0.2429%
2017-09-26 | 21 | 9441 | 152.282 | 1.613% | 22.5122 | 0.2385% | 174.7942 | 1.851% | 2041 | 9418.4878 | 9266.2058 | 1.643% | 0.2429%
2017-10-12 | 15 | 9446 | 152.3194 | 1.613% | 22.5246 | 0.2385% | 174.844 | 1.851% | 2042 | 9423.4754 | 9271.156 | 1.643% | 0.243%
2017-09-01 | 13 | 9448 | 152.3343 | 1.612% | 22.5296 | 0.2385% | 174.8639 | 1.851% | 2043 | 9425.4704 | 9273.1361 | 1.643% | 0.243%
2017-09-24 | 18 | 9448 | 152.3343 | 1.612% | 22.5296 | 0.2385% | 174.8639 | 1.851% | 2044 | 9425.4704 | 9273.1361 | 1.643% | 0.243%
2017-09-22 | 20 | 9452 | 152.3643 | 1.612% | 22.5395 | 0.2385% | 174.9038 | 1.85% | 2045 | 9429.4605 | 9277.0962 | 1.642% | 0.243%
2017-10-12 | 16 | 9463 | 152.4466 | 1.611% | 22.5667 | 0.2385% | 175.0133 | 1.849% | 2046 | 9440.4333 | 9287.9867 | 1.641% | 0.243%
2017-11-20 | 9 | 9468 | 152.484 | 1.611% | 22.5791 | 0.2385% | 175.0631 | 1.849% | 2047 | 9445.4209 | 9292.9369 | 1.641% | 0.243%
2017-10-10 | 12 | 9495 | 152.686 | 1.608% | 22.6459 | 0.2385% | 175.3319 | 1.847% | 2048 | 9472.3541 | 9319.6681 | 1.638% | 0.243%
2017-09-17 | 16 | 9501 | 152.7309 | 1.608% | 22.6608 | 0.2385% | 175.3917 | 1.846% | 2049 | 9478.3392 | 9325.6083 | 1.638% | 0.243%
2017-09-14 | 15 | 9507 | 152.7758 | 1.607% | 22.6756 | 0.2385% | 175.4514 | 1.845% | 2050 | 9484.3244 | 9331.5486 | 1.637% | 0.243%
2017-09-16 | 15 | 9511 | 152.8057 | 1.607% | 22.6855 | 0.2385% | 175.4913 | 1.845% | 2051 | 9488.3145 | 9335.5087 | 1.637% | 0.243%
2017-09-18 | 15 | 9512 | 152.8132 | 1.607% | 22.688 | 0.2385% | 175.5012 | 1.845% | 2052 | 9489.312 | 9336.4988 | 1.637% | 0.243%
2017-09-13 | 19 | 9515 | 152.8357 | 1.606% | 22.6954 | 0.2385% | 175.5311 | 1.845% | 2053 | 9492.3046 | 9339.4689 | 1.636% | 0.243%
2017-09-17 | 18 | 9522 | 152.888 | 1.606% | 22.7128 | 0.2385% | 175.6008 | 1.844% | 2054 | 9499.2872 | 9346.3992 | 1.636% | 0.243%
2017-09-18 | 19 | 9530 | 152.9479 | 1.605% | 22.7326 | 0.2385% | 175.6805 | 1.843% | 2055 | 9507.2674 | 9354.3195 | 1.635% | 0.243%
2017-09-16 | 18 | 9548 | 153.0826 | 1.603% | 22.7771 | 0.2386% | 175.8597 | 1.842% | 2056 | 9525.2229 | 9372.1403 | 1.633% | 0.243%
2017-09-19 | 20 | 9551 | 153.105 | 1.603% | 22.7846 | 0.2386% | 175.8896 | 1.842% | 2057 | 9528.2154 | 9375.1104 | 1.633% | 0.243%
2017-11-27 | 9 | 9562 | 153.1873 | 1.602% | 22.8118 | 0.2386% | 175.9991 | 1.841% | 2058 | 9539.1882 | 9386.0009 | 1.632% | 0.243%
2017-09-24 | 16 | 9570 | 153.2472 | 1.601% | 22.8316 | 0.2386% | 176.0788 | 1.84% | 2059 | 9547.1684 | 9393.9212 | 1.631% | 0.243%
2017-09-21 | 19 | 9577 | 153.2996 | 1.601% | 22.8489 | 0.2386% | 176.1485 | 1.839% | 2060 | 9554.1511 | 9400.8515 | 1.631% | 0.2431%
2017-09-15 | 19 | 9584 | 153.3519 | 1.6% | 22.8663 | 0.2386% | 176.2182 | 1.839% | 2061 | 9561.1337 | 9407.7818 | 1.63% | 0.2431%
2017-09-24 | 17 | 9612 | 153.5614 | 1.598% | 22.9356 | 0.2386% | 176.497 | 1.836% | 2062 | 9589.0644 | 9435.503 | 1.627% | 0.2431%
2017-10-09 | 13 | 9617 | 153.5988 | 1.597% | 22.948 | 0.2386% | 176.5468 | 1.836% | 2063 | 9594.052 | 9440.4532 | 1.627% | 0.2431%
2017-11-20 | 7 | 9617 | 153.5988 | 1.597% | 22.948 | 0.2386% | 176.5468 | 1.836% | 2064 | 9594.052 | 9440.4532 | 1.627% | 0.2431%
2017-09-16 | 16 | 9628 | 153.6811 | 1.596% | 22.9752 | 0.2386% | 176.6564 | 1.835% | 2065 | 9605.0248 | 9451.3436 | 1.626% | 0.2431%
2017-09-17 | 17 | 9630 | 153.6961 | 1.596% | 22.9802 | 0.2386% | 176.6763 | 1.835% | 2066 | 9607.0198 | 9453.3237 | 1.626% | 0.2431%
2017-09-20 | 13 | 9635 | 153.7335 | 1.596% | 22.9925 | 0.2386% | 176.7261 | 1.834% | 2067 | 9612.0075 | 9458.2739 | 1.625% | 0.2431%
2017-09-23 | 15 | 9635 | 153.7335 | 1.596% | 22.9925 | 0.2386% | 176.7261 | 1.834% | 2068 | 9612.0075 | 9458.2739 | 1.625% | 0.2431%
2017-09-26 | 15 | 9640 | 153.7709 | 1.595% | 23.0049 | 0.2386% | 176.7758 | 1.834% | 2069 | 9616.9951 | 9463.2242 | 1.625% | 0.2431%
2017-11-21 | 7 | 9644 | 153.8009 | 1.595% | 23.0148 | 0.2386% | 176.8157 | 1.833% | 2070 | 9620.9852 | 9467.1843 | 1.625% | 0.2431%
2017-09-01 | 17 | 9647 | 153.8233 | 1.595% | 23.0222 | 0.2386% | 176.8456 | 1.833% | 2071 | 9623.9778 | 9470.1544 | 1.624% | 0.2431%
2017-10-11 | 21 | 9651 | 153.8532 | 1.594% | 23.0321 | 0.2387% | 176.8854 | 1.833% | 2072 | 9627.9679 | 9474.1146 | 1.624% | 0.2431%
2017-09-15 | 14 | 9653 | 153.8682 | 1.594% | 23.0371 | 0.2387% | 176.9053 | 1.833% | 2073 | 9629.9629 | 9476.0947 | 1.624% | 0.2431%
2017-09-14 | 16 | 9656 | 153.8906 | 1.594% | 23.0445 | 0.2387% | 176.9352 | 1.832% | 2074 | 9632.9555 | 9479.0648 | 1.623% | 0.2431%
2017-11-28 | 9 | 9658 | 153.9056 | 1.594% | 23.0495 | 0.2387% | 176.9551 | 1.832% | 2075 | 9634.9505 | 9481.0449 | 1.623% | 0.2431%
2017-11-21 | 8 | 9671 | 154.0029 | 1.592% | 23.0817 | 0.2387% | 177.0845 | 1.831% | 2076 | 9647.9183 | 9493.9155 | 1.622% | 0.2431%
2017-09-16 | 17 | 9680 | 154.0702 | 1.592% | 23.1039 | 0.2387% | 177.1742 | 1.83% | 2077 | 9656.8961 | 9502.8258 | 1.621% | 0.2431%
2017-09-14 | 18 | 9685 | 154.1076 | 1.591% | 23.1163 | 0.2387% | 177.224 | 1.83% | 2078 | 9661.8837 | 9507.776 | 1.621% | 0.2431%
2017-09-13 | 16 | 9691 | 154.1525 | 1.591% | 23.1312 | 0.2387% | 177.2837 | 1.829% | 2079 | 9667.8688 | 9513.7163 | 1.62% | 0.2431%
2017-11-27 | 7 | 9702 | 154.2348 | 1.59% | 23.1584 | 0.2387% | 177.3932 | 1.828% | 2080 | 9678.8416 | 9524.6068 | 1.619% | 0.2431%
2017-09-20 | 21 | 9720 | 154.3695 | 1.588% | 23.203 | 0.2387% | 177.5725 | 1.827% | 2081 | 9696.797 | 9542.4275 | 1.618% | 0.2432%
2017-10-11 | 14 | 9720 | 154.3695 | 1.588% | 23.203 | 0.2387% | 177.5725 | 1.827% | 2082 | 9696.797 | 9542.4275 | 1.618% | 0.2432%
2017-09-04 | 19 | 9744 | 154.5491 | 1.586% | 23.2624 | 0.2387% | 177.8115 | 1.825% | 2083 | 9720.7376 | 9566.1885 | 1.616% | 0.2432%
2017-09-26 | 20 | 9747 | 154.5715 | 1.586% | 23.2698 | 0.2387% | 177.8413 | 1.825% | 2084 | 9723.7302 | 9569.1587 | 1.615% | 0.2432%
2017-09-18 | 16 | 9761 | 154.6763 | 1.585% | 23.3045 | 0.2388% | 177.9808 | 1.823% | 2085 | 9737.6955 | 9583.0192 | 1.614% | 0.2432%
2017-09-13 | 18 | 9768 | 154.7287 | 1.584% | 23.3218 | 0.2388% | 178.0505 | 1.823% | 2086 | 9744.6782 | 9589.9495 | 1.613% | 0.2432%
2017-09-23 | 18 | 9769 | 154.7361 | 1.584% | 23.3243 | 0.2388% | 178.0604 | 1.823% | 2087 | 9745.6757 | 9590.9396 | 1.613% | 0.2432%
2017-09-14 | 17 | 9770 | 154.7436 | 1.584% | 23.3268 | 0.2388% | 178.0704 | 1.823% | 2088 | 9746.6732 | 9591.9296 | 1.613% | 0.2432%
2017-10-10 | 21 | 9773 | 154.7661 | 1.584% | 23.3342 | 0.2388% | 178.1003 | 1.822% | 2089 | 9749.6658 | 9594.8997 | 1.613% | 0.2432%
2017-09-04 | 16 | 9789 | 154.8858 | 1.582% | 23.3738 | 0.2388% | 178.2596 | 1.821% | 2090 | 9765.6262 | 9610.7404 | 1.612% | 0.2432%
2017-10-09 | 21 | 9791 | 154.9007 | 1.582% | 23.3788 | 0.2388% | 178.2795 | 1.821% | 2091 | 9767.6212 | 9612.7205 | 1.611% | 0.2432%
2017-09-01 | 14 | 9796 | 154.9382 | 1.582% | 23.3911 | 0.2388% | 178.3293 | 1.82% | 2092 | 9772.6089 | 9617.6707 | 1.611% | 0.2432%
2017-09-27 | 13 | 9796 | 154.9382 | 1.582% | 23.3911 | 0.2388% | 178.3293 | 1.82% | 2093 | 9772.6089 | 9617.6707 | 1.611% | 0.2432%
2017-09-13 | 17 | 9803 | 154.9905 | 1.581% | 23.4085 | 0.2388% | 178.399 | 1.82% | 2094 | 9779.5915 | 9624.601 | 1.61% | 0.2432%
2017-09-26 | 19 | 9811 | 155.0504 | 1.58% | 23.4283 | 0.2388% | 178.4787 | 1.819% | 2095 | 9787.5717 | 9632.5213 | 1.61% | 0.2432%
2017-09-23 | 16 | 9826 | 155.1626 | 1.579% | 23.4654 | 0.2388% | 178.628 | 1.818% | 2096 | 9802.5346 | 9647.372 | 1.608% | 0.2432%
2017-09-19 | 19 | 9836 | 155.2374 | 1.578% | 23.4902 | 0.2388% | 178.7276 | 1.817% | 2097 | 9812.5098 | 9657.2724 | 1.607% | 0.2432%
2017-09-05 | 13 | 9837 | 155.2449 | 1.578% | 23.4926 | 0.2388% | 178.7376 | 1.817% | 2098 | 9813.5074 | 9658.2624 | 1.607% | 0.2432%
2017-09-18 | 18 | 9851 | 155.3497 | 1.577% | 23.5273 | 0.2388% | 178.877 | 1.816% | 2099 | 9827.4727 | 9672.123 | 1.606% | 0.2432%
2017-09-19 | 15 | 9863 | 155.4395 | 1.576% | 23.557 | 0.2388% | 178.9965 | 1.815% | 2100 | 9839.443 | 9684.0035 | 1.605% | 0.2433%
2017-11-20 | 8 | 9863 | 155.4395 | 1.576% | 23.557 | 0.2388% | 178.9965 | 1.815% | 2101 | 9839.443 | 9684.0035 | 1.605% | 0.2433%
2017-09-01 | 16 | 9872 | 155.5068 | 1.575% | 23.5793 | 0.2389% | 179.0861 | 1.814% | 2102 | 9848.4207 | 9692.9139 | 1.604% | 0.2433%
2017-09-18 | 17 | 9883 | 155.5891 | 1.574% | 23.6065 | 0.2389% | 179.1956 | 1.813% | 2103 | 9859.3935 | 9703.8044 | 1.603% | 0.2433%
2017-09-01 | 15 | 9892 | 155.6564 | 1.574% | 23.6288 | 0.2389% | 179.2853 | 1.812% | 2104 | 9868.3712 | 9712.7147 | 1.603% | 0.2433%
2017-09-15 | 15 | 9917 | 155.8435 | 1.571% | 23.6907 | 0.2389% | 179.5342 | 1.81% | 2105 | 9893.3093 | 9737.4658 | 1.6% | 0.2433%
2017-09-22 | 19 | 9919 | 155.8585 | 1.571% | 23.6956 | 0.2389% | 179.5541 | 1.81% | 2106 | 9895.3044 | 9739.4459 | 1.6% | 0.2433%
2017-11-27 | 8 | 9933 | 155.9632 | 1.57% | 23.7303 | 0.2389% | 179.6935 | 1.809% | 2107 | 9909.2697 | 9753.3065 | 1.599% | 0.2433%
2017-09-23 | 17 | 9939 | 156.0081 | 1.57% | 23.7452 | 0.2389% | 179.7533 | 1.809% | 2108 | 9915.2548 | 9759.2467 | 1.599% | 0.2433%
2017-10-10 | 13 | 9947 | 156.068 | 1.569% | 23.765 | 0.2389% | 179.8329 | 1.808% | 2109 | 9923.235 | 9767.1671 | 1.598% | 0.2433%
2017-10-09 | 18 | 9950 | 156.0904 | 1.569% | 23.7724 | 0.2389% | 179.8628 | 1.808% | 2110 | 9926.2276 | 9770.1372 | 1.598% | 0.2433%
2017-09-26 | 16 | 9955 | 156.1278 | 1.568% | 23.7848 | 0.2389% | 179.9126 | 1.807% | 2111 | 9931.2152 | 9775.0874 | 1.597% | 0.2433%
2017-09-21 | 18 | 9961 | 156.1727 | 1.568% | 23.7996 | 0.2389% | 179.9723 | 1.807% | 2112 | 9937.2004 | 9781.0277 | 1.597% | 0.2433%
2017-09-27 | 21 | 9967 | 156.2176 | 1.567% | 23.8145 | 0.2389% | 180.0321 | 1.806% | 2113 | 9943.1855 | 9786.9679 | 1.596% | 0.2433%
2017-10-09 | 19 | 9972 | 156.255 | 1.567% | 23.8269 | 0.2389% | 180.0819 | 1.806% | 2114 | 9948.1731 | 9791.9181 | 1.596% | 0.2433%
2017-09-22 | 14 | 9980 | 156.3149 | 1.566% | 23.8467 | 0.2389% | 180.1616 | 1.805% | 2115 | 9956.1533 | 9799.8384 | 1.595% | 0.2433%
2017-09-15 | 18 | 9989 | 156.3822 | 1.566% | 23.8689 | 0.239% | 180.2512 | 1.804% | 2116 | 9965.1311 | 9808.7488 | 1.594% | 0.2433%
2017-09-04 | 17 | 9991 | 156.3972 | 1.565% | 23.8739 | 0.239% | 180.2711 | 1.804% | 2117 | 9967.1261 | 9810.7289 | 1.594% | 0.2433%
2017-10-11 | 20 | 9992 | 156.4047 | 1.565% | 23.8764 | 0.239% | 180.281 | 1.804% | 2118 | 9968.1236 | 9811.719 | 1.594% | 0.2433%
2017-10-09 | 14 | 10000 | 156.4645 | 1.565% | 23.8962 | 0.239% | 180.3607 | 1.804% | 2119 | 9976.1038 | 9819.6393 | 1.593% | 0.2434%
2017-09-05 | 21 | 10031 | 156.6965 | 1.562% | 23.9729 | 0.239% | 180.6694 | 1.801% | 2120 | 10007.0271 | 9850.3306 | 1.591% | 0.2434%
2017-10-11 | 19 | 10032 | 156.704 | 1.562% | 23.9754 | 0.239% | 180.6794 | 1.801% | 2121 | 10008.0246 | 9851.3206 | 1.591% | 0.2434%
2017-09-04 | 18 | 10044 | 156.7937 | 1.561% | 24.0051 | 0.239% | 180.7989 | 1.8% | 2122 | 10019.9949 | 9863.2011 | 1.59% | 0.2434%
2017-09-21 | 13 | 10046 | 156.8087 | 1.561% | 24.0101 | 0.239% | 180.8188 | 1.8% | 2123 | 10021.9899 | 9865.1812 | 1.59% | 0.2434%
2017-10-09 | 17 | 10075 | 157.0257 | 1.559% | 24.0819 | 0.239% | 181.1076 | 1.798% | 2124 | 10050.9181 | 9893.8924 | 1.587% | 0.2434%
2017-11-28 | 7 | 10089 | 157.1304 | 1.557% | 24.1165 | 0.239% | 181.247 | 1.796% | 2125 | 10064.8835 | 9907.753 | 1.586% | 0.2434%
2017-09-15 | 16 | 10091 | 157.1454 | 1.557% | 24.1215 | 0.239% | 181.2669 | 1.796% | 2126 | 10066.8785 | 9909.7331 | 1.586% | 0.2434%
2017-09-19 | 18 | 10096 | 157.1828 | 1.557% | 24.1339 | 0.239% | 181.3167 | 1.796% | 2127 | 10071.8661 | 9914.6833 | 1.585% | 0.2434%
2017-10-09 | 20 | 10098 | 157.1978 | 1.557% | 24.1388 | 0.239% | 181.3366 | 1.796% | 2128 | 10073.8612 | 9916.6634 | 1.585% | 0.2434%
2017-10-10 | 19 | 10119 | 157.3549 | 1.555% | 24.1908 | 0.2391% | 181.5457 | 1.794% | 2129 | 10094.8092 | 9937.4543 | 1.583% | 0.2434%
2017-10-11 | 18 | 10127 | 157.4148 | 1.554% | 24.2106 | 0.2391% | 181.6254 | 1.793% | 2130 | 10102.7894 | 9945.3746 | 1.583% | 0.2434%
2017-09-26 | 18 | 10128 | 157.4223 | 1.554% | 24.2131 | 0.2391% | 181.6353 | 1.793% | 2131 | 10103.7869 | 9946.3647 | 1.583% | 0.2434%
2017-09-28 | 13 | 10130 | 157.4372 | 1.554% | 24.218 | 0.2391% | 181.6552 | 1.793% | 2132 | 10105.782 | 9948.3448 | 1.583% | 0.2434%
2017-10-11 | 15 | 10130 | 157.4372 | 1.554% | 24.218 | 0.2391% | 181.6552 | 1.793% | 2133 | 10105.782 | 9948.3448 | 1.583% | 0.2434%
2017-09-26 | 17 | 10136 | 157.4821 | 1.554% | 24.2329 | 0.2391% | 181.715 | 1.793% | 2134 | 10111.7671 | 9954.285 | 1.582% | 0.2434%
2017-10-10 | 18 | 10137 | 157.4896 | 1.554% | 24.2354 | 0.2391% | 181.7249 | 1.793% | 2135 | 10112.7646 | 9955.2751 | 1.582% | 0.2434%
2017-09-15 | 17 | 10140 | 157.512 | 1.553% | 24.2428 | 0.2391% | 181.7548 | 1.792% | 2136 | 10115.7572 | 9958.2452 | 1.582% | 0.2434%
2017-10-09 | 15 | 10141 | 157.5195 | 1.553% | 24.2453 | 0.2391% | 181.7648 | 1.792% | 2137 | 10116.7547 | 9959.2352 | 1.582% | 0.2434%
2017-09-28 | 21 | 10144 | 157.542 | 1.553% | 24.2527 | 0.2391% | 181.7947 | 1.792% | 2138 | 10119.7473 | 9962.2053 | 1.581% | 0.2434%
2017-09-19 | 16 | 10148 | 157.5719 | 1.553% | 24.2626 | 0.2391% | 181.8345 | 1.792% | 2139 | 10123.7374 | 9966.1655 | 1.581% | 0.2434%
2017-10-11 | 17 | 10148 | 157.5719 | 1.553% | 24.2626 | 0.2391% | 181.8345 | 1.792% | 2140 | 10123.7374 | 9966.1655 | 1.581% | 0.2434%
2017-09-20 | 20 | 10165 | 157.6991 | 1.551% | 24.3047 | 0.2391% | 182.0038 | 1.79% | 2141 | 10140.6953 | 9982.9962 | 1.58% | 0.2435%
2017-11-28 | 8 | 10193 | 157.9086 | 1.549% | 24.374 | 0.2391% | 182.2826 | 1.788% | 2142 | 10168.626 | 10010.7174 | 1.577% | 0.2435%
2017-10-10 | 20 | 10198 | 157.946 | 1.549% | 24.3864 | 0.2391% | 182.3324 | 1.788% | 2143 | 10173.6136 | 10015.6676 | 1.577% | 0.2435%
2017-10-11 | 16 | 10214 | 158.0657 | 1.548% | 24.426 | 0.2391% | 182.4917 | 1.787% | 2144 | 10189.574 | 10031.5083 | 1.576% | 0.2435%
2017-10-09 | 16 | 10222 | 158.1256 | 1.547% | 24.4458 | 0.2391% | 182.5714 | 1.786% | 2145 | 10197.5542 | 10039.4286 | 1.575% | 0.2435%
2017-10-10 | 17 | 10229 | 158.178 | 1.546% | 24.4631 | 0.2392% | 182.6411 | 1.786% | 2146 | 10204.5369 | 10046.3589 | 1.574% | 0.2435%
2017-09-19 | 17 | 10248 | 158.3201 | 1.545% | 24.5102 | 0.2392% | 182.8303 | 1.784% | 2147 | 10223.4898 | 10065.1697 | 1.573% | 0.2435%
2017-09-05 | 14 | 10254 | 158.365 | 1.544% | 24.525 | 0.2392% | 182.89 | 1.784% | 2148 | 10229.475 | 10071.11 | 1.572% | 0.2435%
2017-10-10 | 14 | 10269 | 158.4772 | 1.543% | 24.5622 | 0.2392% | 183.0394 | 1.782% | 2149 | 10244.4378 | 10085.9606 | 1.571% | 0.2435%
2017-09-05 | 20 | 10281 | 158.567 | 1.542% | 24.5919 | 0.2392% | 183.1589 | 1.782% | 2150 | 10256.4081 | 10097.8411 | 1.57% | 0.2435%
2017-09-21 | 17 | 10292 | 158.6493 | 1.541% | 24.6191 | 0.2392% | 183.2684 | 1.781% | 2151 | 10267.3809 | 10108.7316 | 1.569% | 0.2435% | 10306.4562
2017-09-20 | 19 | 10321 | 158.579 | 1.536% | 24.6805 | 0.2391% | 183.2595 | 1.776% | 2152 | 10296.3195 | 10137.7405 | 1.564% | 0.2435%
2017-10-10 | 16 | 10326 | 158.5176 | 1.535% | 24.6894 | 0.2391% | 183.207 | 1.774% | 2153 | 10301.3106 | 10142.793 | 1.563% | 0.2434%
2017-09-20 | 14 | 10349 | 158.2352 | 1.529% | 24.7299 | 0.239% | 182.9651 | 1.768% | 2154 | 10324.2701 | 10166.0349 | 1.557% | 0.2433%
2017-10-10 | 15 | 10354 | 158.1738 | 1.528% | 24.7387 | 0.2389% | 182.9125 | 1.767% | 2155 | 10329.2613 | 10171.0875 | 1.555% | 0.2432%
2017-09-22 | 15 | 10360 | 158.1001 | 1.526% | 24.7493 | 0.2389% | 182.8494 | 1.765% | 2156 | 10335.2507 | 10177.1506 | 1.553% | 0.2432%
2017-09-27 | 14 | 10392 | 157.7071 | 1.518% | 24.8058 | 0.2387% | 182.5129 | 1.756% | 2157 | 10367.1942 | 10209.4871 | 1.545% | 0.243%
2017-09-05 | 19 | 10448 | 157.0195 | 1.503% | 24.9045 | 0.2384% | 181.924 | 1.741% | 2158 | 10423.0955 | 10266.076 | 1.529% | 0.2426%
2017-09-22 | 18 | 10455 | 156.9335 | 1.501% | 24.9169 | 0.2383% | 181.8504 | 1.739% | 2159 | 10430.0831 | 10273.1496 | 1.528% | 0.2425%
2017-09-21 | 16 | 10489 | 156.516 | 1.492% | 24.9768 | 0.2381% | 181.4928 | 1.73% | 2160 | 10464.0232 | 10307.5072 | 1.518% | 0.2423%
2017-09-27 | 20 | 10518 | 156.1599 | 1.485% | 25.028 | 0.238% | 181.1879 | 1.723% | 2161 | 10492.972 | 10336.8121 | 1.511% | 0.2421%
2017-09-05 | 15 | 10535 | 155.9511 | 1.48% | 25.058 | 0.2379% | 181.0091 | 1.718% | 2162 | 10509.942 | 10353.9909 | 1.506% | 0.242%
2017-09-05 | 18 | 10537 | 155.9266 | 1.48% | 25.0615 | 0.2378% | 180.9881 | 1.718% | 2163 | 10511.9385 | 10356.0119 | 1.506% | 0.242%
2017-09-20 | 15 | 10572 | 155.4968 | 1.471% | 25.1232 | 0.2376% | 180.62 | 1.708% | 2164 | 10546.8768 | 10391.38 | 1.496% | 0.2418%
2017-09-22 | 16 | 10572 | 155.4968 | 1.471% | 25.1232 | 0.2376% | 180.62 | 1.708% | 2165 | 10546.8768 | 10391.38 | 1.496% | 0.2418%
2017-09-21 | 14 | 10579 | 155.4108 | 1.469% | 25.1356 | 0.2376% | 180.5464 | 1.707% | 2166 | 10553.8644 | 10398.4536 | 1.495% | 0.2417%
2017-09-05 | 16 | 10593 | 155.2389 | 1.465% | 25.1602 | 0.2375% | 180.3992 | 1.703% | 2167 | 10567.8398 | 10412.6008 | 1.491% | 0.2416%
2017-09-21 | 15 | 10596 | 155.2021 | 1.465% | 25.1655 | 0.2375% | 180.3676 | 1.702% | 2168 | 10570.8345 | 10415.6324 | 1.49% | 0.2416%
2017-09-28 | 20 | 10597 | 155.1898 | 1.464% | 25.1673 | 0.2375% | 180.3571 | 1.702% | 2169 | 10571.8327 | 10416.6429 | 1.49% | 0.2416%
2017-09-05 | 17 | 10624 | 154.8582 | 1.458% | 25.2149 | 0.2373% | 180.0731 | 1.695% | 2170 | 10598.7851 | 10443.9269 | 1.483% | 0.2414%
2017-09-22 | 17 | 10634 | 154.7354 | 1.455% | 25.2326 | 0.2373% | 179.968 | 1.692% | 2171 | 10608.7674 | 10454.032 | 1.48% | 0.2414%
2017-09-20 | 18 | 10649 | 154.5512 | 1.451% | 25.259 | 0.2372% | 179.8102 | 1.689% | 2172 | 10623.741 | 10469.1898 | 1.476% | 0.2413%
2017-09-27 | 15 | 10700 | 153.925 | 1.439% | 25.349 | 0.2369% | 179.2739 | 1.675% | 2173 | 10674.651 | 10520.7261 | 1.463% | 0.2409%
2017-09-27 | 19 | 10730 | 153.5566 | 1.431% | 25.4019 | 0.2367% | 178.9584 | 1.668% | 2174 | 10704.5981 | 10551.0416 | 1.455% | 0.2408%
2017-09-20 | 16 | 10778 | 152.9671 | 1.419% | 25.4865 | 0.2365% | 178.4537 | 1.656% | 2175 | 10752.5135 | 10599.5463 | 1.443% | 0.2404%
2017-09-28 | 14 | 10810 | 152.5742 | 1.411% | 25.543 | 0.2363% | 178.1171 | 1.648% | 2176 | 10784.457 | 10631.8829 | 1.435% | 0.2402%
2017-09-20 | 17 | 10841 | 152.1935 | 1.404% | 25.5976 | 0.2361% | 177.7911 | 1.64% | 2177 | 10815.4024 | 10663.2089 | 1.427% | 0.2401%
2017-09-28 | 19 | 10841 | 152.1935 | 1.404% | 25.5976 | 0.2361% | 177.7911 | 1.64% | 2178 | 10815.4024 | 10663.2089 | 1.427% | 0.2401%
2017-09-27 | 16 | 10886 | 151.6409 | 1.393% | 25.677 | 0.2359% | 177.3179 | 1.629% | 2179 | 10860.323 | 10708.6821 | 1.416% | 0.2398%
2017-09-27 | 18 | 10952 | 150.8305 | 1.377% | 25.7934 | 0.2355% | 176.6239 | 1.613% | 2180 | 10926.2066 | 10775.3761 | 1.4% | 0.2394%
2017-09-27 | 17 | 11036 | 149.799 | 1.357% | 25.9415 | 0.2351% | 175.7405 | 1.592% | 2181 | 11010.0585 | 10860.2595 | 1.379% | 0.2389%
2017-09-28 | 15 | 11098 | 149.0376 | 1.343% | 26.0509 | 0.2347% | 175.0885 | 1.578% | 2182 | 11071.9491 | 10922.9115 | 1.364% | 0.2385%
2017-09-28 | 18 | 11127 | 148.6815 | 1.336% | 26.102 | 0.2346% | 174.7835 | 1.571% | 2183 | 11100.898 | 10952.2165 | 1.358% | 0.2383% | 11141.7327
2017-09-28 | 16 | 11283 | 146.7659 | 1.301% | 26.3771 | 0.2338% | 173.143 | 1.535% | 2184 | 11256.6229 | 11109.857 | 1.321% | 0.2374%
2017-09-28 | 17 | 11327 | 146.2256 | 1.291% | 26.4547 | 0.2336% | 172.6803 | 1.525% | 2185 | 11300.5453 | 11154.3197 | 1.311% | 0.2372%
|  | 15375677 | 284739.4287 | 1.852% | 39256.8098 | 0.2553% | 323996.2385 | 2.107% |  | 15336420.1902 | 15051680.7615 | 1.892% | 0.2608%
Note on C3: Quaintance, William Harford: Measured at generator energy meter
Note on C4: Quaintance, William Harford: Keep sorted by MW load, smallest to largest

## Losses from PSSE
|  | GSU + Transmission Losses |  |  |  | Transmission Losses Only |  |  |  | GSU Losses Only |  |  |  | CPLE & CPLW Load (MW)
PSSE Case Name | CPLE & CPLW PSSE Load(MW) | Line & Copper Losses (MW) | Core Losses (MW) | Line, Copper, & Core Losses (MW) | Line, Copper, & Core Losses (%) | Line & Copper Losses (MW) | Core Losses (MW) | Line, Copper, & Core Losses (MW) | Line, Copper, & Core Losses (%) | Copper Losses (MW) | Core Losses (MW) | Copper & Core Losses (MW) | Copper & Core Losses (%) | POD (PSSE) LOAD | GEN HIGH SIDE LOAD | GEN LOW SIDE LOAD
Hour_001_2017_10_01_03.sav | 4415.5165 | 124.1743 | 17.7516 | 141.9259 | 3.214% | 115.3169 | 10.8045 | 126.1214 | 2.856% | 8.8574 | 6.9471 | 15.8045 | 0.3579% | 4415.5165 | 4541.6379 | 4557.4424
Hour_001_2017_10_22_22.sav | 5410.5392 | 109.5344 | 17.7516 | 127.286 | 2.353% | 100.8269 | 10.8045 | 111.6314 | 2.063% | 8.7075 | 6.9471 | 15.6546 | 0.2893% | 5410.5392 | 5522.1706 | 5537.8252
Hour_001_2017_11_28_18.sav | 7766.2368 | 141.9557 | 17.7516 | 159.7074 | 2.056% | 130.1415 | 10.8045 | 140.946 | 1.815% | 11.8142 | 6.9471 | 18.7614 | 0.2416% | 7766.2368 | 7907.1828 | 7925.9442
Hour_001_2017_09_21_15.sav | 10123.0486 | 165.6608 | 17.7516 | 183.4124 | 1.812% | 147.9531 | 10.8045 | 158.7575 | 1.568% | 17.7078 | 6.9471 | 24.6549 | 0.2436% | 10123.0486 | 10281.8061 | 10306.461
Hour_001_2017_09_28_16.sav | 10967.2064 | 156.8759 | 17.7516 | 174.6275 | 1.592% | 137.6949 | 10.8045 | 148.4994 | 1.354% | 19.181 | 6.9471 | 26.1282 | 0.2382% | 10967.2064 | 11115.7057 | 11141.8339
From power flow model
From core losses sheet
Calculated values |  |  |  | Note: PSSE Loads are equivalent to POD loads
Note on Q3: Quaintance, William Harford: Represents POD load plus transmission losses
Note on R3: Quaintance, William Harford: Represents POD load plus transmission and GSU losses, equivalent to BA load from control center

## Core Losses
| From: | LS FeLossDoc2018 03-26-18.xlsx
MW
6.9471 | GSU Core Losses
10.8045 | T-T Core Losses
17.7516 | Total