## Final Loss Calculation
Spring Only |  |  | 240226.7997 |  | 39260.9061 | [5 empty] | 14805620.2942 | 1.623% | 0.2652%
[12 empty] | Transmission | GSU
|  | Control | T-only | T-only | GSU-only | GSU-only | GSU+T | GSU+T |  | GSU |  | Losses | Losses |  |  | GSU | T-only | T-only | GSU-only | GSU-only
|  | Area | Losses | Losses | Losses | Losses | Losses | Losses |  | High Side | POD | vs | vs | Model |  | Low Side | Losses | Losses | Losses | Losses
Date | Time | Load | (MW) | (%) | (MW) | (%) | (MW) | (%) | Hour # | Load (MW) | Load (MW) | POD Load | POD Load | Points | Hour # | Load(MW) | (MW) | Slope | (MW) | Slope
2017-04-17 | 4 | 4412 | 73.3302 | 1.662% | 13.3974 | 0.3037% | 86.7276 | 1.966% | 1 | 4398.6026 | 4325.2724 | 1.695% | 0.3097% |  | 6 | 4503.1061 | 75.8379 | 0.027525 | 13.5279 | 0.0014324
2017-04-02 | 4 | 4445 | 74.2385 | 1.67% | 13.4447 | 0.3025% | 87.6832 | 1.973% | 2 | 4431.5553 | 4357.3168 | 1.704% | 0.3086% |  | 413 | 5567.7126 | 105.1413 | 0.0036635 | 15.0529 | 0.0021398
2017-04-02 | 5 | 4466 | 74.8165 | 1.675% | 13.4747 | 0.3017% | 88.2913 | 1.977% | 3 | 4452.5253 | 4377.7087 | 1.709% | 0.3078% |  | 1850 | 8240.5071 | 114.933 | 0.011709 | 20.7721 | 0.0018654
2017-05-14 | 5 | 4474 | 75.0367 | 1.677% | 13.4862 | 0.3014% | 88.5229 | 1.979% | 4 | 4460.5138 | 4385.4771 | 1.711% | 0.3075% |  | 2195 | 10769.8677 | 144.5492 | 0.014438 | 25.4905 | 0.0024194
2017-03-26 | 4 | 4485 | 75.3395 | 1.68% | 13.502 | 0.301% | 88.8415 | 1.981% | 5 | 4471.498 | 4396.1585 | 1.714% | 0.3071% |  | 2206 | 11952.4766 | 161.624 |  | 28.3517
2017-05-14 | 4 | 4495 | 75.6148 | 1.682% | 13.5163 | 0.3007% | 89.1311 | 1.983% | 6 | 4481.4837 | 4405.8689 | 1.716% | 0.3068% | 4502.7941
2017-04-02 | 3 | 4509 | 76.0001 | 1.686% | 13.5363 | 0.3002% | 89.5365 | 1.986% | 7 | 4495.4637 | 4419.4635 | 1.72% | 0.3063%
2017-03-27 | 4 | 4513 | 76.1102 | 1.686% | 13.5421 | 0.3001% | 89.6523 | 1.987% | 8 | 4499.4579 | 4423.3477 | 1.721% | 0.3061%
2017-04-16 | 5 | 4523 | 76.3855 | 1.689% | 13.5564 | 0.2997% | 89.9419 | 1.989% | 9 | 4509.4436 | 4433.0581 | 1.723% | 0.3058%
2017-03-26 | 5 | 4527 | 76.4956 | 1.69% | 13.5621 | 0.2996% | 90.0577 | 1.989% | 10 | 4513.4379 | 4436.9423 | 1.724% | 0.3057%
2017-04-15 | 5 | 4531 | 76.6057 | 1.691% | 13.5679 | 0.2994% | 90.1735 | 1.99% | 11 | 4517.4321 | 4440.8265 | 1.725% | 0.3055%
2017-04-15 | 4 | 4545 | 76.991 | 1.694% | 13.5879 | 0.299% | 90.5789 | 1.993% | 12 | 4531.4121 | 4454.4211 | 1.728% | 0.305%
2017-05-14 | 6 | 4551 | 77.1562 | 1.695% | 13.5965 | 0.2988% | 90.7527 | 1.994% | 13 | 4537.4035 | 4460.2473 | 1.73% | 0.3048%
2017-04-16 | 4 | 4558 | 77.3489 | 1.697% | 13.6065 | 0.2985% | 90.9554 | 1.996% | 14 | 4544.3935 | 4467.0446 | 1.732% | 0.3046%
2017-03-26 | 3 | 4561 | 77.4314 | 1.698% | 13.6108 | 0.2984% | 91.0423 | 1.996% | 15 | 4547.3892 | 4469.9577 | 1.732% | 0.3045%
2017-03-27 | 3 | 4567 | 77.5966 | 1.699% | 13.6194 | 0.2982% | 91.216 | 1.997% | 16 | 4553.3806 | 4475.784 | 1.734% | 0.3043%
2017-05-07 | 5 | 4567 | 77.5966 | 1.699% | 13.6194 | 0.2982% | 91.216 | 1.997% | 17 | 4553.3806 | 4475.784 | 1.734% | 0.3043%
2017-05-14 | 3 | 4573 | 77.7617 | 1.7% | 13.628 | 0.298% | 91.3897 | 1.998% | 18 | 4559.372 | 4481.6103 | 1.735% | 0.3041%
2017-04-14 | 4 | 4580 | 77.9544 | 1.702% | 13.638 | 0.2978% | 91.5924 | 2% | 19 | 4566.362 | 4488.4076 | 1.737% | 0.3039%
2017-04-17 | 3 | 4591 | 78.2572 | 1.705% | 13.6538 | 0.2974% | 91.911 | 2.002% | 20 | 4577.3462 | 4499.089 | 1.739% | 0.3035%
2017-05-07 | 4 | 4594 | 78.3398 | 1.705% | 13.6581 | 0.2973% | 91.9979 | 2.003% | 21 | 4580.3419 | 4502.0021 | 1.74% | 0.3034%
2017-04-15 | 6 | 4595 | 78.3673 | 1.705% | 13.6595 | 0.2973% | 92.0268 | 2.003% | 22 | 4581.3405 | 4502.9732 | 1.74% | 0.3033%
2017-04-23 | 5 | 4595 | 78.3673 | 1.705% | 13.6595 | 0.2973% | 92.0268 | 2.003% | 23 | 4581.3405 | 4502.9732 | 1.74% | 0.3033%
2017-05-08 | 4 | 4599 | 78.4774 | 1.706% | 13.6653 | 0.2971% | 92.1426 | 2.004% | 24 | 4585.3347 | 4506.8574 | 1.741% | 0.3032%
2017-04-01 | 4 | 4600 | 78.5049 | 1.707% | 13.6667 | 0.2971% | 92.1716 | 2.004% | 25 | 4586.3333 | 4507.8284 | 1.742% | 0.3032%
2017-04-01 | 5 | 4609 | 78.7526 | 1.709% | 13.6796 | 0.2968% | 92.4322 | 2.005% | 26 | 4595.3204 | 4516.5678 | 1.744% | 0.3029%
2017-04-16 | 6 | 4611 | 78.8077 | 1.709% | 13.6824 | 0.2967% | 92.4901 | 2.006% | 27 | 4597.3176 | 4518.5099 | 1.744% | 0.3028%
2017-04-14 | 5 | 4612 | 78.8352 | 1.709% | 13.6839 | 0.2967% | 92.5191 | 2.006% | 28 | 4598.3161 | 4519.4809 | 1.744% | 0.3028%
2017-04-23 | 6 | 4612 | 78.8352 | 1.709% | 13.6839 | 0.2967% | 92.5191 | 2.006% | 29 | 4598.3161 | 4519.4809 | 1.744% | 0.3028%
2017-05-14 | 7 | 4612 | 78.8352 | 1.709% | 13.6839 | 0.2967% | 92.5191 | 2.006% | 30 | 4598.3161 | 4519.4809 | 1.744% | 0.3028%
2017-04-02 | 6 | 4614 | 78.8903 | 1.71% | 13.6867 | 0.2966% | 92.577 | 2.006% | 31 | 4600.3133 | 4521.423 | 1.745% | 0.3027%
2017-05-08 | 3 | 4615 | 78.9178 | 1.71% | 13.6882 | 0.2966% | 92.606 | 2.007% | 32 | 4601.3118 | 4522.394 | 1.745% | 0.3027%
2017-05-07 | 3 | 4621 | 79.0829 | 1.711% | 13.6968 | 0.2964% | 92.7797 | 2.008% | 33 | 4607.3032 | 4528.2203 | 1.746% | 0.3025%
2017-04-10 | 3 | 4631 | 79.3582 | 1.714% | 13.7111 | 0.2961% | 93.0693 | 2.01% | 34 | 4617.2889 | 4537.9307 | 1.749% | 0.3021%
2017-04-03 | 4 | 4636 | 79.4958 | 1.715% | 13.7183 | 0.2959% | 93.2141 | 2.011% | 35 | 4622.2817 | 4542.7859 | 1.75% | 0.302%
2017-03-27 | 5 | 4646 | 79.7711 | 1.717% | 13.7326 | 0.2956% | 93.5036 | 2.013% | 36 | 4632.2674 | 4552.4964 | 1.752% | 0.3016%
2017-04-03 | 3 | 4646 | 79.7711 | 1.717% | 13.7326 | 0.2956% | 93.5036 | 2.013% | 37 | 4632.2674 | 4552.4964 | 1.752% | 0.3016%
2017-04-01 | 3 | 4650 | 79.8812 | 1.718% | 13.7383 | 0.2954% | 93.6195 | 2.013% | 38 | 4636.2617 | 4556.3805 | 1.753% | 0.3015%
2017-05-06 | 4 | 4650 | 79.8812 | 1.718% | 13.7383 | 0.2954% | 93.6195 | 2.013% | 39 | 4636.2617 | 4556.3805 | 1.753% | 0.3015%
2017-04-02 | 2 | 4653 | 79.9637 | 1.719% | 13.7426 | 0.2953% | 93.7064 | 2.014% | 40 | 4639.2574 | 4559.2936 | 1.754% | 0.3014%
2017-04-23 | 4 | 4653 | 79.9637 | 1.719% | 13.7426 | 0.2953% | 93.7064 | 2.014% | 41 | 4639.2574 | 4559.2936 | 1.754% | 0.3014%
2017-04-10 | 4 | 4656 | 80.0463 | 1.719% | 13.7469 | 0.2953% | 93.7932 | 2.014% | 42 | 4642.2531 | 4562.2068 | 1.755% | 0.3013%
2017-03-26 | 6 | 4665 | 80.294 | 1.721% | 13.7598 | 0.295% | 94.0538 | 2.016% | 43 | 4651.2402 | 4570.9462 | 1.757% | 0.301%
2017-05-06 | 5 | 4667 | 80.3491 | 1.722% | 13.7627 | 0.2949% | 94.1118 | 2.017% | 44 | 4653.2373 | 4572.8882 | 1.757% | 0.301%
2017-05-08 | 2 | 4671 | 80.4592 | 1.723% | 13.7684 | 0.2948% | 94.2276 | 2.017% | 45 | 4657.2316 | 4576.7724 | 1.758% | 0.3008%
2017-05-13 | 5 | 4675 | 80.5693 | 1.723% | 13.7741 | 0.2946% | 94.3434 | 2.018% | 46 | 4661.2259 | 4580.6566 | 1.759% | 0.3007%
2017-04-14 | 3 | 4677 | 80.6243 | 1.724% | 13.777 | 0.2946% | 94.4013 | 2.018% | 47 | 4663.223 | 4582.5987 | 1.759% | 0.3006%
2017-04-15 | 3 | 4680 | 80.7069 | 1.725% | 13.7813 | 0.2945% | 94.4882 | 2.019% | 48 | 4666.2187 | 4585.5118 | 1.76% | 0.3005%
2017-04-11 | 4 | 4683 | 80.7895 | 1.725% | 13.7856 | 0.2944% | 94.5751 | 2.02% | 49 | 4669.2144 | 4588.4249 | 1.761% | 0.3004%
2017-05-09 | 3 | 4683 | 80.7895 | 1.725% | 13.7856 | 0.2944% | 94.5751 | 2.02% | 50 | 4669.2144 | 4588.4249 | 1.761% | 0.3004%
2017-05-13 | 4 | 4686 | 80.8721 | 1.726% | 13.7899 | 0.2943% | 94.662 | 2.02% | 51 | 4672.2101 | 4591.338 | 1.761% | 0.3003%
2017-03-30 | 4 | 4688 | 80.9271 | 1.726% | 13.7927 | 0.2942% | 94.7199 | 2.02% | 52 | 4674.2073 | 4593.2801 | 1.762% | 0.3003%
2017-04-24 | 4 | 4691 | 81.0097 | 1.727% | 13.797 | 0.2941% | 94.8067 | 2.021% | 53 | 4677.203 | 4596.1933 | 1.763% | 0.3002%
2017-03-26 | 2 | 4694 | 81.0923 | 1.728% | 13.8013 | 0.294% | 94.8936 | 2.022% | 54 | 4680.1987 | 4599.1064 | 1.763% | 0.3001%
2017-04-26 | 4 | 4694 | 81.0923 | 1.728% | 13.8013 | 0.294% | 94.8936 | 2.022% | 55 | 4680.1987 | 4599.1064 | 1.763% | 0.3001%
2017-04-19 | 4 | 4695 | 81.1198 | 1.728% | 13.8028 | 0.294% | 94.9226 | 2.022% | 56 | 4681.1972 | 4600.0774 | 1.763% | 0.3001%
2017-05-07 | 6 | 4696 | 81.1473 | 1.728% | 13.8042 | 0.294% | 94.9515 | 2.022% | 57 | 4682.1958 | 4601.0485 | 1.764% | 0.3%
2017-05-06 | 3 | 4697 | 81.1748 | 1.728% | 13.8056 | 0.2939% | 94.9805 | 2.022% | 58 | 4683.1944 | 4602.0195 | 1.764% | 0.3%
2017-05-15 | 4 | 4702 | 81.3125 | 1.729% | 13.8128 | 0.2938% | 95.1253 | 2.023% | 59 | 4688.1872 | 4606.8747 | 1.765% | 0.2998%
2017-04-16 | 7 | 4704 | 81.3675 | 1.73% | 13.8157 | 0.2937% | 95.1832 | 2.023% | 60 | 4690.1843 | 4608.8168 | 1.765% | 0.2998%
2017-03-27 | 2 | 4705 | 81.395 | 1.73% | 13.8171 | 0.2937% | 95.2121 | 2.024% | 61 | 4691.1829 | 4609.7879 | 1.766% | 0.2997%
2017-03-22 | 4 | 4707 | 81.4501 | 1.73% | 13.82 | 0.2936% | 95.2701 | 2.024% | 62 | 4693.18 | 4611.7299 | 1.766% | 0.2997%
2017-03-28 | 4 | 4708 | 81.4776 | 1.731% | 13.8214 | 0.2936% | 95.299 | 2.024% | 63 | 4694.1786 | 4612.701 | 1.766% | 0.2996%
2017-03-30 | 3 | 4712 | 81.5877 | 1.731% | 13.8271 | 0.2934% | 95.4148 | 2.025% | 64 | 4698.1729 | 4616.5852 | 1.767% | 0.2995%
2017-04-03 | 2 | 4712 | 81.5877 | 1.731% | 13.8271 | 0.2934% | 95.4148 | 2.025% | 65 | 4698.1729 | 4616.5852 | 1.767% | 0.2995%
2017-04-16 | 3 | 4714 | 81.6428 | 1.732% | 13.83 | 0.2934% | 95.4728 | 2.025% | 66 | 4700.17 | 4618.5272 | 1.768% | 0.2994%
2017-05-14 | 2 | 4718 | 81.7529 | 1.733% | 13.8357 | 0.2933% | 95.5886 | 2.026% | 67 | 4704.1643 | 4622.4114 | 1.769% | 0.2993%
2017-03-29 | 4 | 4724 | 81.918 | 1.734% | 13.8443 | 0.2931% | 95.7623 | 2.027% | 68 | 4710.1557 | 4628.2377 | 1.77% | 0.2991%
2017-04-24 | 3 | 4724 | 81.918 | 1.734% | 13.8443 | 0.2931% | 95.7623 | 2.027% | 69 | 4710.1557 | 4628.2377 | 1.77% | 0.2991%
2017-05-09 | 4 | 4726 | 81.9731 | 1.735% | 13.8472 | 0.293% | 95.8203 | 2.028% | 70 | 4712.1528 | 4630.1797 | 1.77% | 0.2991%
2017-04-23 | 7 | 4729 | 82.0557 | 1.735% | 13.8515 | 0.2929% | 95.9071 | 2.028% | 71 | 4715.1485 | 4633.0929 | 1.771% | 0.299%
2017-03-22 | 5 | 4730 | 82.0832 | 1.735% | 13.8529 | 0.2929% | 95.9361 | 2.028% | 72 | 4716.1471 | 4634.0639 | 1.771% | 0.2989%
2017-04-10 | 2 | 4735 | 82.2208 | 1.736% | 13.8601 | 0.2927% | 96.0809 | 2.029% | 73 | 4721.1399 | 4638.9191 | 1.772% | 0.2988%
2017-04-01 | 6 | 4745 | 82.4961 | 1.739% | 13.8744 | 0.2924% | 96.3704 | 2.031% | 74 | 4731.1256 | 4648.6296 | 1.775% | 0.2985%
2017-04-15 | 7 | 4745 | 82.4961 | 1.739% | 13.8744 | 0.2924% | 96.3704 | 2.031% | 75 | 4731.1256 | 4648.6296 | 1.775% | 0.2985%
2017-05-07 | 2 | 4750 | 82.6337 | 1.74% | 13.8816 | 0.2922% | 96.5152 | 2.032% | 76 | 4736.1184 | 4653.4848 | 1.776% | 0.2983%
2017-04-11 | 3 | 4762 | 82.964 | 1.742% | 13.8987 | 0.2919% | 96.8627 | 2.034% | 77 | 4748.1013 | 4665.1373 | 1.778% | 0.2979%
2017-04-12 | 4 | 4764 | 83.019 | 1.743% | 13.9016 | 0.2918% | 96.9206 | 2.034% | 78 | 4750.0984 | 4667.0794 | 1.779% | 0.2979%
2017-03-28 | 3 | 4771 | 83.2117 | 1.744% | 13.9116 | 0.2916% | 97.1233 | 2.036% | 79 | 4757.0884 | 4673.8767 | 1.78% | 0.2976%
2017-05-27 | 5 | 4771 | 83.2117 | 1.744% | 13.9116 | 0.2916% | 97.1233 | 2.036% | 80 | 4757.0884 | 4673.8767 | 1.78% | 0.2976%
2017-05-13 | 6 | 4776 | 83.3493 | 1.745% | 13.9188 | 0.2914% | 97.2681 | 2.037% | 81 | 4762.0812 | 4678.7319 | 1.781% | 0.2975%
2017-03-30 | 5 | 4778 | 83.4044 | 1.746% | 13.9217 | 0.2914% | 97.326 | 2.037% | 82 | 4764.0783 | 4680.674 | 1.782% | 0.2974%
2017-04-11 | 5 | 4781 | 83.487 | 1.746% | 13.926 | 0.2913% | 97.4129 | 2.038% | 83 | 4767.074 | 4683.5871 | 1.783% | 0.2973%
2017-05-08 | 5 | 4785 | 83.5971 | 1.747% | 13.9317 | 0.2912% | 97.5287 | 2.038% | 84 | 4771.0683 | 4687.4713 | 1.783% | 0.2972%
2017-03-31 | 4 | 4787 | 83.6521 | 1.747% | 13.9346 | 0.2911% | 97.5867 | 2.039% | 85 | 4773.0654 | 4689.4133 | 1.784% | 0.2971%
2017-03-28 | 5 | 4788 | 83.6796 | 1.748% | 13.936 | 0.2911% | 97.6156 | 2.039% | 86 | 4774.064 | 4690.3844 | 1.784% | 0.2971%
2017-05-09 | 2 | 4788 | 83.6796 | 1.748% | 13.936 | 0.2911% | 97.6156 | 2.039% | 87 | 4774.064 | 4690.3844 | 1.784% | 0.2971%
2017-04-05 | 4 | 4790 | 83.7347 | 1.748% | 13.9389 | 0.291% | 97.6735 | 2.039% | 88 | 4776.0611 | 4692.3265 | 1.785% | 0.2971%
2017-04-20 | 4 | 4790 | 83.7347 | 1.748% | 13.9389 | 0.291% | 97.6735 | 2.039% | 89 | 4776.0611 | 4692.3265 | 1.785% | 0.2971%
2017-05-15 | 5 | 4790 | 83.7347 | 1.748% | 13.9389 | 0.291% | 97.6735 | 2.039% | 90 | 4776.0611 | 4692.3265 | 1.785% | 0.2971%
2017-04-26 | 3 | 4791 | 83.7622 | 1.748% | 13.9403 | 0.291% | 97.7025 | 2.039% | 91 | 4777.0597 | 4693.2975 | 1.785% | 0.297%
2017-05-06 | 6 | 4791 | 83.7622 | 1.748% | 13.9403 | 0.291% | 97.7025 | 2.039% | 92 | 4777.0597 | 4693.2975 | 1.785% | 0.297%
2017-04-19 | 3 | 4792 | 83.7897 | 1.749% | 13.9417 | 0.2909% | 97.7315 | 2.039% | 93 | 4778.0583 | 4694.2685 | 1.785% | 0.297%
2017-04-24 | 2 | 4794 | 83.8448 | 1.749% | 13.9446 | 0.2909% | 97.7894 | 2.04% | 94 | 4780.0554 | 4696.2106 | 1.785% | 0.2969%
2017-05-10 | 4 | 4794 | 83.8448 | 1.749% | 13.9446 | 0.2909% | 97.7894 | 2.04% | 95 | 4780.0554 | 4696.2106 | 1.785% | 0.2969%
2017-05-27 | 4 | 4800 | 84.0099 | 1.75% | 13.9532 | 0.2907% | 97.9631 | 2.041% | 96 | 4786.0468 | 4702.0369 | 1.787% | 0.2967%
2017-05-13 | 3 | 4802 | 84.065 | 1.751% | 13.956 | 0.2906% | 98.021 | 2.041% | 97 | 4788.044 | 4703.979 | 1.787% | 0.2967%
2017-04-19 | 5 | 4804 | 84.12 | 1.751% | 13.9589 | 0.2906% | 98.0789 | 2.042% | 98 | 4790.0411 | 4705.9211 | 1.788% | 0.2966%
2017-03-29 | 3 | 4805 | 84.1476 | 1.751% | 13.9603 | 0.2905% | 98.1079 | 2.042% | 99 | 4791.0397 | 4706.8921 | 1.788% | 0.2966%
2017-03-29 | 5 | 4805 | 84.1476 | 1.751% | 13.9603 | 0.2905% | 98.1079 | 2.042% | 100 | 4791.0397 | 4706.8921 | 1.788% | 0.2966%
2017-04-13 | 4 | 4805 | 84.1476 | 1.751% | 13.9603 | 0.2905% | 98.1079 | 2.042% | 101 | 4791.0397 | 4706.8921 | 1.788% | 0.2966%
2017-05-03 | 4 | 4805 | 84.1476 | 1.751% | 13.9603 | 0.2905% | 98.1079 | 2.042% | 102 | 4791.0397 | 4706.8921 | 1.788% | 0.2966%
2017-05-07 | 7 | 4807 | 84.2026 | 1.752% | 13.9632 | 0.2905% | 98.1658 | 2.042% | 103 | 4793.0368 | 4708.8342 | 1.788% | 0.2965%
2017-05-15 | 3 | 4810 | 84.2852 | 1.752% | 13.9675 | 0.2904% | 98.2527 | 2.043% | 104 | 4796.0325 | 4711.7473 | 1.789% | 0.2964%
2017-05-27 | 6 | 4815 | 84.4228 | 1.753% | 13.9747 | 0.2902% | 98.3975 | 2.044% | 105 | 4801.0253 | 4716.6025 | 1.79% | 0.2963%
2017-04-04 | 4 | 4816 | 84.4503 | 1.754% | 13.9761 | 0.2902% | 98.4264 | 2.044% | 106 | 4802.0239 | 4717.5736 | 1.79% | 0.2963%
2017-05-26 | 4 | 4816 | 84.4503 | 1.754% | 13.9761 | 0.2902% | 98.4264 | 2.044% | 107 | 4802.0239 | 4717.5736 | 1.79% | 0.2963%
2017-04-12 | 5 | 4824 | 84.6705 | 1.755% | 13.9876 | 0.29% | 98.6581 | 2.045% | 108 | 4810.0124 | 4725.3419 | 1.792% | 0.296%
2017-04-24 | 5 | 4825 | 84.6981 | 1.755% | 13.989 | 0.2899% | 98.687 | 2.045% | 109 | 4811.011 | 4726.313 | 1.792% | 0.296%
2017-05-27 | 7 | 4827 | 84.7531 | 1.756% | 13.9918 | 0.2899% | 98.745 | 2.046% | 110 | 4813.0082 | 4728.255 | 1.792% | 0.2959%
2017-04-17 | 2 | 4830 | 84.8357 | 1.756% | 13.9961 | 0.2898% | 98.8318 | 2.046% | 111 | 4816.0039 | 4731.1682 | 1.793% | 0.2958%
2017-04-03 | 5 | 4832 | 84.8907 | 1.757% | 13.999 | 0.2897% | 98.8898 | 2.047% | 112 | 4818.001 | 4733.1102 | 1.794% | 0.2958%
2017-04-02 | 7 | 4833 | 84.9183 | 1.757% | 14.0004 | 0.2897% | 98.9187 | 2.047% | 113 | 4818.9996 | 4734.0813 | 1.794% | 0.2957%
2017-03-30 | 2 | 4834 | 84.9458 | 1.757% | 14.0019 | 0.2897% | 98.9477 | 2.047% | 114 | 4819.9981 | 4735.0523 | 1.794% | 0.2957%
2017-04-06 | 4 | 4834 | 84.9458 | 1.757% | 14.0019 | 0.2897% | 98.9477 | 2.047% | 115 | 4819.9981 | 4735.0523 | 1.794% | 0.2957%
2017-04-26 | 5 | 4834 | 84.9458 | 1.757% | 14.0019 | 0.2897% | 98.9477 | 2.047% | 116 | 4819.9981 | 4735.0523 | 1.794% | 0.2957%
2017-04-10 | 1 | 4835 | 84.9733 | 1.757% | 14.0033 | 0.2896% | 98.9766 | 2.047% | 117 | 4820.9967 | 4736.0234 | 1.794% | 0.2957%
2017-03-08 | 4 | 4838 | 85.0559 | 1.758% | 14.0076 | 0.2895% | 99.0635 | 2.048% | 118 | 4823.9924 | 4738.9365 | 1.795% | 0.2956%
2017-04-01 | 2 | 4838 | 85.0559 | 1.758% | 14.0076 | 0.2895% | 99.0635 | 2.048% | 119 | 4823.9924 | 4738.9365 | 1.795% | 0.2956%
2017-04-23 | 3 | 4838 | 85.0559 | 1.758% | 14.0076 | 0.2895% | 99.0635 | 2.048% | 120 | 4823.9924 | 4738.9365 | 1.795% | 0.2956%
2017-04-14 | 6 | 4841 | 85.1385 | 1.759% | 14.0119 | 0.2894% | 99.1504 | 2.048% | 121 | 4826.9881 | 4741.8496 | 1.795% | 0.2955%
2017-04-12 | 3 | 4844 | 85.221 | 1.759% | 14.0162 | 0.2894% | 99.2372 | 2.049% | 122 | 4829.9838 | 4744.7628 | 1.796% | 0.2954%
2017-05-09 | 5 | 4844 | 85.221 | 1.759% | 14.0162 | 0.2894% | 99.2372 | 2.049% | 123 | 4829.9838 | 4744.7628 | 1.796% | 0.2954%
2017-03-01 | 4 | 4845 | 85.2486 | 1.76% | 14.0176 | 0.2893% | 99.2662 | 2.049% | 124 | 4830.9824 | 4745.7338 | 1.796% | 0.2954%
2017-04-05 | 5 | 4848 | 85.3311 | 1.76% | 14.0219 | 0.2892% | 99.3531 | 2.049% | 125 | 4833.9781 | 4748.6469 | 1.797% | 0.2953%
2017-03-31 | 3 | 4854 | 85.4963 | 1.761% | 14.0305 | 0.2891% | 99.5268 | 2.05% | 126 | 4839.9695 | 4754.4732 | 1.798% | 0.2951%
2017-03-08 | 3 | 4856 | 85.5513 | 1.762% | 14.0334 | 0.289% | 99.5847 | 2.051% | 127 | 4841.9666 | 4756.4153 | 1.799% | 0.295%
2017-04-13 | 5 | 4857 | 85.5789 | 1.762% | 14.0348 | 0.289% | 99.6137 | 2.051% | 128 | 4842.9652 | 4757.3863 | 1.799% | 0.295%
2017-05-10 | 3 | 4859 | 85.6339 | 1.762% | 14.0377 | 0.2889% | 99.6716 | 2.051% | 129 | 4844.9623 | 4759.3284 | 1.799% | 0.295%
2017-05-04 | 4 | 4862 | 85.7165 | 1.763% | 14.042 | 0.2888% | 99.7585 | 2.052% | 130 | 4847.958 | 4762.2415 | 1.8% | 0.2949%
2017-04-20 | 5 | 4865 | 85.7991 | 1.764% | 14.0463 | 0.2887% | 99.8454 | 2.052% | 131 | 4850.9537 | 4765.1546 | 1.801% | 0.2948%
2017-05-03 | 5 | 4866 | 85.8266 | 1.764% | 14.0477 | 0.2887% | 99.8743 | 2.052% | 132 | 4851.9523 | 4766.1257 | 1.801% | 0.2947%
2017-04-10 | 5 | 4868 | 85.8816 | 1.764% | 14.0506 | 0.2886% | 99.9322 | 2.053% | 133 | 4853.9494 | 4768.0678 | 1.801% | 0.2947%
2017-03-02 | 4 | 4870 | 85.9367 | 1.765% | 14.0534 | 0.2886% | 99.9901 | 2.053% | 134 | 4855.9466 | 4770.0099 | 1.802% | 0.2946%
2017-04-06 | 3 | 4872 | 85.9917 | 1.765% | 14.0563 | 0.2885% | 100.0481 | 2.054% | 135 | 4857.9437 | 4771.9519 | 1.802% | 0.2946%
2017-05-03 | 3 | 4873 | 86.0193 | 1.765% | 14.0577 | 0.2885% | 100.077 | 2.054% | 136 | 4858.9423 | 4772.923 | 1.802% | 0.2945%
2017-03-31 | 5 | 4874 | 86.0468 | 1.765% | 14.0592 | 0.2885% | 100.106 | 2.054% | 137 | 4859.9408 | 4773.894 | 1.802% | 0.2945%
2017-04-14 | 2 | 4875 | 86.0743 | 1.766% | 14.0606 | 0.2884% | 100.1349 | 2.054% | 138 | 4860.9394 | 4774.8651 | 1.803% | 0.2945%
2017-04-05 | 3 | 4876 | 86.1018 | 1.766% | 14.062 | 0.2884% | 100.1639 | 2.054% | 139 | 4861.938 | 4775.8361 | 1.803% | 0.2944%
2017-03-26 | 7 | 4877 | 86.1294 | 1.766% | 14.0635 | 0.2884% | 100.1928 | 2.054% | 140 | 4862.9365 | 4776.8072 | 1.803% | 0.2944%
2017-05-26 | 3 | 4877 | 86.1294 | 1.766% | 14.0635 | 0.2884% | 100.1928 | 2.054% | 141 | 4862.9365 | 4776.8072 | 1.803% | 0.2944%
2017-03-25 | 4 | 4878 | 86.1569 | 1.766% | 14.0649 | 0.2883% | 100.2218 | 2.055% | 142 | 4863.9351 | 4777.7782 | 1.803% | 0.2944%
2017-04-18 | 4 | 4878 | 86.1569 | 1.766% | 14.0649 | 0.2883% | 100.2218 | 2.055% | 143 | 4863.9351 | 4777.7782 | 1.803% | 0.2944%
2017-05-10 | 5 | 4879 | 86.1844 | 1.766% | 14.0663 | 0.2883% | 100.2508 | 2.055% | 144 | 4864.9337 | 4778.7492 | 1.803% | 0.2944%
2017-04-04 | 3 | 4881 | 86.2395 | 1.767% | 14.0692 | 0.2882% | 100.3087 | 2.055% | 145 | 4866.9308 | 4780.6913 | 1.804% | 0.2943%
2017-04-15 | 2 | 4883 | 86.2945 | 1.767% | 14.0721 | 0.2882% | 100.3666 | 2.055% | 146 | 4868.9279 | 4782.6334 | 1.804% | 0.2942%
2017-04-16 | 8 | 4883 | 86.2945 | 1.767% | 14.0721 | 0.2882% | 100.3666 | 2.055% | 147 | 4868.9279 | 4782.6334 | 1.804% | 0.2942%
2017-05-06 | 7 | 4886 | 86.3771 | 1.768% | 14.0764 | 0.2881% | 100.4535 | 2.056% | 148 | 4871.9236 | 4785.5465 | 1.805% | 0.2941%
2017-04-11 | 2 | 4887 | 86.4046 | 1.768% | 14.0778 | 0.2881% | 100.4824 | 2.056% | 149 | 4872.9222 | 4786.5176 | 1.805% | 0.2941%
2017-04-17 | 5 | 4889 | 86.4597 | 1.768% | 14.0807 | 0.288% | 100.5403 | 2.056% | 150 | 4874.9193 | 4788.4597 | 1.806% | 0.2941%
2017-04-20 | 3 | 4890 | 86.4872 | 1.769% | 14.0821 | 0.288% | 100.5693 | 2.057% | 151 | 4875.9179 | 4789.4307 | 1.806% | 0.294%
2017-05-26 | 5 | 4893 | 86.5698 | 1.769% | 14.0864 | 0.2879% | 100.6562 | 2.057% | 152 | 4878.9136 | 4792.3438 | 1.806% | 0.2939%
2017-04-03 | 1 | 4896 | 86.6523 | 1.77% | 14.0907 | 0.2878% | 100.743 | 2.058% | 153 | 4881.9093 | 4795.257 | 1.807% | 0.2938%
2017-05-06 | 2 | 4896 | 86.6523 | 1.77% | 14.0907 | 0.2878% | 100.743 | 2.058% | 154 | 4881.9093 | 4795.257 | 1.807% | 0.2938%
2017-03-25 | 3 | 4900 | 86.7625 | 1.771% | 14.0964 | 0.2877% | 100.8589 | 2.058% | 155 | 4885.9036 | 4799.1411 | 1.808% | 0.2937%
2017-04-13 | 3 | 4900 | 86.7625 | 1.771% | 14.0964 | 0.2877% | 100.8589 | 2.058% | 156 | 4885.9036 | 4799.1411 | 1.808% | 0.2937%
2017-04-25 | 4 | 4901 | 86.79 | 1.771% | 14.0978 | 0.2877% | 100.8878 | 2.059% | 157 | 4886.9022 | 4800.1122 | 1.808% | 0.2937%
2017-03-01 | 3 | 4905 | 86.9001 | 1.772% | 14.1036 | 0.2875% | 101.0037 | 2.059% | 158 | 4890.8964 | 4803.9963 | 1.809% | 0.2936%
2017-03-28 | 2 | 4905 | 86.9001 | 1.772% | 14.1036 | 0.2875% | 101.0037 | 2.059% | 159 | 4890.8964 | 4803.9963 | 1.809% | 0.2936%
2017-03-31 | 2 | 4911 | 87.0652 | 1.773% | 14.1122 | 0.2874% | 101.1774 | 2.06% | 160 | 4896.8878 | 4809.8226 | 1.81% | 0.2934%
2017-05-08 | 1 | 4913 | 87.1203 | 1.773% | 14.115 | 0.2873% | 101.2353 | 2.061% | 161 | 4898.885 | 4811.7647 | 1.811% | 0.2933%
2017-03-02 | 3 | 4919 | 87.2854 | 1.774% | 14.1236 | 0.2871% | 101.4091 | 2.062% | 162 | 4904.8764 | 4817.5909 | 1.812% | 0.2932%
2017-04-04 | 5 | 4925 | 87.4506 | 1.776% | 14.1322 | 0.2869% | 101.5828 | 2.063% | 163 | 4910.8678 | 4823.4172 | 1.813% | 0.293%
2017-05-13 | 2 | 4925 | 87.4506 | 1.776% | 14.1322 | 0.2869% | 101.5828 | 2.063% | 164 | 4910.8678 | 4823.4172 | 1.813% | 0.293%
2017-04-06 | 5 | 4926 | 87.4781 | 1.776% | 14.1337 | 0.2869% | 101.6118 | 2.063% | 165 | 4911.8663 | 4824.3882 | 1.813% | 0.293%
2017-04-02 | 1 | 4927 | 87.5056 | 1.776% | 14.1351 | 0.2869% | 101.6407 | 2.063% | 166 | 4912.8649 | 4825.3593 | 1.813% | 0.2929%
2017-04-16 | 2 | 4934 | 87.6983 | 1.777% | 14.1451 | 0.2867% | 101.8434 | 2.064% | 167 | 4919.8549 | 4832.1566 | 1.815% | 0.2927%
2017-04-26 | 2 | 4936 | 87.7534 | 1.778% | 14.148 | 0.2866% | 101.9013 | 2.064% | 168 | 4921.852 | 4834.0987 | 1.815% | 0.2927%
2017-04-23 | 8 | 4937 | 87.7809 | 1.778% | 14.1494 | 0.2866% | 101.9303 | 2.065% | 169 | 4922.8506 | 4835.0697 | 1.816% | 0.2926%
2017-03-08 | 2 | 4939 | 87.8359 | 1.778% | 14.1523 | 0.2865% | 101.9882 | 2.065% | 170 | 4924.8477 | 4837.0118 | 1.816% | 0.2926%
2017-05-04 | 5 | 4943 | 87.946 | 1.779% | 14.158 | 0.2864% | 102.104 | 2.066% | 171 | 4928.842 | 4840.896 | 1.817% | 0.2925%
2017-05-13 | 7 | 4943 | 87.946 | 1.779% | 14.158 | 0.2864% | 102.104 | 2.066% | 172 | 4928.842 | 4840.896 | 1.817% | 0.2925%
2017-03-26 | 1 | 4946 | 88.0286 | 1.78% | 14.1623 | 0.2863% | 102.1909 | 2.066% | 173 | 4931.8377 | 4843.8091 | 1.817% | 0.2924%
2017-04-27 | 4 | 4949 | 88.1112 | 1.78% | 14.1666 | 0.2863% | 102.2778 | 2.067% | 174 | 4934.8334 | 4846.7222 | 1.818% | 0.2923%
2017-04-15 | 8 | 4952 | 88.1938 | 1.781% | 14.1709 | 0.2862% | 102.3647 | 2.067% | 175 | 4937.8291 | 4849.6353 | 1.819% | 0.2922%
2017-03-27 | 1 | 4953 | 88.2213 | 1.781% | 14.1723 | 0.2861% | 102.3936 | 2.067% | 176 | 4938.8277 | 4850.6064 | 1.819% | 0.2922%
2017-03-29 | 2 | 4955 | 88.2763 | 1.782% | 14.1752 | 0.2861% | 102.4515 | 2.068% | 177 | 4940.8248 | 4852.5485 | 1.819% | 0.2921%
2017-05-04 | 3 | 4955 | 88.2763 | 1.782% | 14.1752 | 0.2861% | 102.4515 | 2.068% | 178 | 4940.8248 | 4852.5485 | 1.819% | 0.2921%
2017-05-10 | 2 | 4955 | 88.2763 | 1.782% | 14.1752 | 0.2861% | 102.4515 | 2.068% | 179 | 4940.8248 | 4852.5485 | 1.819% | 0.2921%
2017-04-25 | 3 | 4956 | 88.3039 | 1.782% | 14.1766 | 0.286% | 102.4805 | 2.068% | 180 | 4941.8234 | 4853.5195 | 1.819% | 0.2921%
2017-03-22 | 3 | 4958 | 88.3589 | 1.782% | 14.1795 | 0.286% | 102.5384 | 2.068% | 181 | 4943.8205 | 4855.4616 | 1.82% | 0.292%
2017-03-25 | 5 | 4959 | 88.3864 | 1.782% | 14.1809 | 0.286% | 102.5674 | 2.068% | 182 | 4944.8191 | 4856.4326 | 1.82% | 0.292%
2017-03-08 | 5 | 4961 | 88.4415 | 1.783% | 14.1838 | 0.2859% | 102.6253 | 2.069% | 183 | 4946.8162 | 4858.3747 | 1.82% | 0.2919%
2017-05-14 | 8 | 4962 | 88.469 | 1.783% | 14.1852 | 0.2859% | 102.6542 | 2.069% | 184 | 4947.8148 | 4859.3458 | 1.821% | 0.2919%
2017-04-19 | 2 | 4966 | 88.5791 | 1.784% | 14.191 | 0.2858% | 102.7701 | 2.069% | 185 | 4951.809 | 4863.2299 | 1.821% | 0.2918%
2017-05-27 | 3 | 4967 | 88.6066 | 1.784% | 14.1924 | 0.2857% | 102.799 | 2.07% | 186 | 4952.8076 | 4864.201 | 1.822% | 0.2918%
2017-03-02 | 5 | 4970 | 88.6892 | 1.784% | 14.1967 | 0.2856% | 102.8859 | 2.07% | 187 | 4955.8033 | 4867.1141 | 1.822% | 0.2917%
2017-04-17 | 6 | 4973 | 88.7718 | 1.785% | 14.201 | 0.2856% | 102.9728 | 2.071% | 188 | 4958.799 | 4870.0272 | 1.823% | 0.2916%
2017-05-15 | 2 | 4976 | 88.8544 | 1.786% | 14.2053 | 0.2855% | 103.0596 | 2.071% | 189 | 4961.7947 | 4872.9404 | 1.823% | 0.2915%
2017-03-01 | 5 | 4983 | 89.047 | 1.787% | 14.2153 | 0.2853% | 103.2623 | 2.072% | 190 | 4968.7847 | 4879.7377 | 1.825% | 0.2913%
2017-04-27 | 5 | 4984 | 89.0746 | 1.787% | 14.2167 | 0.2852% | 103.2913 | 2.072% | 191 | 4969.7833 | 4880.7087 | 1.825% | 0.2913%
2017-04-06 | 2 | 4989 | 89.2122 | 1.788% | 14.2239 | 0.2851% | 103.4361 | 2.073% | 192 | 4974.7761 | 4885.5639 | 1.826% | 0.2911%
2017-04-24 | 1 | 4989 | 89.2122 | 1.788% | 14.2239 | 0.2851% | 103.4361 | 2.073% | 193 | 4974.7761 | 4885.5639 | 1.826% | 0.2911%
2017-04-18 | 3 | 4991 | 89.2672 | 1.789% | 14.2268 | 0.285% | 103.494 | 2.074% | 194 | 4976.7732 | 4887.506 | 1.826% | 0.2911%
2017-04-25 | 5 | 4998 | 89.4599 | 1.79% | 14.2368 | 0.2848% | 103.6967 | 2.075% | 195 | 4983.7632 | 4894.3033 | 1.828% | 0.2909%
2017-05-14 | 1 | 5003 | 89.5975 | 1.791% | 14.244 | 0.2847% | 103.8415 | 2.076% | 196 | 4988.756 | 4899.1585 | 1.829% | 0.2907%
2017-03-02 | 2 | 5009 | 89.7627 | 1.792% | 14.2525 | 0.2845% | 104.0152 | 2.077% | 197 | 4994.7475 | 4904.9848 | 1.83% | 0.2906%
2017-04-04 | 2 | 5010 | 89.7902 | 1.792% | 14.254 | 0.2845% | 104.0442 | 2.077% | 198 | 4995.746 | 4905.9558 | 1.83% | 0.2905%
2017-05-26 | 2 | 5013 | 89.8728 | 1.793% | 14.2583 | 0.2844% | 104.1311 | 2.077% | 199 | 4998.7417 | 4908.8689 | 1.831% | 0.2905%
2017-04-01 | 7 | 5015 | 89.9278 | 1.793% | 14.2611 | 0.2844% | 104.189 | 2.078% | 200 | 5000.7389 | 4910.811 | 1.831% | 0.2904%
2017-04-12 | 2 | 5018 | 90.0104 | 1.794% | 14.2654 | 0.2843% | 104.2759 | 2.078% | 201 | 5003.7346 | 4913.7241 | 1.832% | 0.2903%
2017-03-01 | 2 | 5019 | 90.0379 | 1.794% | 14.2669 | 0.2843% | 104.3048 | 2.078% | 202 | 5004.7331 | 4914.6952 | 1.832% | 0.2903%
2017-05-09 | 1 | 5019 | 90.0379 | 1.794% | 14.2669 | 0.2843% | 104.3048 | 2.078% | 203 | 5004.7331 | 4914.6952 | 1.832% | 0.2903%
2017-03-25 | 2 | 5043 | 90.6985 | 1.799% | 14.3013 | 0.2836% | 104.9998 | 2.082% | 204 | 5028.6987 | 4938.0002 | 1.837% | 0.2896%
2017-04-05 | 2 | 5045 | 90.7536 | 1.799% | 14.3041 | 0.2835% | 105.0577 | 2.082% | 205 | 5030.6959 | 4939.9423 | 1.837% | 0.2896%
2017-04-20 | 2 | 5047 | 90.8086 | 1.799% | 14.307 | 0.2835% | 105.1156 | 2.083% | 206 | 5032.693 | 4941.8844 | 1.838% | 0.2895%
2017-04-23 | 2 | 5052 | 90.9463 | 1.8% | 14.3141 | 0.2833% | 105.2604 | 2.084% | 207 | 5037.6859 | 4946.7396 | 1.839% | 0.2894%
2017-05-07 | 1 | 5055 | 91.0288 | 1.801% | 14.3184 | 0.2833% | 105.3473 | 2.084% | 208 | 5040.6816 | 4949.6527 | 1.839% | 0.2893%
2017-03-22 | 2 | 5057 | 91.0839 | 1.801% | 14.3213 | 0.2832% | 105.4052 | 2.084% | 209 | 5042.6787 | 4951.5948 | 1.839% | 0.2892%
2017-04-27 | 3 | 5063 | 91.249 | 1.802% | 14.3299 | 0.283% | 105.5789 | 2.085% | 210 | 5048.6701 | 4957.4211 | 1.841% | 0.2891%
2017-05-16 | 4 | 5066 | 91.3316 | 1.803% | 14.3342 | 0.2829% | 105.6658 | 2.086% | 211 | 5051.6658 | 4960.3342 | 1.841% | 0.289%
2017-04-25 | 2 | 5071 | 91.4692 | 1.804% | 14.3414 | 0.2828% | 105.8106 | 2.087% | 212 | 5056.6586 | 4965.1894 | 1.842% | 0.2888%
2017-04-22 | 5 | 5088 | 91.9372 | 1.807% | 14.3657 | 0.2823% | 106.3029 | 2.089% | 213 | 5073.6343 | 4981.6971 | 1.845% | 0.2884%
2017-04-18 | 5 | 5091 | 92.0198 | 1.807% | 14.37 | 0.2823% | 106.3898 | 2.09% | 214 | 5076.63 | 4984.6102 | 1.846% | 0.2883%
2017-05-16 | 5 | 5092 | 92.0473 | 1.808% | 14.3714 | 0.2822% | 106.4187 | 2.09% | 215 | 5077.6286 | 4985.5813 | 1.846% | 0.2883%
2017-04-11 | 1 | 5097 | 92.1849 | 1.809% | 14.3786 | 0.2821% | 106.5635 | 2.091% | 216 | 5082.6214 | 4990.4365 | 1.847% | 0.2881%
2017-05-03 | 2 | 5104 | 92.3776 | 1.81% | 14.3886 | 0.2819% | 106.7662 | 2.092% | 217 | 5089.6114 | 4997.2338 | 1.849% | 0.2879%
2017-04-02 | 8 | 5106 | 92.4326 | 1.81% | 14.3915 | 0.2819% | 106.8241 | 2.092% | 218 | 5091.6085 | 4999.1759 | 1.849% | 0.2879%
2017-03-27 | 6 | 5119 | 92.7905 | 1.813% | 14.4101 | 0.2815% | 107.2006 | 2.094% | 219 | 5104.5899 | 5011.7994 | 1.851% | 0.2875%
2017-04-01 | 1 | 5119 | 92.7905 | 1.813% | 14.4101 | 0.2815% | 107.2006 | 2.094% | 220 | 5104.5899 | 5011.7994 | 1.851% | 0.2875%
2017-04-13 | 2 | 5120 | 92.818 | 1.813% | 14.4115 | 0.2815% | 107.2295 | 2.094% | 221 | 5105.5885 | 5012.7705 | 1.852% | 0.2875%
2017-04-17 | 1 | 5120 | 92.818 | 1.813% | 14.4115 | 0.2815% | 107.2295 | 2.094% | 222 | 5105.5885 | 5012.7705 | 1.852% | 0.2875%
2017-03-31 | 1 | 5121 | 92.8455 | 1.813% | 14.413 | 0.2814% | 107.2585 | 2.094% | 223 | 5106.587 | 5013.7415 | 1.852% | 0.2875%
2017-03-30 | 1 | 5125 | 92.9556 | 1.814% | 14.4187 | 0.2813% | 107.3743 | 2.095% | 224 | 5110.5813 | 5017.6257 | 1.853% | 0.2874%
2017-05-12 | 5 | 5127 | 93.0107 | 1.814% | 14.4216 | 0.2813% | 107.4322 | 2.095% | 225 | 5112.5784 | 5019.5678 | 1.853% | 0.2873%
2017-05-07 | 8 | 5132 | 93.1483 | 1.815% | 14.4287 | 0.2812% | 107.577 | 2.096% | 226 | 5117.5713 | 5024.423 | 1.854% | 0.2872%
2017-04-07 | 3 | 5135 | 93.2309 | 1.816% | 14.433 | 0.2811% | 107.6639 | 2.097% | 227 | 5120.567 | 5027.3361 | 1.854% | 0.2871%
2017-04-22 | 6 | 5139 | 93.341 | 1.816% | 14.4388 | 0.281% | 107.7797 | 2.097% | 228 | 5124.5612 | 5031.2203 | 1.855% | 0.287%
2017-03-22 | 1 | 5141 | 93.396 | 1.817% | 14.4416 | 0.2809% | 107.8376 | 2.098% | 229 | 5126.5584 | 5033.1624 | 1.856% | 0.2869%
2017-03-08 | 1 | 5143 | 93.4511 | 1.817% | 14.4445 | 0.2809% | 107.8956 | 2.098% | 230 | 5128.5555 | 5035.1044 | 1.856% | 0.2869%
2017-05-12 | 4 | 5147 | 93.5612 | 1.818% | 14.4502 | 0.2808% | 108.0114 | 2.099% | 231 | 5132.5498 | 5038.9886 | 1.857% | 0.2868%
2017-04-12 | 6 | 5148 | 93.5887 | 1.818% | 14.4517 | 0.2807% | 108.0403 | 2.099% | 232 | 5133.5483 | 5039.9597 | 1.857% | 0.2867%
2017-05-04 | 2 | 5148 | 93.5887 | 1.818% | 14.4517 | 0.2807% | 108.0403 | 2.099% | 233 | 5133.5483 | 5039.9597 | 1.857% | 0.2867%
2017-03-25 | 6 | 5149 | 93.6162 | 1.818% | 14.4531 | 0.2807% | 108.0693 | 2.099% | 234 | 5134.5469 | 5040.9307 | 1.857% | 0.2867%
2017-04-21 | 4 | 5149 | 93.6162 | 1.818% | 14.4531 | 0.2807% | 108.0693 | 2.099% | 235 | 5134.5469 | 5040.9307 | 1.857% | 0.2867%
2017-05-06 | 1 | 5151 | 93.6713 | 1.819% | 14.456 | 0.2806% | 108.1272 | 2.099% | 236 | 5136.544 | 5042.8728 | 1.857% | 0.2867%
2017-05-11 | 4 | 5153 | 93.7263 | 1.819% | 14.4588 | 0.2806% | 108.1851 | 2.099% | 237 | 5138.5412 | 5044.8149 | 1.858% | 0.2866%
2017-05-15 | 6 | 5156 | 93.8089 | 1.819% | 14.4631 | 0.2805% | 108.272 | 2.1% | 238 | 5141.5369 | 5047.728 | 1.858% | 0.2865%
2017-04-15 | 1 | 5163 | 94.0016 | 1.821% | 14.4731 | 0.2803% | 108.4747 | 2.101% | 239 | 5148.5269 | 5054.5253 | 1.86% | 0.2863%
2017-05-03 | 6 | 5163 | 94.0016 | 1.821% | 14.4731 | 0.2803% | 108.4747 | 2.101% | 240 | 5148.5269 | 5054.5253 | 1.86% | 0.2863%
2017-04-21 | 5 | 5164 | 94.0291 | 1.821% | 14.4746 | 0.2803% | 108.5037 | 2.101% | 241 | 5149.5254 | 5055.4963 | 1.86% | 0.2863%
2017-04-22 | 4 | 5164 | 94.0291 | 1.821% | 14.4746 | 0.2803% | 108.5037 | 2.101% | 242 | 5149.5254 | 5055.4963 | 1.86% | 0.2863%
2017-05-13 | 1 | 5168 | 94.1392 | 1.822% | 14.4803 | 0.2802% | 108.6195 | 2.102% | 243 | 5153.5197 | 5059.3805 | 1.861% | 0.2862%
2017-03-10 | 3 | 5170 | 94.1942 | 1.822% | 14.4832 | 0.2801% | 108.6774 | 2.102% | 244 | 5155.5168 | 5061.3226 | 1.861% | 0.2862%
2017-04-06 | 1 | 5171 | 94.2218 | 1.822% | 14.4846 | 0.2801% | 108.7064 | 2.102% | 245 | 5156.5154 | 5062.2936 | 1.861% | 0.2861%
2017-04-19 | 6 | 5173 | 94.2768 | 1.822% | 14.4875 | 0.2801% | 108.7643 | 2.103% | 246 | 5158.5125 | 5064.2357 | 1.862% | 0.2861%
2017-03-26 | 8 | 5179 | 94.442 | 1.824% | 14.4961 | 0.2799% | 108.938 | 2.103% | 247 | 5164.5039 | 5070.062 | 1.863% | 0.2859%
2017-05-13 | 8 | 5180 | 94.4695 | 1.824% | 14.4975 | 0.2799% | 108.967 | 2.104% | 248 | 5165.5025 | 5071.033 | 1.863% | 0.2859%
2017-04-11 | 6 | 5182 | 94.5245 | 1.824% | 14.5004 | 0.2798% | 109.0249 | 2.104% | 249 | 5167.4996 | 5072.9751 | 1.863% | 0.2858%
2017-04-26 | 1 | 5182 | 94.5245 | 1.824% | 14.5004 | 0.2798% | 109.0249 | 2.104% | 250 | 5167.4996 | 5072.9751 | 1.863% | 0.2858%
2017-05-11 | 5 | 5184 | 94.5796 | 1.824% | 14.5032 | 0.2798% | 109.0828 | 2.104% | 251 | 5169.4968 | 5074.9172 | 1.864% | 0.2858%
2017-05-26 | 6 | 5186 | 94.6346 | 1.825% | 14.5061 | 0.2797% | 109.1407 | 2.105% | 252 | 5171.4939 | 5076.8593 | 1.864% | 0.2857%
2017-03-22 | 6 | 5188 | 94.6897 | 1.825% | 14.509 | 0.2797% | 109.1986 | 2.105% | 253 | 5173.491 | 5078.8014 | 1.864% | 0.2857%
2017-04-14 | 7 | 5190 | 94.7447 | 1.826% | 14.5118 | 0.2796% | 109.2566 | 2.105% | 254 | 5175.4882 | 5080.7434 | 1.865% | 0.2856%
2017-03-10 | 4 | 5195 | 94.8824 | 1.826% | 14.519 | 0.2795% | 109.4013 | 2.106% | 255 | 5180.481 | 5085.5987 | 1.866% | 0.2855%
2017-04-05 | 6 | 5198 | 94.9649 | 1.827% | 14.5233 | 0.2794% | 109.4882 | 2.106% | 256 | 5183.4767 | 5088.5118 | 1.866% | 0.2854%
2017-04-18 | 2 | 5198 | 94.9649 | 1.827% | 14.5233 | 0.2794% | 109.4882 | 2.106% | 257 | 5183.4767 | 5088.5118 | 1.866% | 0.2854%
2017-04-14 | 1 | 5199 | 94.9925 | 1.827% | 14.5247 | 0.2794% | 109.5172 | 2.107% | 258 | 5184.4753 | 5089.4828 | 1.866% | 0.2854%
2017-03-10 | 2 | 5201 | 95.0475 | 1.827% | 14.5276 | 0.2793% | 109.5751 | 2.107% | 259 | 5186.4724 | 5091.4249 | 1.867% | 0.2853%
2017-04-07 | 4 | 5202 | 95.075 | 1.828% | 14.529 | 0.2793% | 109.604 | 2.107% | 260 | 5187.471 | 5092.396 | 1.867% | 0.2853%
2017-05-24 | 4 | 5204 | 95.1301 | 1.828% | 14.5319 | 0.2792% | 109.662 | 2.107% | 261 | 5189.4681 | 5094.338 | 1.867% | 0.2853%
2017-04-19 | 1 | 5205 | 95.1576 | 1.828% | 14.5333 | 0.2792% | 109.6909 | 2.107% | 262 | 5190.4667 | 5095.3091 | 1.868% | 0.2852%
2017-04-13 | 6 | 5210 | 95.2952 | 1.829% | 14.5405 | 0.2791% | 109.8357 | 2.108% | 263 | 5195.4595 | 5100.1643 | 1.868% | 0.2851%
2017-03-29 | 6 | 5213 | 95.3778 | 1.83% | 14.5448 | 0.279% | 109.9226 | 2.109% | 264 | 5198.4552 | 5103.0774 | 1.869% | 0.285%
2017-03-28 | 6 | 5217 | 95.4879 | 1.83% | 14.5505 | 0.2789% | 110.0384 | 2.109% | 265 | 5202.4495 | 5106.9616 | 1.87% | 0.2849%
2017-05-16 | 3 | 5220 | 95.5705 | 1.831% | 14.5548 | 0.2788% | 110.1253 | 2.11% | 266 | 5205.4452 | 5109.8747 | 1.87% | 0.2848%
2017-04-20 | 6 | 5221 | 95.598 | 1.831% | 14.5562 | 0.2788% | 110.1542 | 2.11% | 267 | 5206.4438 | 5110.8458 | 1.87% | 0.2848%
2017-05-10 | 1 | 5222 | 95.6255 | 1.831% | 14.5577 | 0.2788% | 110.1832 | 2.11% | 268 | 5207.4423 | 5111.8168 | 1.871% | 0.2848%
2017-05-12 | 3 | 5222 | 95.6255 | 1.831% | 14.5577 | 0.2788% | 110.1832 | 2.11% | 269 | 5207.4423 | 5111.8168 | 1.871% | 0.2848%
2017-03-01 | 1 | 5223 | 95.6531 | 1.831% | 14.5591 | 0.2787% | 110.2122 | 2.11% | 270 | 5208.4409 | 5112.7878 | 1.871% | 0.2848%
2017-04-07 | 2 | 5224 | 95.6806 | 1.832% | 14.5605 | 0.2787% | 110.2411 | 2.11% | 271 | 5209.4395 | 5113.7589 | 1.871% | 0.2847%
2017-05-06 | 8 | 5229 | 95.8182 | 1.832% | 14.5677 | 0.2786% | 110.3859 | 2.111% | 272 | 5214.4323 | 5118.6141 | 1.872% | 0.2846%
2017-05-21 | 6 | 5229 | 95.8182 | 1.832% | 14.5677 | 0.2786% | 110.3859 | 2.111% | 273 | 5214.4323 | 5118.6141 | 1.872% | 0.2846%
2017-05-21 | 7 | 5230 | 95.8457 | 1.833% | 14.5691 | 0.2786% | 110.4149 | 2.111% | 274 | 5215.4309 | 5119.5851 | 1.872% | 0.2846%
2017-05-28 | 7 | 5232 | 95.9008 | 1.833% | 14.572 | 0.2785% | 110.4728 | 2.111% | 275 | 5217.428 | 5121.5272 | 1.873% | 0.2845%
2017-04-09 | 24 | 5240 | 96.121 | 1.834% | 14.5834 | 0.2783% | 110.7044 | 2.113% | 276 | 5225.4166 | 5129.2956 | 1.874% | 0.2843%
2017-05-27 | 2 | 5241 | 96.1485 | 1.835% | 14.5849 | 0.2783% | 110.7334 | 2.113% | 277 | 5226.4151 | 5130.2666 | 1.874% | 0.2843%
2017-05-27 | 8 | 5249 | 96.3687 | 1.836% | 14.5963 | 0.2781% | 110.9651 | 2.114% | 278 | 5234.4037 | 5138.0349 | 1.876% | 0.2841%
2017-05-21 | 5 | 5251 | 96.4238 | 1.836% | 14.5992 | 0.278% | 111.023 | 2.114% | 279 | 5236.4008 | 5139.977 | 1.876% | 0.284%
2017-05-07 | 24 | 5253 | 96.4788 | 1.837% | 14.6021 | 0.278% | 111.0809 | 2.115% | 280 | 5238.3979 | 5141.9191 | 1.876% | 0.284%
2017-04-24 | 6 | 5254 | 96.5063 | 1.837% | 14.6035 | 0.2779% | 111.1098 | 2.115% | 281 | 5239.3965 | 5142.8902 | 1.877% | 0.284%
2017-05-11 | 3 | 5255 | 96.5339 | 1.837% | 14.6049 | 0.2779% | 111.1388 | 2.115% | 282 | 5240.3951 | 5143.8612 | 1.877% | 0.2839%
2017-04-26 | 6 | 5261 | 96.699 | 1.838% | 14.6135 | 0.2778% | 111.3125 | 2.116% | 283 | 5246.3865 | 5149.6875 | 1.878% | 0.2838%
2017-05-28 | 6 | 5261 | 96.699 | 1.838% | 14.6135 | 0.2778% | 111.3125 | 2.116% | 284 | 5246.3865 | 5149.6875 | 1.878% | 0.2838%
2017-04-22 | 7 | 5263 | 96.7541 | 1.838% | 14.6164 | 0.2777% | 111.3705 | 2.116% | 285 | 5248.3836 | 5151.6295 | 1.878% | 0.2837%
2017-05-10 | 6 | 5263 | 96.7541 | 1.838% | 14.6164 | 0.2777% | 111.3705 | 2.116% | 286 | 5248.3836 | 5151.6295 | 1.878% | 0.2837%
2017-05-15 | 1 | 5263 | 96.7541 | 1.838% | 14.6164 | 0.2777% | 111.3705 | 2.116% | 287 | 5248.3836 | 5151.6295 | 1.878% | 0.2837%
2017-04-18 | 6 | 5264 | 96.7816 | 1.839% | 14.6178 | 0.2777% | 111.3994 | 2.116% | 288 | 5249.3822 | 5152.6006 | 1.878% | 0.2837%
2017-04-04 | 1 | 5266 | 96.8367 | 1.839% | 14.6207 | 0.2776% | 111.4573 | 2.117% | 289 | 5251.3793 | 5154.5427 | 1.879% | 0.2836%
2017-05-22 | 4 | 5269 | 96.9192 | 1.839% | 14.625 | 0.2776% | 111.5442 | 2.117% | 290 | 5254.375 | 5157.4558 | 1.879% | 0.2836%
2017-04-16 | 1 | 5270 | 96.9468 | 1.84% | 14.6264 | 0.2775% | 111.5732 | 2.117% | 291 | 5255.3736 | 5158.4268 | 1.879% | 0.2835%
2017-03-30 | 6 | 5271 | 96.9743 | 1.84% | 14.6278 | 0.2775% | 111.6021 | 2.117% | 292 | 5256.3722 | 5159.3979 | 1.88% | 0.2835%
2017-05-24 | 5 | 5271 | 96.9743 | 1.84% | 14.6278 | 0.2775% | 111.6021 | 2.117% | 293 | 5256.3722 | 5159.3979 | 1.88% | 0.2835%
2017-05-25 | 5 | 5273 | 97.0293 | 1.84% | 14.6307 | 0.2775% | 111.66 | 2.118% | 294 | 5258.3693 | 5161.34 | 1.88% | 0.2835%
2017-04-02 | 24 | 5274 | 97.0569 | 1.84% | 14.6321 | 0.2774% | 111.689 | 2.118% | 295 | 5259.3679 | 5162.311 | 1.88% | 0.2834%
2017-04-21 | 3 | 5274 | 97.0569 | 1.84% | 14.6321 | 0.2774% | 111.689 | 2.118% | 296 | 5259.3679 | 5162.311 | 1.88% | 0.2834%
2017-05-08 | 6 | 5274 | 97.0569 | 1.84% | 14.6321 | 0.2774% | 111.689 | 2.118% | 297 | 5259.3679 | 5162.311 | 1.88% | 0.2834%
2017-05-28 | 5 | 5274 | 97.0569 | 1.84% | 14.6321 | 0.2774% | 111.689 | 2.118% | 298 | 5259.3679 | 5162.311 | 1.88% | 0.2834%
2017-05-25 | 4 | 5275 | 97.0844 | 1.84% | 14.6336 | 0.2774% | 111.7179 | 2.118% | 299 | 5260.3664 | 5163.2821 | 1.88% | 0.2834%
2017-03-02 | 1 | 5278 | 97.167 | 1.841% | 14.6379 | 0.2773% | 111.8048 | 2.118% | 300 | 5263.3621 | 5166.1952 | 1.881% | 0.2833%
2017-03-10 | 1 | 5279 | 97.1945 | 1.841% | 14.6393 | 0.2773% | 111.8338 | 2.118% | 301 | 5264.3607 | 5167.1662 | 1.881% | 0.2833%
2017-04-06 | 6 | 5282 | 97.2771 | 1.842% | 14.6436 | 0.2772% | 111.9207 | 2.119% | 302 | 5267.3564 | 5170.0793 | 1.882% | 0.2832%
2017-04-27 | 2 | 5287 | 97.4147 | 1.843% | 14.6508 | 0.2771% | 112.0654 | 2.12% | 303 | 5272.3492 | 5174.9346 | 1.882% | 0.2831%
2017-03-31 | 6 | 5288 | 97.4422 | 1.843% | 14.6522 | 0.2771% | 112.0944 | 2.12% | 304 | 5273.3478 | 5175.9056 | 1.883% | 0.2831%
2017-05-24 | 3 | 5290 | 97.4973 | 1.843% | 14.6551 | 0.277% | 112.1523 | 2.12% | 305 | 5275.3449 | 5177.8477 | 1.883% | 0.283%
2017-04-20 | 1 | 5294 | 97.6074 | 1.844% | 14.6608 | 0.2769% | 112.2681 | 2.121% | 306 | 5279.3392 | 5181.7319 | 1.884% | 0.2829%
2017-04-25 | 1 | 5300 | 97.7725 | 1.845% | 14.6694 | 0.2768% | 112.4419 | 2.122% | 307 | 5285.3306 | 5187.5581 | 1.885% | 0.2828%
2017-04-05 | 1 | 5304 | 97.8826 | 1.845% | 14.6751 | 0.2767% | 112.5577 | 2.122% | 308 | 5289.3249 | 5191.4423 | 1.885% | 0.2827%
2017-05-09 | 6 | 5304 | 97.8826 | 1.845% | 14.6751 | 0.2767% | 112.5577 | 2.122% | 309 | 5289.3249 | 5191.4423 | 1.885% | 0.2827%
2017-05-29 | 5 | 5305 | 97.9101 | 1.846% | 14.6765 | 0.2767% | 112.5867 | 2.122% | 310 | 5290.3235 | 5192.4133 | 1.886% | 0.2827%
2017-04-04 | 6 | 5307 | 97.9652 | 1.846% | 14.6794 | 0.2766% | 112.6446 | 2.123% | 311 | 5292.3206 | 5194.3554 | 1.886% | 0.2826%
2017-05-29 | 6 | 5311 | 98.0753 | 1.847% | 14.6851 | 0.2765% | 112.7604 | 2.123% | 312 | 5296.3149 | 5198.2396 | 1.887% | 0.2825%
2017-04-09 | 2 | 5316 | 98.2129 | 1.847% | 14.6923 | 0.2764% | 112.9052 | 2.124% | 313 | 5301.3077 | 5203.0948 | 1.888% | 0.2824%
2017-05-04 | 6 | 5316 | 98.2129 | 1.847% | 14.6923 | 0.2764% | 112.9052 | 2.124% | 314 | 5301.3077 | 5203.0948 | 1.888% | 0.2824%
2017-04-03 | 6 | 5322 | 98.3781 | 1.849% | 14.7009 | 0.2762% | 113.079 | 2.125% | 315 | 5307.2991 | 5208.921 | 1.889% | 0.2822%
2017-05-29 | 7 | 5324 | 98.4331 | 1.849% | 14.7038 | 0.2762% | 113.1369 | 2.125% | 316 | 5309.2962 | 5210.8631 | 1.889% | 0.2822%
2017-04-23 | 24 | 5325 | 98.4606 | 1.849% | 14.7052 | 0.2762% | 113.1658 | 2.125% | 317 | 5310.2948 | 5211.8342 | 1.889% | 0.2822%
2017-04-01 | 8 | 5326 | 98.4882 | 1.849% | 14.7066 | 0.2761% | 113.1948 | 2.125% | 318 | 5311.2934 | 5212.8052 | 1.889% | 0.2821%
2017-04-12 | 1 | 5332 | 98.6533 | 1.85% | 14.7152 | 0.276% | 113.3685 | 2.126% | 319 | 5317.2848 | 5218.6315 | 1.89% | 0.282%
2017-04-09 | 3 | 5334 | 98.7084 | 1.851% | 14.7181 | 0.2759% | 113.4264 | 2.126% | 320 | 5319.2819 | 5220.5736 | 1.891% | 0.2819%
2017-04-27 | 6 | 5345 | 99.0111 | 1.852% | 14.7338 | 0.2757% | 113.745 | 2.128% | 321 | 5330.2662 | 5231.255 | 1.893% | 0.2817%
2017-05-22 | 3 | 5346 | 99.0387 | 1.853% | 14.7353 | 0.2756% | 113.7739 | 2.128% | 322 | 5331.2647 | 5232.2261 | 1.893% | 0.2816%
2017-05-03 | 1 | 5348 | 99.0937 | 1.853% | 14.7381 | 0.2756% | 113.8318 | 2.128% | 323 | 5333.2619 | 5234.1682 | 1.893% | 0.2816%
2017-05-21 | 4 | 5348 | 99.0937 | 1.853% | 14.7381 | 0.2756% | 113.8318 | 2.128% | 324 | 5333.2619 | 5234.1682 | 1.893% | 0.2816%
2017-05-05 | 4 | 5351 | 99.1763 | 1.853% | 14.7424 | 0.2755% | 113.9187 | 2.129% | 325 | 5336.2576 | 5237.0813 | 1.894% | 0.2815%
2017-05-01 | 4 | 5353 | 99.2313 | 1.854% | 14.7453 | 0.2755% | 113.9766 | 2.129% | 326 | 5338.2547 | 5239.0234 | 1.894% | 0.2815%
2017-04-01 | 24 | 5355 | 99.2864 | 1.854% | 14.7482 | 0.2754% | 114.0346 | 2.129% | 327 | 5340.2518 | 5240.9654 | 1.894% | 0.2814%
2017-04-13 | 1 | 5356 | 99.3139 | 1.854% | 14.7496 | 0.2754% | 114.0635 | 2.13% | 328 | 5341.2504 | 5241.9365 | 1.895% | 0.2814%
2017-05-23 | 4 | 5356 | 99.3139 | 1.854% | 14.7496 | 0.2754% | 114.0635 | 2.13% | 329 | 5341.2504 | 5241.9365 | 1.895% | 0.2814%
2017-03-26 | 24 | 5361 | 99.4515 | 1.855% | 14.7568 | 0.2753% | 114.2083 | 2.13% | 330 | 5346.2432 | 5246.7917 | 1.895% | 0.2813%
2017-04-23 | 9 | 5362 | 99.4791 | 1.855% | 14.7582 | 0.2752% | 114.2373 | 2.13% | 331 | 5347.2418 | 5247.7627 | 1.896% | 0.2812%
2017-05-26 | 1 | 5367 | 99.6167 | 1.856% | 14.7654 | 0.2751% | 114.382 | 2.131% | 332 | 5352.2346 | 5252.618 | 1.897% | 0.2811%
2017-03-25 | 24 | 5371 | 99.7268 | 1.857% | 14.7711 | 0.275% | 114.4979 | 2.132% | 333 | 5356.2289 | 5256.5021 | 1.897% | 0.281%
2017-05-22 | 5 | 5371 | 99.7268 | 1.857% | 14.7711 | 0.275% | 114.4979 | 2.132% | 334 | 5356.2289 | 5256.5021 | 1.897% | 0.281%
2017-04-22 | 3 | 5373 | 99.7818 | 1.857% | 14.7739 | 0.275% | 114.5558 | 2.132% | 335 | 5358.2261 | 5258.4442 | 1.898% | 0.281%
2017-05-06 | 24 | 5374 | 99.8094 | 1.857% | 14.7754 | 0.2749% | 114.5847 | 2.132% | 336 | 5359.2246 | 5259.4153 | 1.898% | 0.2809%
2017-04-07 | 5 | 5378 | 99.9195 | 1.858% | 14.7811 | 0.2748% | 114.7006 | 2.133% | 337 | 5363.2189 | 5263.2994 | 1.898% | 0.2808%
2017-05-29 | 4 | 5379 | 99.947 | 1.858% | 14.7825 | 0.2748% | 114.7295 | 2.133% | 338 | 5364.2175 | 5264.2705 | 1.899% | 0.2808%
2017-03-10 | 5 | 5380 | 99.9745 | 1.858% | 14.784 | 0.2748% | 114.7585 | 2.133% | 339 | 5365.216 | 5265.2415 | 1.899% | 0.2808%
2017-04-14 | 8 | 5389 | 100.2222 | 1.86% | 14.7969 | 0.2746% | 115.0191 | 2.134% | 340 | 5374.2031 | 5273.9809 | 1.9% | 0.2806%
2017-03-25 | 1 | 5393 | 100.3323 | 1.86% | 14.8026 | 0.2745% | 115.1349 | 2.135% | 341 | 5378.1974 | 5277.8651 | 1.901% | 0.2805%
2017-04-07 | 1 | 5395 | 100.3874 | 1.861% | 14.8055 | 0.2744% | 115.1929 | 2.135% | 342 | 5380.1945 | 5279.8071 | 1.901% | 0.2804%
2017-05-25 | 3 | 5396 | 100.4149 | 1.861% | 14.8069 | 0.2744% | 115.2218 | 2.135% | 343 | 5381.1931 | 5280.7782 | 1.902% | 0.2804%
2017-04-09 | 1 | 5397 | 100.4424 | 1.861% | 14.8083 | 0.2744% | 115.2508 | 2.135% | 344 | 5382.1917 | 5281.7492 | 1.902% | 0.2804%
2017-04-10 | 6 | 5397 | 100.4424 | 1.861% | 14.8083 | 0.2744% | 115.2508 | 2.135% | 345 | 5382.1917 | 5281.7492 | 1.902% | 0.2804%
2017-05-05 | 3 | 5397 | 100.4424 | 1.861% | 14.8083 | 0.2744% | 115.2508 | 2.135% | 346 | 5382.1917 | 5281.7492 | 1.902% | 0.2804%
2017-05-16 | 6 | 5398 | 100.47 | 1.861% | 14.8098 | 0.2744% | 115.2797 | 2.136% | 347 | 5383.1902 | 5282.7203 | 1.902% | 0.2803%
2017-05-28 | 4 | 5400 | 100.525 | 1.862% | 14.8126 | 0.2743% | 115.3376 | 2.136% | 348 | 5385.1874 | 5284.6624 | 1.902% | 0.2803%
2017-03-08 | 6 | 5404 | 100.6351 | 1.862% | 14.8184 | 0.2742% | 115.4535 | 2.136% | 349 | 5389.1816 | 5288.5465 | 1.903% | 0.2802%
2017-04-25 | 6 | 5404 | 100.6351 | 1.862% | 14.8184 | 0.2742% | 115.4535 | 2.136% | 350 | 5389.1816 | 5288.5465 | 1.903% | 0.2802%
2017-04-09 | 4 | 5405 | 100.6626 | 1.862% | 14.8198 | 0.2742% | 115.4824 | 2.137% | 351 | 5390.1802 | 5289.5176 | 1.903% | 0.2802%
2017-05-17 | 5 | 5405 | 100.6626 | 1.862% | 14.8198 | 0.2742% | 115.4824 | 2.137% | 352 | 5390.1802 | 5289.5176 | 1.903% | 0.2802%
2017-05-14 | 9 | 5408 | 100.7452 | 1.863% | 14.8241 | 0.2741% | 115.5693 | 2.137% | 353 | 5393.1759 | 5292.4307 | 1.904% | 0.2801%
2017-04-15 | 9 | 5411 | 100.8278 | 1.863% | 14.8284 | 0.274% | 115.6562 | 2.137% | 354 | 5396.1716 | 5295.3438 | 1.904% | 0.28%
2017-05-13 | 24 | 5412 | 100.8553 | 1.864% | 14.8298 | 0.274% | 115.6851 | 2.138% | 355 | 5397.1702 | 5296.3149 | 1.904% | 0.28%
2017-05-17 | 4 | 5414 | 100.9104 | 1.864% | 14.8327 | 0.274% | 115.743 | 2.138% | 356 | 5399.1673 | 5298.257 | 1.905% | 0.28%
2017-05-24 | 2 | 5417 | 100.9929 | 1.864% | 14.837 | 0.2739% | 115.8299 | 2.138% | 357 | 5402.163 | 5301.1701 | 1.905% | 0.2799%
2017-04-28 | 4 | 5424 | 101.1856 | 1.866% | 14.847 | 0.2737% | 116.0326 | 2.139% | 358 | 5409.153 | 5307.9674 | 1.906% | 0.2797%
2017-04-30 | 5 | 5426 | 101.2407 | 1.866% | 14.8499 | 0.2737% | 116.0905 | 2.14% | 359 | 5411.1501 | 5309.9095 | 1.907% | 0.2797%
2017-05-01 | 5 | 5428 | 101.2957 | 1.866% | 14.8527 | 0.2736% | 116.1485 | 2.14% | 360 | 5413.1473 | 5311.8515 | 1.907% | 0.2796%
2017-04-30 | 6 | 5429 | 101.3232 | 1.866% | 14.8542 | 0.2736% | 116.1774 | 2.14% | 361 | 5414.1458 | 5312.8226 | 1.907% | 0.2796%
2017-05-02 | 5 | 5431 | 101.3783 | 1.867% | 14.857 | 0.2736% | 116.2353 | 2.14% | 362 | 5416.143 | 5314.7647 | 1.907% | 0.2795%
2017-05-20 | 5 | 5431 | 101.3783 | 1.867% | 14.857 | 0.2736% | 116.2353 | 2.14% | 363 | 5416.143 | 5314.7647 | 1.907% | 0.2795%
2017-05-05 | 5 | 5432 | 101.4058 | 1.867% | 14.8585 | 0.2735% | 116.2643 | 2.14% | 364 | 5417.1415 | 5315.7357 | 1.908% | 0.2795%
2017-03-01 | 6 | 5433 | 101.4333 | 1.867% | 14.8599 | 0.2735% | 116.2932 | 2.14% | 365 | 5418.1401 | 5316.7068 | 1.908% | 0.2795%
2017-04-23 | 1 | 5436 | 101.5159 | 1.867% | 14.8642 | 0.2734% | 116.3801 | 2.141% | 366 | 5421.1358 | 5319.6199 | 1.908% | 0.2794%
2017-03-02 | 6 | 5438 | 101.571 | 1.868% | 14.8671 | 0.2734% | 116.438 | 2.141% | 367 | 5423.1329 | 5321.562 | 1.909% | 0.2794%
2017-05-23 | 5 | 5441 | 101.6536 | 1.868% | 14.8714 | 0.2733% | 116.5249 | 2.142% | 368 | 5426.1286 | 5324.4751 | 1.909% | 0.2793%
2017-05-07 | 9 | 5443 | 101.7086 | 1.869% | 14.8742 | 0.2733% | 116.5828 | 2.142% | 369 | 5428.1258 | 5326.4172 | 1.91% | 0.2793%
2017-05-16 | 2 | 5444 | 101.7361 | 1.869% | 14.8756 | 0.2732% | 116.6118 | 2.142% | 370 | 5429.1244 | 5327.3882 | 1.91% | 0.2792%
2017-05-21 | 8 | 5448 | 101.8462 | 1.869% | 14.8814 | 0.2732% | 116.7276 | 2.143% | 371 | 5433.1186 | 5331.2724 | 1.91% | 0.2791%
2017-05-01 | 3 | 5449 | 101.8738 | 1.87% | 14.8828 | 0.2731% | 116.7566 | 2.143% | 372 | 5434.1172 | 5332.2434 | 1.911% | 0.2791%
2017-05-11 | 2 | 5452 | 101.9563 | 1.87% | 14.8871 | 0.2731% | 116.8434 | 2.143% | 373 | 5437.1129 | 5335.1566 | 1.911% | 0.279%
2017-05-12 | 2 | 5453 | 101.9839 | 1.87% | 14.8885 | 0.273% | 116.8724 | 2.143% | 374 | 5438.1115 | 5336.1276 | 1.911% | 0.279%
2017-05-12 | 6 | 5455 | 102.0389 | 1.871% | 14.8914 | 0.273% | 116.9303 | 2.144% | 375 | 5440.1086 | 5338.0697 | 1.912% | 0.279%
2017-03-07 | 24 | 5459 | 102.149 | 1.871% | 14.8971 | 0.2729% | 117.0461 | 2.144% | 376 | 5444.1029 | 5341.9539 | 1.912% | 0.2789%
2017-03-28 | 1 | 5459 | 102.149 | 1.871% | 14.8971 | 0.2729% | 117.0461 | 2.144% | 377 | 5444.1029 | 5341.9539 | 1.912% | 0.2789%
2017-05-02 | 4 | 5463 | 102.2591 | 1.872% | 14.9029 | 0.2728% | 117.162 | 2.145% | 378 | 5448.0971 | 5345.838 | 1.913% | 0.2788%
2017-05-23 | 3 | 5472 | 102.5068 | 1.873% | 14.9158 | 0.2726% | 117.4226 | 2.146% | 379 | 5457.0842 | 5354.5774 | 1.914% | 0.2786%
2017-04-28 | 5 | 5483 | 102.8096 | 1.875% | 14.9315 | 0.2723% | 117.7411 | 2.147% | 380 | 5468.0685 | 5365.2589 | 1.916% | 0.2783%
2017-04-30 | 7 | 5484 | 102.8371 | 1.875% | 14.9329 | 0.2723% | 117.7701 | 2.148% | 381 | 5469.0671 | 5366.2299 | 1.916% | 0.2783%
2017-05-22 | 2 | 5485 | 102.8647 | 1.875% | 14.9344 | 0.2723% | 117.799 | 2.148% | 382 | 5470.0656 | 5367.201 | 1.917% | 0.2783%
2017-04-21 | 6 | 5488 | 102.9472 | 1.876% | 14.9387 | 0.2722% | 117.8859 | 2.148% | 383 | 5473.0613 | 5370.1141 | 1.917% | 0.2782%
2017-05-20 | 6 | 5490 | 103.0023 | 1.876% | 14.9415 | 0.2722% | 117.9438 | 2.148% | 384 | 5475.0585 | 5372.0562 | 1.917% | 0.2781%
2017-03-12 | 2 | 5493 | 103.0849 | 1.877% | 14.9458 | 0.2721% | 118.0307 | 2.149% | 385 | 5478.0542 | 5374.9693 | 1.918% | 0.2781%
2017-05-11 | 6 | 5500 | 103.2775 | 1.878% | 14.9559 | 0.2719% | 118.2334 | 2.15% | 386 | 5485.0441 | 5381.7666 | 1.919% | 0.2779%
2017-05-20 | 4 | 5501 | 103.3051 | 1.878% | 14.9573 | 0.2719% | 118.2624 | 2.15% | 387 | 5486.0427 | 5382.7376 | 1.919% | 0.2779%
2017-04-16 | 9 | 5504 | 103.3876 | 1.878% | 14.9616 | 0.2718% | 118.3492 | 2.15% | 388 | 5489.0384 | 5385.6508 | 1.92% | 0.2778%
2017-05-04 | 1 | 5504 | 103.3876 | 1.878% | 14.9616 | 0.2718% | 118.3492 | 2.15% | 389 | 5489.0384 | 5385.6508 | 1.92% | 0.2778%
2017-03-21 | 3 | 5509 | 103.5253 | 1.879% | 14.9688 | 0.2717% | 118.494 | 2.151% | 390 | 5494.0312 | 5390.506 | 1.921% | 0.2777%
2017-03-25 | 7 | 5511 | 103.5803 | 1.88% | 14.9716 | 0.2717% | 118.5519 | 2.151% | 391 | 5496.0284 | 5392.4481 | 1.921% | 0.2776%
2017-03-29 | 1 | 5515 | 103.6904 | 1.88% | 14.9773 | 0.2716% | 118.6678 | 2.152% | 392 | 5500.0227 | 5396.3322 | 1.921% | 0.2775%
2017-05-18 | 4 | 5519 | 103.8005 | 1.881% | 14.9831 | 0.2715% | 118.7836 | 2.152% | 393 | 5504.0169 | 5400.2164 | 1.922% | 0.2775%
2017-04-28 | 3 | 5521 | 103.8556 | 1.881% | 14.9859 | 0.2714% | 118.8415 | 2.153% | 394 | 5506.0141 | 5402.1585 | 1.922% | 0.2774%
2017-04-22 | 8 | 5522 | 103.8831 | 1.881% | 14.9874 | 0.2714% | 118.8705 | 2.153% | 395 | 5507.0126 | 5403.1295 | 1.923% | 0.2774%
2017-05-08 | 24 | 5522 | 103.8831 | 1.881% | 14.9874 | 0.2714% | 118.8705 | 2.153% | 396 | 5507.0126 | 5403.1295 | 1.923% | 0.2774%
2017-04-18 | 1 | 5529 | 104.0758 | 1.882% | 14.9974 | 0.2712% | 119.0732 | 2.154% | 397 | 5514.0026 | 5409.9268 | 1.924% | 0.2772%
2017-05-30 | 4 | 5529 | 104.0758 | 1.882% | 14.9974 | 0.2712% | 119.0732 | 2.154% | 398 | 5514.0026 | 5409.9268 | 1.924% | 0.2772%
2017-03-21 | 4 | 5530 | 104.1033 | 1.883% | 14.9988 | 0.2712% | 119.1021 | 2.154% | 399 | 5515.0012 | 5410.8979 | 1.924% | 0.2772%
2017-05-18 | 5 | 5534 | 104.2134 | 1.883% | 15.0046 | 0.2711% | 119.218 | 2.154% | 400 | 5518.9954 | 5414.782 | 1.925% | 0.2771%
2017-05-30 | 5 | 5535 | 104.2409 | 1.883% | 15.006 | 0.2711% | 119.2469 | 2.154% | 401 | 5519.994 | 5415.7531 | 1.925% | 0.2771%
2017-04-17 | 7 | 5537 | 104.296 | 1.884% | 15.0089 | 0.2711% | 119.3048 | 2.155% | 402 | 5521.9911 | 5417.6952 | 1.925% | 0.277%
2017-04-30 | 4 | 5538 | 104.3235 | 1.884% | 15.0103 | 0.271% | 119.3338 | 2.155% | 403 | 5522.9897 | 5418.6662 | 1.925% | 0.277%
2017-04-21 | 2 | 5551 | 104.6813 | 1.886% | 15.0289 | 0.2707% | 119.7102 | 2.157% | 404 | 5535.9711 | 5431.2898 | 1.927% | 0.2767%
2017-05-13 | 9 | 5551 | 104.6813 | 1.886% | 15.0289 | 0.2707% | 119.7102 | 2.157% | 405 | 5535.9711 | 5431.2898 | 1.927% | 0.2767%
2017-05-06 | 9 | 5558 | 104.874 | 1.887% | 15.0389 | 0.2706% | 119.9129 | 2.157% | 406 | 5542.9611 | 5438.0871 | 1.929% | 0.2765%
2017-05-19 | 5 | 5559 | 104.9015 | 1.887% | 15.0404 | 0.2706% | 119.9419 | 2.158% | 407 | 5543.9596 | 5439.0581 | 1.929% | 0.2765%
2017-05-12 | 24 | 5560 | 104.929 | 1.887% | 15.0418 | 0.2705% | 119.9708 | 2.158% | 408 | 5544.9582 | 5440.0292 | 1.929% | 0.2765%
2017-05-05 | 24 | 5561 | 104.9566 | 1.887% | 15.0432 | 0.2705% | 119.9998 | 2.158% | 409 | 5545.9568 | 5441.0002 | 1.929% | 0.2765%
2017-03-21 | 2 | 5564 | 105.0391 | 1.888% | 15.0475 | 0.2704% | 120.0867 | 2.158% | 410 | 5548.9525 | 5443.9133 | 1.929% | 0.2764%
2017-04-09 | 5 | 5564 | 105.0391 | 1.888% | 15.0475 | 0.2704% | 120.0867 | 2.158% | 411 | 5548.9525 | 5443.9133 | 1.929% | 0.2764%
2017-05-20 | 7 | 5564 | 105.0391 | 1.888% | 15.0475 | 0.2704% | 120.0867 | 2.158% | 412 | 5548.9525 | 5443.9133 | 1.929% | 0.2764%
2017-03-30 | 24 | 5566 | 105.0942 | 1.888% | 15.0504 | 0.2704% | 120.1446 | 2.159% | 413 | 5550.9496 | 5445.8554 | 1.93% | 0.2764% | 5567.3234
2017-03-09 | 24 | 5571 | 105.1534 | 1.888% | 15.0599 | 0.2703% | 120.2133 | 2.158% | 414 | 5555.9401 | 5450.7867 | 1.929% | 0.2763%
2017-05-05 | 2 | 5572 | 105.157 | 1.887% | 15.062 | 0.2703% | 120.2191 | 2.158% | 415 | 5556.938 | 5451.7809 | 1.929% | 0.2763%
2017-03-29 | 24 | 5574 | 105.1644 | 1.887% | 15.0663 | 0.2703% | 120.2307 | 2.157% | 416 | 5558.9337 | 5453.7693 | 1.928% | 0.2763%
2017-05-25 | 6 | 5577 | 105.1754 | 1.886% | 15.0727 | 0.2703% | 120.2481 | 2.156% | 417 | 5561.9273 | 5456.7519 | 1.927% | 0.2762%
2017-04-08 | 17 | 5582 | 105.1937 | 1.885% | 15.0834 | 0.2702% | 120.2771 | 2.155% | 418 | 5566.9166 | 5461.7229 | 1.926% | 0.2762%
2017-05-17 | 3 | 5587 | 105.212 | 1.883% | 15.0941 | 0.2702% | 120.3061 | 2.153% | 419 | 5571.9059 | 5466.6939 | 1.925% | 0.2761%
2017-05-24 | 6 | 5588 | 105.2157 | 1.883% | 15.0963 | 0.2702% | 120.3119 | 2.153% | 420 | 5572.9037 | 5467.6881 | 1.924% | 0.2761%
2017-04-14 | 24 | 5590 | 105.223 | 1.882% | 15.1005 | 0.2701% | 120.3235 | 2.152% | 421 | 5574.8995 | 5469.6765 | 1.924% | 0.2761%
2017-05-21 | 3 | 5591 | 105.2266 | 1.882% | 15.1027 | 0.2701% | 120.3293 | 2.152% | 422 | 5575.8973 | 5470.6707 | 1.923% | 0.2761%
2017-05-25 | 2 | 5594 | 105.2376 | 1.881% | 15.1091 | 0.2701% | 120.3467 | 2.151% | 423 | 5578.8909 | 5473.6533 | 1.923% | 0.276%
2017-04-02 | 9 | 5595 | 105.2413 | 1.881% | 15.1112 | 0.2701% | 120.3525 | 2.151% | 424 | 5579.8888 | 5474.6475 | 1.922% | 0.276%
2017-05-29 | 3 | 5596 | 105.245 | 1.881% | 15.1134 | 0.2701% | 120.3583 | 2.151% | 425 | 5580.8866 | 5475.6417 | 1.922% | 0.276%
2017-04-03 | 24 | 5600 | 105.2596 | 1.88% | 15.1219 | 0.27% | 120.3816 | 2.15% | 426 | 5584.8781 | 5479.6184 | 1.921% | 0.276%
2017-04-27 | 1 | 5608 | 105.2889 | 1.877% | 15.1391 | 0.27% | 120.428 | 2.147% | 427 | 5592.8609 | 5487.572 | 1.919% | 0.2759%
2017-03-09 | 2 | 5610 | 105.2963 | 1.877% | 15.1433 | 0.2699% | 120.4396 | 2.147% | 428 | 5594.8567 | 5489.5604 | 1.918% | 0.2759%
2017-04-10 | 24 | 5611 | 105.2999 | 1.877% | 15.1455 | 0.2699% | 120.4454 | 2.147% | 429 | 5595.8545 | 5490.5546 | 1.918% | 0.2758%
2017-04-08 | 18 | 5612 | 105.3036 | 1.876% | 15.1476 | 0.2699% | 120.4512 | 2.146% | 430 | 5596.8524 | 5491.5488 | 1.918% | 0.2758%
2017-05-19 | 4 | 5612 | 105.3036 | 1.876% | 15.1476 | 0.2699% | 120.4512 | 2.146% | 431 | 5596.8524 | 5491.5488 | 1.918% | 0.2758%
2017-05-28 | 3 | 5620 | 105.3329 | 1.874% | 15.1647 | 0.2698% | 120.4976 | 2.144% | 432 | 5604.8353 | 5499.5024 | 1.915% | 0.2757%
2017-05-07 | 10 | 5621 | 105.3365 | 1.874% | 15.1669 | 0.2698% | 120.5034 | 2.144% | 433 | 5605.8331 | 5500.4966 | 1.915% | 0.2757%
2017-05-14 | 10 | 5623 | 105.3439 | 1.873% | 15.1712 | 0.2698% | 120.515 | 2.143% | 434 | 5607.8288 | 5502.485 | 1.914% | 0.2757%
2017-05-01 | 2 | 5624 | 105.3475 | 1.873% | 15.1733 | 0.2698% | 120.5208 | 2.143% | 435 | 5608.8267 | 5503.4792 | 1.914% | 0.2757%
2017-04-05 | 24 | 5631 | 105.3732 | 1.871% | 15.1883 | 0.2697% | 120.5615 | 2.141% | 436 | 5615.8117 | 5510.4385 | 1.912% | 0.2756%
2017-04-25 | 24 | 5632 | 105.3768 | 1.871% | 15.1904 | 0.2697% | 120.5673 | 2.141% | 437 | 5616.8096 | 5511.4327 | 1.912% | 0.2756%
2017-04-02 | 14 | 5633 | 105.3805 | 1.871% | 15.1926 | 0.2697% | 120.5731 | 2.14% | 438 | 5617.8074 | 5512.4269 | 1.912% | 0.2756%
2017-05-28 | 8 | 5634 | 105.3842 | 1.871% | 15.1947 | 0.2697% | 120.5789 | 2.14% | 439 | 5618.8053 | 5513.4211 | 1.911% | 0.2756%
2017-04-02 | 13 | 5635 | 105.3878 | 1.87% | 15.1968 | 0.2697% | 120.5847 | 2.14% | 440 | 5619.8032 | 5514.4153 | 1.911% | 0.2756%
2017-04-16 | 24 | 5636 | 105.3915 | 1.87% | 15.199 | 0.2697% | 120.5905 | 2.14% | 441 | 5620.801 | 5515.4095 | 1.911% | 0.2756%
2017-04-08 | 19 | 5638 | 105.3988 | 1.869% | 15.2033 | 0.2697% | 120.6021 | 2.139% | 442 | 5622.7967 | 5517.3979 | 1.91% | 0.2756%
2017-04-08 | 24 | 5642 | 105.4135 | 1.868% | 15.2118 | 0.2696% | 120.6253 | 2.138% | 443 | 5626.7882 | 5521.3747 | 1.909% | 0.2755%
2017-05-07 | 12 | 5643 | 105.4171 | 1.868% | 15.214 | 0.2696% | 120.6311 | 2.138% | 444 | 5627.786 | 5522.3689 | 1.909% | 0.2755%
2017-05-30 | 3 | 5646 | 105.4281 | 1.867% | 15.2204 | 0.2696% | 120.6485 | 2.137% | 445 | 5630.7796 | 5525.3515 | 1.908% | 0.2755%
2017-04-18 | 24 | 5648 | 105.4355 | 1.867% | 15.2247 | 0.2696% | 120.6601 | 2.136% | 446 | 5632.7753 | 5527.3399 | 1.908% | 0.2754%
2017-03-01 | 24 | 5653 | 105.4538 | 1.865% | 15.2354 | 0.2695% | 120.6891 | 2.135% | 447 | 5637.7646 | 5532.3109 | 1.906% | 0.2754%
2017-03-09 | 1 | 5654 | 105.4574 | 1.865% | 15.2375 | 0.2695% | 120.6949 | 2.135% | 448 | 5638.7625 | 5533.3051 | 1.906% | 0.2754%
2017-04-02 | 15 | 5657 | 105.4684 | 1.864% | 15.2439 | 0.2695% | 120.7123 | 2.134% | 449 | 5641.7561 | 5536.2877 | 1.905% | 0.2753%
2017-04-14 | 9 | 5663 | 105.4904 | 1.863% | 15.2568 | 0.2694% | 120.7472 | 2.132% | 450 | 5647.7432 | 5542.2528 | 1.903% | 0.2753%
2017-04-13 | 24 | 5665 | 105.4977 | 1.862% | 15.261 | 0.2694% | 120.7588 | 2.132% | 451 | 5649.739 | 5544.2412 | 1.903% | 0.2753%
2017-05-07 | 13 | 5665 | 105.4977 | 1.862% | 15.261 | 0.2694% | 120.7588 | 2.132% | 452 | 5649.739 | 5544.2412 | 1.903% | 0.2753%
2017-05-31 | 4 | 5669 | 105.5124 | 1.861% | 15.2696 | 0.2694% | 120.782 | 2.131% | 453 | 5653.7304 | 5548.218 | 1.902% | 0.2752%
2017-05-20 | 3 | 5670 | 105.5161 | 1.861% | 15.2717 | 0.2693% | 120.7878 | 2.13% | 454 | 5654.7283 | 5549.2122 | 1.901% | 0.2752%
2017-04-22 | 2 | 5672 | 105.5234 | 1.86% | 15.276 | 0.2693% | 120.7994 | 2.13% | 455 | 5656.724 | 5551.2006 | 1.901% | 0.2752%
2017-03-09 | 3 | 5675 | 105.5344 | 1.86% | 15.2824 | 0.2693% | 120.8168 | 2.129% | 456 | 5659.7176 | 5554.1832 | 1.9% | 0.2752%
2017-03-19 | 2 | 5675 | 105.5344 | 1.86% | 15.2824 | 0.2693% | 120.8168 | 2.129% | 457 | 5659.7176 | 5554.1832 | 1.9% | 0.2752%
2017-03-31 | 24 | 5675 | 105.5344 | 1.86% | 15.2824 | 0.2693% | 120.8168 | 2.129% | 458 | 5659.7176 | 5554.1832 | 1.9% | 0.2752%
2017-04-23 | 10 | 5679 | 105.549 | 1.859% | 15.291 | 0.2693% | 120.84 | 2.128% | 459 | 5663.709 | 5558.16 | 1.899% | 0.2751%
2017-04-02 | 12 | 5683 | 105.5637 | 1.858% | 15.2995 | 0.2692% | 120.8632 | 2.127% | 460 | 5667.7005 | 5562.1368 | 1.898% | 0.2751%
2017-04-24 | 24 | 5684 | 105.5673 | 1.857% | 15.3017 | 0.2692% | 120.869 | 2.126% | 461 | 5668.6983 | 5563.131 | 1.898% | 0.2751%
2017-03-26 | 9 | 5689 | 105.5857 | 1.856% | 15.3124 | 0.2692% | 120.8981 | 2.125% | 462 | 5673.6876 | 5568.1019 | 1.896% | 0.275%
2017-03-24 | 24 | 5690 | 105.5893 | 1.856% | 15.3145 | 0.2691% | 120.9039 | 2.125% | 463 | 5674.6855 | 5569.0961 | 1.896% | 0.275%
2017-05-27 | 1 | 5690 | 105.5893 | 1.856% | 15.3145 | 0.2691% | 120.9039 | 2.125% | 464 | 5674.6855 | 5569.0961 | 1.896% | 0.275%
2017-03-19 | 3 | 5692 | 105.5967 | 1.855% | 15.3188 | 0.2691% | 120.9155 | 2.124% | 465 | 5676.6812 | 5571.0845 | 1.895% | 0.275%
2017-04-09 | 14 | 5693 | 105.6003 | 1.855% | 15.3209 | 0.2691% | 120.9213 | 2.124% | 466 | 5677.6791 | 5572.0787 | 1.895% | 0.275%
2017-05-07 | 11 | 5694 | 105.604 | 1.855% | 15.3231 | 0.2691% | 120.9271 | 2.124% | 467 | 5678.6769 | 5573.0729 | 1.895% | 0.2749%
2017-04-01 | 9 | 5696 | 105.6113 | 1.854% | 15.3274 | 0.2691% | 120.9387 | 2.123% | 468 | 5680.6726 | 5575.0613 | 1.894% | 0.2749%
2017-05-17 | 6 | 5696 | 105.6113 | 1.854% | 15.3274 | 0.2691% | 120.9387 | 2.123% | 469 | 5680.6726 | 5575.0613 | 1.894% | 0.2749%
2017-03-21 | 1 | 5698 | 105.6186 | 1.854% | 15.3316 | 0.2691% | 120.9503 | 2.123% | 470 | 5682.6684 | 5577.0497 | 1.894% | 0.2749%
2017-05-07 | 14 | 5699 | 105.6223 | 1.853% | 15.3338 | 0.2691% | 120.9561 | 2.122% | 471 | 5683.6662 | 5578.0439 | 1.894% | 0.2749%
2017-04-28 | 2 | 5701 | 105.6296 | 1.853% | 15.3381 | 0.269% | 120.9677 | 2.122% | 472 | 5685.6619 | 5580.0323 | 1.893% | 0.2749%
2017-05-09 | 24 | 5701 | 105.6296 | 1.853% | 15.3381 | 0.269% | 120.9677 | 2.122% | 473 | 5685.6619 | 5580.0323 | 1.893% | 0.2749%
2017-04-06 | 24 | 5713 | 105.6736 | 1.85% | 15.3637 | 0.2689% | 121.0373 | 2.119% | 474 | 5697.6363 | 5591.9627 | 1.89% | 0.2747%
2017-04-09 | 15 | 5716 | 105.6846 | 1.849% | 15.3702 | 0.2689% | 121.0547 | 2.118% | 475 | 5700.6298 | 5594.9453 | 1.889% | 0.2747%
2017-04-02 | 11 | 5717 | 105.6882 | 1.849% | 15.3723 | 0.2689% | 121.0605 | 2.118% | 476 | 5701.6277 | 5595.9395 | 1.889% | 0.2747%
2017-05-26 | 7 | 5717 | 105.6882 | 1.849% | 15.3723 | 0.2689% | 121.0605 | 2.118% | 477 | 5701.6277 | 5595.9395 | 1.889% | 0.2747%
2017-03-21 | 5 | 5718 | 105.6919 | 1.848% | 15.3744 | 0.2689% | 121.0663 | 2.117% | 478 | 5702.6256 | 5596.9337 | 1.888% | 0.2747%
2017-05-23 | 2 | 5718 | 105.6919 | 1.848% | 15.3744 | 0.2689% | 121.0663 | 2.117% | 479 | 5702.6256 | 5596.9337 | 1.888% | 0.2747%
2017-05-07 | 15 | 5723 | 105.7102 | 1.847% | 15.3851 | 0.2688% | 121.0954 | 2.116% | 480 | 5707.6149 | 5601.9046 | 1.887% | 0.2746%
2017-05-31 | 5 | 5724 | 105.7139 | 1.847% | 15.3873 | 0.2688% | 121.1012 | 2.116% | 481 | 5708.6127 | 5602.8988 | 1.887% | 0.2746%
2017-04-30 | 3 | 5726 | 105.7212 | 1.846% | 15.3916 | 0.2688% | 121.1128 | 2.115% | 482 | 5710.6084 | 5604.8872 | 1.886% | 0.2746%
2017-05-24 | 1 | 5729 | 105.7322 | 1.846% | 15.398 | 0.2688% | 121.1302 | 2.114% | 483 | 5713.602 | 5607.8698 | 1.885% | 0.2746%
2017-03-21 | 24 | 5731 | 105.7395 | 1.845% | 15.4023 | 0.2688% | 121.1418 | 2.114% | 484 | 5715.5977 | 5609.8582 | 1.885% | 0.2746%
2017-04-09 | 13 | 5732 | 105.7432 | 1.845% | 15.4044 | 0.2687% | 121.1476 | 2.114% | 485 | 5716.5956 | 5610.8524 | 1.885% | 0.2745%
2017-05-02 | 3 | 5732 | 105.7432 | 1.845% | 15.4044 | 0.2687% | 121.1476 | 2.114% | 486 | 5716.5956 | 5610.8524 | 1.885% | 0.2745%
2017-05-18 | 3 | 5732 | 105.7432 | 1.845% | 15.4044 | 0.2687% | 121.1476 | 2.114% | 487 | 5716.5956 | 5610.8524 | 1.885% | 0.2745%
2017-03-07 | 2 | 5743 | 105.7835 | 1.842% | 15.4279 | 0.2686% | 121.2114 | 2.111% | 488 | 5727.5721 | 5621.7886 | 1.882% | 0.2744%
2017-04-02 | 10 | 5747 | 105.7981 | 1.841% | 15.4365 | 0.2686% | 121.2346 | 2.11% | 489 | 5731.5635 | 5625.7654 | 1.881% | 0.2744%
2017-04-02 | 16 | 5749 | 105.8055 | 1.84% | 15.4408 | 0.2686% | 121.2463 | 2.109% | 490 | 5733.5592 | 5627.7537 | 1.88% | 0.2744%
2017-05-02 | 6 | 5750 | 105.8091 | 1.84% | 15.4429 | 0.2686% | 121.2521 | 2.109% | 491 | 5734.5571 | 5628.7479 | 1.88% | 0.2744%
2017-05-07 | 23 | 5753 | 105.8201 | 1.839% | 15.4493 | 0.2685% | 121.2695 | 2.108% | 492 | 5737.5507 | 5631.7305 | 1.879% | 0.2743%
2017-03-19 | 1 | 5755 | 105.8275 | 1.839% | 15.4536 | 0.2685% | 121.2811 | 2.107% | 493 | 5739.5464 | 5633.7189 | 1.878% | 0.2743%
2017-05-05 | 6 | 5758 | 105.8384 | 1.838% | 15.46 | 0.2685% | 121.2985 | 2.107% | 494 | 5742.54 | 5636.7015 | 1.878% | 0.2743%
2017-04-08 | 20 | 5762 | 105.8531 | 1.837% | 15.4686 | 0.2685% | 121.3217 | 2.106% | 495 | 5746.5314 | 5640.6783 | 1.877% | 0.2742%
2017-05-29 | 8 | 5763 | 105.8568 | 1.837% | 15.4707 | 0.2684% | 121.3275 | 2.105% | 496 | 5747.5293 | 5641.6725 | 1.876% | 0.2742%
2017-05-06 | 23 | 5766 | 105.8678 | 1.836% | 15.4772 | 0.2684% | 121.3449 | 2.104% | 497 | 5750.5228 | 5644.6551 | 1.876% | 0.2742%
2017-05-06 | 16 | 5767 | 105.8714 | 1.836% | 15.4793 | 0.2684% | 121.3507 | 2.104% | 498 | 5751.5207 | 5645.6493 | 1.875% | 0.2742%
2017-05-15 | 7 | 5770 | 105.8824 | 1.835% | 15.4857 | 0.2684% | 121.3681 | 2.103% | 499 | 5754.5143 | 5648.6319 | 1.874% | 0.2741%
2017-04-08 | 16 | 5771 | 105.8861 | 1.835% | 15.4879 | 0.2684% | 121.3739 | 2.103% | 500 | 5755.5121 | 5649.6261 | 1.874% | 0.2741%
2017-04-02 | 23 | 5772 | 105.8897 | 1.835% | 15.49 | 0.2684% | 121.3797 | 2.103% | 501 | 5756.51 | 5650.6203 | 1.874% | 0.2741%
2017-04-09 | 23 | 5774 | 105.8971 | 1.834% | 15.4943 | 0.2683% | 121.3913 | 2.102% | 502 | 5758.5057 | 5652.6087 | 1.873% | 0.2741%
2017-05-19 | 3 | 5775 | 105.9007 | 1.834% | 15.4964 | 0.2683% | 121.3971 | 2.102% | 503 | 5759.5036 | 5653.6029 | 1.873% | 0.2741%
2017-04-29 | 6 | 5778 | 105.9117 | 1.833% | 15.5028 | 0.2683% | 121.4145 | 2.101% | 504 | 5762.4972 | 5656.5855 | 1.872% | 0.2741%
2017-05-22 | 6 | 5778 | 105.9117 | 1.833% | 15.5028 | 0.2683% | 121.4145 | 2.101% | 505 | 5762.4972 | 5656.5855 | 1.872% | 0.2741%
2017-04-19 | 24 | 5780 | 105.919 | 1.833% | 15.5071 | 0.2683% | 121.4262 | 2.101% | 506 | 5764.4929 | 5658.5738 | 1.872% | 0.274%
2017-04-09 | 12 | 5782 | 105.9264 | 1.832% | 15.5114 | 0.2683% | 121.4378 | 2.1% | 507 | 5766.4886 | 5660.5622 | 1.871% | 0.274%
2017-04-29 | 5 | 5785 | 105.9374 | 1.831% | 15.5178 | 0.2682% | 121.4552 | 2.099% | 508 | 5769.4822 | 5663.5448 | 1.871% | 0.274%
2017-04-12 | 7 | 5786 | 105.941 | 1.831% | 15.52 | 0.2682% | 121.461 | 2.099% | 509 | 5770.48 | 5664.539 | 1.87% | 0.274%
2017-04-09 | 16 | 5787 | 105.9447 | 1.831% | 15.5221 | 0.2682% | 121.4668 | 2.099% | 510 | 5771.4779 | 5665.5332 | 1.87% | 0.274%
2017-05-06 | 15 | 5788 | 105.9483 | 1.83% | 15.5242 | 0.2682% | 121.4726 | 2.099% | 511 | 5772.4758 | 5666.5274 | 1.87% | 0.274%
2017-03-07 | 3 | 5790 | 105.9557 | 1.83% | 15.5285 | 0.2682% | 121.4842 | 2.098% | 512 | 5774.4715 | 5668.5158 | 1.869% | 0.2739%
2017-05-23 | 6 | 5792 | 105.963 | 1.829% | 15.5328 | 0.2682% | 121.4958 | 2.098% | 513 | 5776.4672 | 5670.5042 | 1.869% | 0.2739%
2017-04-30 | 8 | 5793 | 105.9667 | 1.829% | 15.5349 | 0.2682% | 121.5016 | 2.097% | 514 | 5777.4651 | 5671.4984 | 1.868% | 0.2739%
2017-03-19 | 4 | 5797 | 105.9813 | 1.828% | 15.5435 | 0.2681% | 121.5248 | 2.096% | 515 | 5781.4565 | 5675.4752 | 1.867% | 0.2739%
2017-05-07 | 16 | 5800 | 105.9923 | 1.827% | 15.5499 | 0.2681% | 121.5422 | 2.096% | 516 | 5784.4501 | 5678.4578 | 1.867% | 0.2738%
2017-04-08 | 15 | 5804 | 106.007 | 1.826% | 15.5585 | 0.2681% | 121.5654 | 2.095% | 517 | 5788.4415 | 5682.4346 | 1.866% | 0.2738%
2017-03-07 | 4 | 5808 | 106.0216 | 1.825% | 15.567 | 0.268% | 121.5886 | 2.093% | 518 | 5792.433 | 5686.4114 | 1.864% | 0.2738%
2017-04-19 | 7 | 5810 | 106.0289 | 1.825% | 15.5713 | 0.268% | 121.6003 | 2.093% | 519 | 5794.4287 | 5688.3997 | 1.864% | 0.2737%
2017-05-03 | 7 | 5812 | 106.0363 | 1.824% | 15.5756 | 0.268% | 121.6119 | 2.092% | 520 | 5796.4244 | 5690.3881 | 1.863% | 0.2737%
2017-04-09 | 6 | 5813 | 106.0399 | 1.824% | 15.5777 | 0.268% | 121.6177 | 2.092% | 521 | 5797.4223 | 5691.3823 | 1.863% | 0.2737%
2017-04-23 | 23 | 5815 | 106.0473 | 1.824% | 15.582 | 0.268% | 121.6293 | 2.092% | 522 | 5799.418 | 5693.3707 | 1.863% | 0.2737%
2017-05-06 | 10 | 5816 | 106.0509 | 1.823% | 15.5841 | 0.268% | 121.6351 | 2.091% | 523 | 5800.4159 | 5694.3649 | 1.862% | 0.2737%
2017-05-06 | 14 | 5824 | 106.0802 | 1.821% | 15.6013 | 0.2679% | 121.6815 | 2.089% | 524 | 5808.3987 | 5702.3185 | 1.86% | 0.2736%
2017-05-04 | 7 | 5825 | 106.0839 | 1.821% | 15.6034 | 0.2679% | 121.6873 | 2.089% | 525 | 5809.3966 | 5703.3127 | 1.86% | 0.2736%
2017-04-13 | 7 | 5830 | 106.1022 | 1.82% | 15.6141 | 0.2678% | 121.7163 | 2.088% | 526 | 5814.3859 | 5708.2837 | 1.859% | 0.2735%
2017-04-23 | 11 | 5830 | 106.1022 | 1.82% | 15.6141 | 0.2678% | 121.7163 | 2.088% | 527 | 5814.3859 | 5708.2837 | 1.859% | 0.2735%
2017-03-25 | 8 | 5832 | 106.1095 | 1.819% | 15.6184 | 0.2678% | 121.7279 | 2.087% | 528 | 5816.3816 | 5710.2721 | 1.858% | 0.2735%
2017-05-06 | 17 | 5833 | 106.1132 | 1.819% | 15.6205 | 0.2678% | 121.7337 | 2.087% | 529 | 5817.3795 | 5711.2663 | 1.858% | 0.2735%
2017-05-14 | 24 | 5835 | 106.1205 | 1.819% | 15.6248 | 0.2678% | 121.7453 | 2.086% | 530 | 5819.3752 | 5713.2547 | 1.857% | 0.2735%
2017-05-12 | 1 | 5837 | 106.1279 | 1.818% | 15.6291 | 0.2678% | 121.7569 | 2.086% | 531 | 5821.3709 | 5715.2431 | 1.857% | 0.2735%
2017-05-13 | 10 | 5837 | 106.1279 | 1.818% | 15.6291 | 0.2678% | 121.7569 | 2.086% | 532 | 5821.3709 | 5715.2431 | 1.857% | 0.2735%
2017-05-31 | 3 | 5839 | 106.1352 | 1.818% | 15.6334 | 0.2677% | 121.7685 | 2.085% | 533 | 5823.3666 | 5717.2315 | 1.856% | 0.2734%
2017-04-01 | 23 | 5842 | 106.1462 | 1.817% | 15.6398 | 0.2677% | 121.786 | 2.085% | 534 | 5826.3602 | 5720.214 | 1.856% | 0.2734%
2017-05-25 | 24 | 5842 | 106.1462 | 1.817% | 15.6398 | 0.2677% | 121.786 | 2.085% | 535 | 5826.3602 | 5720.214 | 1.856% | 0.2734%
2017-03-08 | 24 | 5843 | 106.1498 | 1.817% | 15.6419 | 0.2677% | 121.7918 | 2.084% | 536 | 5827.3581 | 5721.2082 | 1.855% | 0.2734%
2017-04-15 | 24 | 5843 | 106.1498 | 1.817% | 15.6419 | 0.2677% | 121.7918 | 2.084% | 537 | 5827.3581 | 5721.2082 | 1.855% | 0.2734%
2017-03-09 | 4 | 5847 | 106.1645 | 1.816% | 15.6505 | 0.2677% | 121.815 | 2.083% | 538 | 5831.3495 | 5725.185 | 1.854% | 0.2734%
2017-05-14 | 11 | 5847 | 106.1645 | 1.816% | 15.6505 | 0.2677% | 121.815 | 2.083% | 539 | 5831.3495 | 5725.185 | 1.854% | 0.2734%
2017-04-28 | 6 | 5848 | 106.1682 | 1.815% | 15.6526 | 0.2677% | 121.8208 | 2.083% | 540 | 5832.3474 | 5726.1792 | 1.854% | 0.2734%
2017-05-27 | 9 | 5849 | 106.1718 | 1.815% | 15.6548 | 0.2676% | 121.8266 | 2.083% | 541 | 5833.3452 | 5727.1734 | 1.854% | 0.2733%
2017-04-15 | 10 | 5850 | 106.1755 | 1.815% | 15.6569 | 0.2676% | 121.8324 | 2.083% | 542 | 5834.3431 | 5728.1676 | 1.854% | 0.2733%
2017-04-29 | 4 | 5851 | 106.1791 | 1.815% | 15.659 | 0.2676% | 121.8382 | 2.082% | 543 | 5835.341 | 5729.1618 | 1.853% | 0.2733%
2017-04-08 | 2 | 5852 | 106.1828 | 1.814% | 15.6612 | 0.2676% | 121.844 | 2.082% | 544 | 5836.3388 | 5730.156 | 1.853% | 0.2733%
2017-05-22 | 1 | 5852 | 106.1828 | 1.814% | 15.6612 | 0.2676% | 121.844 | 2.082% | 545 | 5836.3388 | 5730.156 | 1.853% | 0.2733%
2017-04-11 | 7 | 5855 | 106.1938 | 1.814% | 15.6676 | 0.2676% | 121.8614 | 2.081% | 546 | 5839.3324 | 5733.1386 | 1.852% | 0.2733%
2017-04-04 | 24 | 5856 | 106.1975 | 1.813% | 15.6697 | 0.2676% | 121.8672 | 2.081% | 547 | 5840.3303 | 5734.1328 | 1.852% | 0.2733%
2017-05-25 | 1 | 5861 | 106.2158 | 1.812% | 15.6804 | 0.2675% | 121.8962 | 2.08% | 548 | 5845.3196 | 5739.1038 | 1.851% | 0.2732%
2017-03-07 | 1 | 5862 | 106.2194 | 1.812% | 15.6826 | 0.2675% | 121.902 | 2.08% | 549 | 5846.3174 | 5740.098 | 1.85% | 0.2732%
2017-04-20 | 7 | 5867 | 106.2378 | 1.811% | 15.6933 | 0.2675% | 121.931 | 2.078% | 550 | 5851.3067 | 5745.069 | 1.849% | 0.2732%
2017-04-17 | 8 | 5869 | 106.2451 | 1.81% | 15.6976 | 0.2675% | 121.9426 | 2.078% | 551 | 5853.3024 | 5747.0574 | 1.849% | 0.2731%
2017-05-13 | 20 | 5870 | 106.2488 | 1.81% | 15.6997 | 0.2675% | 121.9484 | 2.077% | 552 | 5854.3003 | 5748.0516 | 1.848% | 0.2731%
2017-05-30 | 6 | 5870 | 106.2488 | 1.81% | 15.6997 | 0.2675% | 121.9484 | 2.077% | 553 | 5854.3003 | 5748.0516 | 1.848% | 0.2731%
2017-05-17 | 2 | 5872 | 106.2561 | 1.81% | 15.704 | 0.2674% | 121.9601 | 2.077% | 554 | 5856.296 | 5750.0399 | 1.848% | 0.2731%
2017-05-01 | 6 | 5873 | 106.2597 | 1.809% | 15.7061 | 0.2674% | 121.9659 | 2.077% | 555 | 5857.2939 | 5751.0341 | 1.848% | 0.2731%
2017-04-08 | 3 | 5874 | 106.2634 | 1.809% | 15.7083 | 0.2674% | 121.9717 | 2.076% | 556 | 5858.2917 | 5752.0283 | 1.847% | 0.2731%
2017-04-11 | 24 | 5874 | 106.2634 | 1.809% | 15.7083 | 0.2674% | 121.9717 | 2.076% | 557 | 5858.2917 | 5752.0283 | 1.847% | 0.2731%
2017-05-06 | 13 | 5877 | 106.2744 | 1.808% | 15.7147 | 0.2674% | 121.9891 | 2.076% | 558 | 5861.2853 | 5755.0109 | 1.847% | 0.2731%
2017-03-10 | 6 | 5878 | 106.2781 | 1.808% | 15.7168 | 0.2674% | 121.9949 | 2.075% | 559 | 5862.2832 | 5756.0051 | 1.846% | 0.2731%
2017-04-23 | 12 | 5878 | 106.2781 | 1.808% | 15.7168 | 0.2674% | 121.9949 | 2.075% | 560 | 5862.2832 | 5756.0051 | 1.846% | 0.2731%
2017-05-05 | 1 | 5880 | 106.2854 | 1.808% | 15.7211 | 0.2674% | 122.0065 | 2.075% | 561 | 5864.2789 | 5757.9935 | 1.846% | 0.273%
2017-05-19 | 6 | 5883 | 106.2964 | 1.807% | 15.7275 | 0.2673% | 122.0239 | 2.074% | 562 | 5867.2725 | 5760.9761 | 1.845% | 0.273%
2017-05-18 | 6 | 5887 | 106.311 | 1.806% | 15.7361 | 0.2673% | 122.0471 | 2.073% | 563 | 5871.2639 | 5764.9529 | 1.844% | 0.273%
2017-05-06 | 18 | 5893 | 106.333 | 1.804% | 15.7489 | 0.2672% | 122.0819 | 2.072% | 564 | 5877.2511 | 5770.9181 | 1.843% | 0.2729%
2017-03-25 | 23 | 5894 | 106.3367 | 1.804% | 15.7511 | 0.2672% | 122.0877 | 2.071% | 565 | 5878.2489 | 5771.9123 | 1.842% | 0.2729%
2017-04-02 | 17 | 5895 | 106.3403 | 1.804% | 15.7532 | 0.2672% | 122.0935 | 2.071% | 566 | 5879.2468 | 5772.9065 | 1.842% | 0.2729%
2017-05-16 | 1 | 5899 | 106.355 | 1.803% | 15.7617 | 0.2672% | 122.1167 | 2.07% | 567 | 5883.2383 | 5776.8833 | 1.841% | 0.2728%
2017-04-21 | 1 | 5901 | 106.3623 | 1.802% | 15.766 | 0.2672% | 122.1283 | 2.07% | 568 | 5885.234 | 5778.8717 | 1.841% | 0.2728%
2017-04-01 | 10 | 5910 | 106.3953 | 1.8% | 15.7853 | 0.2671% | 122.1806 | 2.067% | 569 | 5894.2147 | 5787.8194 | 1.838% | 0.2727%
2017-05-30 | 2 | 5913 | 106.4063 | 1.8% | 15.7917 | 0.2671% | 122.198 | 2.067% | 570 | 5897.2083 | 5790.802 | 1.838% | 0.2727%
2017-04-08 | 23 | 5916 | 106.4173 | 1.799% | 15.7981 | 0.267% | 122.2154 | 2.066% | 571 | 5900.2019 | 5793.7846 | 1.837% | 0.2727%
2017-05-02 | 2 | 5918 | 106.4246 | 1.798% | 15.8024 | 0.267% | 122.227 | 2.065% | 572 | 5902.1976 | 5795.773 | 1.836% | 0.2727%
2017-03-18 | 3 | 5919 | 106.4283 | 1.798% | 15.8045 | 0.267% | 122.2328 | 2.065% | 573 | 5903.1955 | 5796.7672 | 1.836% | 0.2726%
2017-03-27 | 24 | 5919 | 106.4283 | 1.798% | 15.8045 | 0.267% | 122.2328 | 2.065% | 574 | 5903.1955 | 5796.7672 | 1.836% | 0.2726%
2017-04-01 | 13 | 5920 | 106.4319 | 1.798% | 15.8067 | 0.267% | 122.2386 | 2.065% | 575 | 5904.1933 | 5797.7614 | 1.836% | 0.2726%
2017-04-07 | 6 | 5921 | 106.4356 | 1.798% | 15.8088 | 0.267% | 122.2444 | 2.065% | 576 | 5905.1912 | 5798.7556 | 1.835% | 0.2726%
2017-04-12 | 24 | 5921 | 106.4356 | 1.798% | 15.8088 | 0.267% | 122.2444 | 2.065% | 577 | 5905.1912 | 5798.7556 | 1.835% | 0.2726%
2017-03-18 | 4 | 5922 | 106.4393 | 1.797% | 15.811 | 0.267% | 122.2502 | 2.064% | 578 | 5906.189 | 5799.7498 | 1.835% | 0.2726%
2017-03-26 | 12 | 5923 | 106.4429 | 1.797% | 15.8131 | 0.267% | 122.256 | 2.064% | 579 | 5907.1869 | 5800.744 | 1.835% | 0.2726%
2017-04-09 | 17 | 5927 | 106.4576 | 1.796% | 15.8217 | 0.2669% | 122.2792 | 2.063% | 580 | 5911.1783 | 5804.7208 | 1.834% | 0.2726%
2017-04-14 | 10 | 5927 | 106.4576 | 1.796% | 15.8217 | 0.2669% | 122.2792 | 2.063% | 581 | 5911.1783 | 5804.7208 | 1.834% | 0.2726%
2017-05-06 | 19 | 5927 | 106.4576 | 1.796% | 15.8217 | 0.2669% | 122.2792 | 2.063% | 582 | 5911.1783 | 5804.7208 | 1.834% | 0.2726%
2017-05-21 | 9 | 5927 | 106.4576 | 1.796% | 15.8217 | 0.2669% | 122.2792 | 2.063% | 583 | 5911.1783 | 5804.7208 | 1.834% | 0.2726%
2017-05-29 | 2 | 5929 | 106.4649 | 1.796% | 15.8259 | 0.2669% | 122.2908 | 2.063% | 584 | 5913.1741 | 5806.7092 | 1.833% | 0.2725%
2017-05-06 | 11 | 5931 | 106.4722 | 1.795% | 15.8302 | 0.2669% | 122.3024 | 2.062% | 585 | 5915.1698 | 5808.6976 | 1.833% | 0.2725%
2017-04-01 | 12 | 5932 | 106.4759 | 1.795% | 15.8324 | 0.2669% | 122.3083 | 2.062% | 586 | 5916.1676 | 5809.6917 | 1.833% | 0.2725%
2017-05-28 | 2 | 5932 | 106.4759 | 1.795% | 15.8324 | 0.2669% | 122.3083 | 2.062% | 587 | 5916.1676 | 5809.6917 | 1.833% | 0.2725%
2017-05-07 | 17 | 5933 | 106.4796 | 1.795% | 15.8345 | 0.2669% | 122.3141 | 2.062% | 588 | 5917.1655 | 5810.6859 | 1.832% | 0.2725%
2017-05-13 | 23 | 5936 | 106.4905 | 1.794% | 15.8409 | 0.2669% | 122.3315 | 2.061% | 589 | 5920.1591 | 5813.6685 | 1.832% | 0.2725%
2017-03-26 | 10 | 5938 | 106.4979 | 1.793% | 15.8452 | 0.2668% | 122.3431 | 2.06% | 590 | 5922.1548 | 5815.6569 | 1.831% | 0.2725%
2017-04-08 | 14 | 5938 | 106.4979 | 1.793% | 15.8452 | 0.2668% | 122.3431 | 2.06% | 591 | 5922.1548 | 5815.6569 | 1.831% | 0.2725%
2017-03-26 | 11 | 5939 | 106.5015 | 1.793% | 15.8473 | 0.2668% | 122.3489 | 2.06% | 592 | 5923.1527 | 5816.6511 | 1.831% | 0.2724%
2017-04-05 | 7 | 5940 | 106.5052 | 1.793% | 15.8495 | 0.2668% | 122.3547 | 2.06% | 593 | 5924.1505 | 5817.6453 | 1.831% | 0.2724%
2017-05-11 | 1 | 5945 | 106.5235 | 1.792% | 15.8602 | 0.2668% | 122.3837 | 2.059% | 594 | 5929.1398 | 5822.6163 | 1.829% | 0.2724%
2017-04-01 | 11 | 5946 | 106.5272 | 1.792% | 15.8623 | 0.2668% | 122.3895 | 2.058% | 595 | 5930.1377 | 5823.6105 | 1.829% | 0.2724%
2017-03-28 | 7 | 5953 | 106.5528 | 1.79% | 15.8773 | 0.2667% | 122.4301 | 2.057% | 596 | 5937.1227 | 5830.5699 | 1.827% | 0.2723%
2017-05-02 | 24 | 5953 | 106.5528 | 1.79% | 15.8773 | 0.2667% | 122.4301 | 2.057% | 597 | 5937.1227 | 5830.5699 | 1.827% | 0.2723%
2017-04-16 | 10 | 5954 | 106.5565 | 1.79% | 15.8794 | 0.2667% | 122.4359 | 2.056% | 598 | 5938.1206 | 5831.5641 | 1.827% | 0.2723%
2017-04-08 | 1 | 5959 | 106.5748 | 1.788% | 15.8901 | 0.2667% | 122.4649 | 2.055% | 599 | 5943.1099 | 5836.5351 | 1.826% | 0.2723%
2017-04-01 | 14 | 5961 | 106.5821 | 1.788% | 15.8944 | 0.2666% | 122.4765 | 2.055% | 600 | 5945.1056 | 5838.5235 | 1.825% | 0.2722%
2017-05-06 | 20 | 5962 | 106.5858 | 1.788% | 15.8966 | 0.2666% | 122.4824 | 2.054% | 601 | 5946.1034 | 5839.5176 | 1.825% | 0.2722%
2017-03-26 | 13 | 5963 | 106.5895 | 1.788% | 15.8987 | 0.2666% | 122.4882 | 2.054% | 602 | 5947.1013 | 5840.5118 | 1.825% | 0.2722%
2017-03-22 | 7 | 5964 | 106.5931 | 1.787% | 15.9008 | 0.2666% | 122.494 | 2.054% | 603 | 5948.0992 | 5841.506 | 1.825% | 0.2722%
2017-04-08 | 4 | 5968 | 106.6078 | 1.786% | 15.9094 | 0.2666% | 122.5172 | 2.053% | 604 | 5952.0906 | 5845.4828 | 1.824% | 0.2722%
2017-03-27 | 7 | 5969 | 106.6114 | 1.786% | 15.9115 | 0.2666% | 122.523 | 2.053% | 605 | 5953.0885 | 5846.477 | 1.824% | 0.2722%
2017-05-06 | 12 | 5969 | 106.6114 | 1.786% | 15.9115 | 0.2666% | 122.523 | 2.053% | 606 | 5953.0885 | 5846.477 | 1.824% | 0.2722%
2017-03-20 | 24 | 5970 | 106.6151 | 1.786% | 15.9137 | 0.2666% | 122.5288 | 2.052% | 607 | 5954.0863 | 5847.4712 | 1.823% | 0.2721%
2017-05-10 | 7 | 5972 | 106.6224 | 1.785% | 15.918 | 0.2665% | 122.5404 | 2.052% | 608 | 5956.082 | 5849.4596 | 1.823% | 0.2721%
2017-05-14 | 12 | 5973 | 106.6261 | 1.785% | 15.9201 | 0.2665% | 122.5462 | 2.052% | 609 | 5957.0799 | 5850.4538 | 1.823% | 0.2721%
2017-05-21 | 2 | 5973 | 106.6261 | 1.785% | 15.9201 | 0.2665% | 122.5462 | 2.052% | 610 | 5957.0799 | 5850.4538 | 1.823% | 0.2721%
2017-05-20 | 2 | 5975 | 106.6334 | 1.785% | 15.9244 | 0.2665% | 122.5578 | 2.051% | 611 | 5959.0756 | 5852.4422 | 1.822% | 0.2721%
2017-03-19 | 5 | 5976 | 106.6371 | 1.784% | 15.9265 | 0.2665% | 122.5636 | 2.051% | 612 | 5960.0735 | 5853.4364 | 1.822% | 0.2721%
2017-03-25 | 15 | 5976 | 106.6371 | 1.784% | 15.9265 | 0.2665% | 122.5636 | 2.051% | 613 | 5960.0735 | 5853.4364 | 1.822% | 0.2721%
2017-04-23 | 16 | 5977 | 106.6407 | 1.784% | 15.9287 | 0.2665% | 122.5694 | 2.051% | 614 | 5961.0713 | 5854.4306 | 1.822% | 0.2721%
2017-04-23 | 13 | 5978 | 106.6444 | 1.784% | 15.9308 | 0.2665% | 122.5752 | 2.05% | 615 | 5962.0692 | 5855.4248 | 1.821% | 0.2721%
2017-03-26 | 23 | 5983 | 106.6627 | 1.783% | 15.9415 | 0.2664% | 122.6042 | 2.049% | 616 | 5967.0585 | 5860.3958 | 1.82% | 0.272%
2017-04-29 | 7 | 5983 | 106.6627 | 1.783% | 15.9415 | 0.2664% | 122.6042 | 2.049% | 617 | 5967.0585 | 5860.3958 | 1.82% | 0.272%
2017-03-25 | 16 | 5986 | 106.6737 | 1.782% | 15.9479 | 0.2664% | 122.6216 | 2.048% | 618 | 5970.0521 | 5863.3784 | 1.819% | 0.272%
2017-04-18 | 7 | 5989 | 106.6847 | 1.781% | 15.9543 | 0.2664% | 122.639 | 2.048% | 619 | 5973.0457 | 5866.361 | 1.819% | 0.272%
2017-04-23 | 15 | 5989 | 106.6847 | 1.781% | 15.9543 | 0.2664% | 122.639 | 2.048% | 620 | 5973.0457 | 5866.361 | 1.819% | 0.272%
2017-04-22 | 24 | 5995 | 106.7067 | 1.78% | 15.9672 | 0.2663% | 122.6739 | 2.046% | 621 | 5979.0328 | 5872.3261 | 1.817% | 0.2719%
2017-05-09 | 7 | 5996 | 106.7104 | 1.78% | 15.9693 | 0.2663% | 122.6797 | 2.046% | 622 | 5980.0307 | 5873.3203 | 1.817% | 0.2719%
2017-03-26 | 15 | 5997 | 106.714 | 1.779% | 15.9715 | 0.2663% | 122.6855 | 2.046% | 623 | 5981.0285 | 5874.3145 | 1.817% | 0.2719%
2017-05-12 | 7 | 5997 | 106.714 | 1.779% | 15.9715 | 0.2663% | 122.6855 | 2.046% | 624 | 5981.0285 | 5874.3145 | 1.817% | 0.2719%
2017-04-23 | 14 | 5998 | 106.7177 | 1.779% | 15.9736 | 0.2663% | 122.6913 | 2.046% | 625 | 5982.0264 | 5875.3087 | 1.816% | 0.2719%
2017-05-20 | 8 | 6001 | 106.7287 | 1.779% | 15.98 | 0.2663% | 122.7087 | 2.045% | 626 | 5985.02 | 5878.2913 | 1.816% | 0.2718%
2017-04-17 | 24 | 6003 | 106.736 | 1.778% | 15.9843 | 0.2663% | 122.7203 | 2.044% | 627 | 5987.0157 | 5880.2797 | 1.815% | 0.2718%
2017-03-18 | 5 | 6005 | 106.7433 | 1.778% | 15.9886 | 0.2663% | 122.7319 | 2.044% | 628 | 5989.0114 | 5882.2681 | 1.815% | 0.2718%
2017-05-13 | 11 | 6005 | 106.7433 | 1.778% | 15.9886 | 0.2663% | 122.7319 | 2.044% | 629 | 5989.0114 | 5882.2681 | 1.815% | 0.2718%
2017-04-26 | 7 | 6006 | 106.747 | 1.777% | 15.9907 | 0.2662% | 122.7377 | 2.044% | 630 | 5990.0093 | 5883.2623 | 1.814% | 0.2718%
2017-03-28 | 24 | 6007 | 106.7506 | 1.777% | 15.9928 | 0.2662% | 122.7435 | 2.043% | 631 | 5991.0072 | 5884.2565 | 1.814% | 0.2718%
2017-05-01 | 1 | 6007 | 106.7506 | 1.777% | 15.9928 | 0.2662% | 122.7435 | 2.043% | 632 | 5991.0072 | 5884.2565 | 1.814% | 0.2718%
2017-04-28 | 1 | 6009 | 106.758 | 1.777% | 15.9971 | 0.2662% | 122.7551 | 2.043% | 633 | 5993.0029 | 5886.2449 | 1.814% | 0.2718%
2017-03-26 | 14 | 6010 | 106.7616 | 1.776% | 15.9993 | 0.2662% | 122.7609 | 2.043% | 634 | 5994.0007 | 5887.2391 | 1.813% | 0.2718%
2017-05-13 | 13 | 6015 | 106.78 | 1.775% | 16.01 | 0.2662% | 122.7899 | 2.041% | 635 | 5998.99 | 5892.2101 | 1.812% | 0.2717%
2017-03-07 | 23 | 6017 | 106.7873 | 1.775% | 16.0142 | 0.2662% | 122.8015 | 2.041% | 636 | 6000.9858 | 5894.1985 | 1.812% | 0.2717%
2017-05-16 | 7 | 6017 | 106.7873 | 1.775% | 16.0142 | 0.2662% | 122.8015 | 2.041% | 637 | 6000.9858 | 5894.1985 | 1.812% | 0.2717%
2017-04-23 | 17 | 6019 | 106.7946 | 1.774% | 16.0185 | 0.2661% | 122.8131 | 2.04% | 638 | 6002.9815 | 5896.1869 | 1.811% | 0.2717%
2017-05-13 | 14 | 6025 | 106.8166 | 1.773% | 16.0314 | 0.2661% | 122.848 | 2.039% | 639 | 6008.9686 | 5902.152 | 1.81% | 0.2716%
2017-03-29 | 7 | 6028 | 106.8276 | 1.772% | 16.0378 | 0.2661% | 122.8654 | 2.038% | 640 | 6011.9622 | 5905.1346 | 1.809% | 0.2716%
2017-04-01 | 15 | 6029 | 106.8312 | 1.772% | 16.0399 | 0.266% | 122.8712 | 2.038% | 641 | 6012.9601 | 5906.1288 | 1.809% | 0.2716%
2017-05-26 | 8 | 6029 | 106.8312 | 1.772% | 16.0399 | 0.266% | 122.8712 | 2.038% | 642 | 6012.9601 | 5906.1288 | 1.809% | 0.2716%
2017-04-02 | 18 | 6030 | 106.8349 | 1.772% | 16.0421 | 0.266% | 122.877 | 2.038% | 643 | 6013.9579 | 5907.123 | 1.809% | 0.2716%
2017-03-05 | 16 | 6033 | 106.8459 | 1.771% | 16.0485 | 0.266% | 122.8944 | 2.037% | 644 | 6016.9515 | 5910.1056 | 1.808% | 0.2715%
2017-04-09 | 11 | 6036 | 106.8569 | 1.77% | 16.0549 | 0.266% | 122.9118 | 2.036% | 645 | 6019.9451 | 5913.0882 | 1.807% | 0.2715%
2017-04-14 | 11 | 6039 | 106.8679 | 1.77% | 16.0613 | 0.266% | 122.9292 | 2.036% | 646 | 6022.9387 | 5916.0708 | 1.806% | 0.2715%
2017-05-03 | 24 | 6039 | 106.8679 | 1.77% | 16.0613 | 0.266% | 122.9292 | 2.036% | 647 | 6022.9387 | 5916.0708 | 1.806% | 0.2715%
2017-03-25 | 19 | 6041 | 106.8752 | 1.769% | 16.0656 | 0.2659% | 122.9408 | 2.035% | 648 | 6024.9344 | 5918.0592 | 1.806% | 0.2715%
2017-03-31 | 7 | 6041 | 106.8752 | 1.769% | 16.0656 | 0.2659% | 122.9408 | 2.035% | 649 | 6024.9344 | 5918.0592 | 1.806% | 0.2715%
2017-04-21 | 7 | 6043 | 106.8825 | 1.769% | 16.0699 | 0.2659% | 122.9524 | 2.035% | 650 | 6026.9301 | 5920.0476 | 1.805% | 0.2714%
2017-04-29 | 3 | 6043 | 106.8825 | 1.769% | 16.0699 | 0.2659% | 122.9524 | 2.035% | 651 | 6026.9301 | 5920.0476 | 1.805% | 0.2714%
2017-05-18 | 2 | 6043 | 106.8825 | 1.769% | 16.0699 | 0.2659% | 122.9524 | 2.035% | 652 | 6026.9301 | 5920.0476 | 1.805% | 0.2714%
2017-03-24 | 17 | 6047 | 106.8972 | 1.768% | 16.0784 | 0.2659% | 122.9756 | 2.034% | 653 | 6030.9216 | 5924.0244 | 1.804% | 0.2714%
2017-03-25 | 14 | 6047 | 106.8972 | 1.768% | 16.0784 | 0.2659% | 122.9756 | 2.034% | 654 | 6030.9216 | 5924.0244 | 1.804% | 0.2714%
2017-04-27 | 7 | 6047 | 106.8972 | 1.768% | 16.0784 | 0.2659% | 122.9756 | 2.034% | 655 | 6030.9216 | 5924.0244 | 1.804% | 0.2714%
2017-04-22 | 9 | 6050 | 106.9082 | 1.767% | 16.0849 | 0.2659% | 122.993 | 2.033% | 656 | 6033.9151 | 5927.007 | 1.804% | 0.2714%
2017-03-24 | 23 | 6053 | 106.9192 | 1.766% | 16.0913 | 0.2658% | 123.0104 | 2.032% | 657 | 6036.9087 | 5929.9896 | 1.803% | 0.2714%
2017-03-25 | 17 | 6053 | 106.9192 | 1.766% | 16.0913 | 0.2658% | 123.0104 | 2.032% | 658 | 6036.9087 | 5929.9896 | 1.803% | 0.2714%
2017-04-30 | 2 | 6053 | 106.9192 | 1.766% | 16.0913 | 0.2658% | 123.0104 | 2.032% | 659 | 6036.9087 | 5929.9896 | 1.803% | 0.2714%
2017-03-18 | 2 | 6058 | 106.9375 | 1.765% | 16.102 | 0.2658% | 123.0395 | 2.031% | 660 | 6041.898 | 5934.9605 | 1.802% | 0.2713%
2017-05-19 | 2 | 6058 | 106.9375 | 1.765% | 16.102 | 0.2658% | 123.0395 | 2.031% | 661 | 6041.898 | 5934.9605 | 1.802% | 0.2713%
2017-05-13 | 12 | 6060 | 106.9448 | 1.765% | 16.1063 | 0.2658% | 123.0511 | 2.031% | 662 | 6043.8937 | 5936.9489 | 1.801% | 0.2713%
2017-03-09 | 23 | 6066 | 106.9668 | 1.763% | 16.1191 | 0.2657% | 123.0859 | 2.029% | 663 | 6049.8809 | 5942.9141 | 1.8% | 0.2712%
2017-03-07 | 5 | 6071 | 106.9851 | 1.762% | 16.1298 | 0.2657% | 123.1149 | 2.028% | 664 | 6054.8702 | 5947.8851 | 1.799% | 0.2712%
2017-03-18 | 18 | 6073 | 106.9924 | 1.762% | 16.1341 | 0.2657% | 123.1265 | 2.027% | 665 | 6056.8659 | 5949.8735 | 1.798% | 0.2712%
2017-04-24 | 7 | 6073 | 106.9924 | 1.762% | 16.1341 | 0.2657% | 123.1265 | 2.027% | 666 | 6056.8659 | 5949.8735 | 1.798% | 0.2712%
2017-05-13 | 15 | 6073 | 106.9924 | 1.762% | 16.1341 | 0.2657% | 123.1265 | 2.027% | 667 | 6056.8659 | 5949.8735 | 1.798% | 0.2712%
2017-03-06 | 24 | 6077 | 107.0071 | 1.761% | 16.1426 | 0.2656% | 123.1497 | 2.026% | 668 | 6060.8574 | 5953.8503 | 1.797% | 0.2711%
2017-03-18 | 24 | 6077 | 107.0071 | 1.761% | 16.1426 | 0.2656% | 123.1497 | 2.026% | 669 | 6060.8574 | 5953.8503 | 1.797% | 0.2711%
2017-05-08 | 7 | 6080 | 107.0181 | 1.76% | 16.1491 | 0.2656% | 123.1671 | 2.026% | 670 | 6063.8509 | 5956.8329 | 1.797% | 0.2711%
2017-03-23 | 1 | 6083 | 107.0291 | 1.759% | 16.1555 | 0.2656% | 123.1845 | 2.025% | 671 | 6066.8445 | 5959.8155 | 1.796% | 0.2711%
2017-04-04 | 7 | 6086 | 107.0401 | 1.759% | 16.1619 | 0.2656% | 123.202 | 2.024% | 672 | 6069.8381 | 5962.798 | 1.795% | 0.271%
2017-03-25 | 18 | 6091 | 107.0584 | 1.758% | 16.1726 | 0.2655% | 123.231 | 2.023% | 673 | 6074.8274 | 5967.769 | 1.794% | 0.271%
2017-04-08 | 22 | 6091 | 107.0584 | 1.758% | 16.1726 | 0.2655% | 123.231 | 2.023% | 674 | 6074.8274 | 5967.769 | 1.794% | 0.271%
2017-04-22 | 1 | 6094 | 107.0694 | 1.757% | 16.179 | 0.2655% | 123.2484 | 2.022% | 675 | 6077.821 | 5970.7516 | 1.793% | 0.271%
2017-03-25 | 13 | 6095 | 107.073 | 1.757% | 16.1812 | 0.2655% | 123.2542 | 2.022% | 676 | 6078.8188 | 5971.7458 | 1.793% | 0.271%
2017-05-31 | 2 | 6095 | 107.073 | 1.757% | 16.1812 | 0.2655% | 123.2542 | 2.022% | 677 | 6078.8188 | 5971.7458 | 1.793% | 0.271%
2017-05-23 | 1 | 6096 | 107.0767 | 1.757% | 16.1833 | 0.2655% | 123.26 | 2.022% | 678 | 6079.8167 | 5972.74 | 1.793% | 0.271%
2017-05-31 | 6 | 6098 | 107.084 | 1.756% | 16.1876 | 0.2655% | 123.2716 | 2.022% | 679 | 6081.8124 | 5974.7284 | 1.792% | 0.2709%
2017-05-25 | 7 | 6099 | 107.0877 | 1.756% | 16.1897 | 0.2654% | 123.2774 | 2.021% | 680 | 6082.8103 | 5975.7226 | 1.792% | 0.2709%
2017-04-12 | 8 | 6101 | 107.095 | 1.755% | 16.194 | 0.2654% | 123.289 | 2.021% | 681 | 6084.806 | 5977.711 | 1.792% | 0.2709%
2017-05-06 | 22 | 6101 | 107.095 | 1.755% | 16.194 | 0.2654% | 123.289 | 2.021% | 682 | 6084.806 | 5977.711 | 1.792% | 0.2709%
2017-04-19 | 8 | 6102 | 107.0987 | 1.755% | 16.1961 | 0.2654% | 123.2948 | 2.021% | 683 | 6085.8039 | 5978.7052 | 1.791% | 0.2709%
2017-03-05 | 17 | 6104 | 107.106 | 1.755% | 16.2004 | 0.2654% | 123.3064 | 2.02% | 684 | 6087.7996 | 5980.6936 | 1.791% | 0.2709%
2017-04-06 | 7 | 6104 | 107.106 | 1.755% | 16.2004 | 0.2654% | 123.3064 | 2.02% | 685 | 6087.7996 | 5980.6936 | 1.791% | 0.2709%
2017-05-14 | 13 | 6106 | 107.1133 | 1.754% | 16.2047 | 0.2654% | 123.318 | 2.02% | 686 | 6089.7953 | 5982.682 | 1.79% | 0.2709%
2017-04-09 | 18 | 6108 | 107.1207 | 1.754% | 16.209 | 0.2654% | 123.3296 | 2.019% | 687 | 6091.791 | 5984.6704 | 1.79% | 0.2708%
2017-05-07 | 18 | 6108 | 107.1207 | 1.754% | 16.209 | 0.2654% | 123.3296 | 2.019% | 688 | 6091.791 | 5984.6704 | 1.79% | 0.2708%
2017-03-26 | 16 | 6110 | 107.128 | 1.753% | 16.2133 | 0.2654% | 123.3412 | 2.019% | 689 | 6093.7867 | 5986.6588 | 1.789% | 0.2708%
2017-03-23 | 2 | 6113 | 107.139 | 1.753% | 16.2197 | 0.2653% | 123.3586 | 2.018% | 690 | 6096.7803 | 5989.6414 | 1.789% | 0.2708%
2017-04-03 | 23 | 6118 | 107.1573 | 1.752% | 16.2304 | 0.2653% | 123.3877 | 2.017% | 691 | 6101.7696 | 5994.6123 | 1.788% | 0.2707%
2017-04-13 | 8 | 6121 | 107.1683 | 1.751% | 16.2368 | 0.2653% | 123.4051 | 2.016% | 692 | 6104.7632 | 5997.5949 | 1.787% | 0.2707%
2017-05-05 | 23 | 6122 | 107.1719 | 1.751% | 16.2389 | 0.2653% | 123.4109 | 2.016% | 693 | 6105.7611 | 5998.5891 | 1.787% | 0.2707%
2017-03-18 | 17 | 6127 | 107.1903 | 1.749% | 16.2496 | 0.2652% | 123.4399 | 2.015% | 694 | 6110.7504 | 6003.5601 | 1.785% | 0.2707%
2017-03-30 | 23 | 6130 | 107.2013 | 1.749% | 16.256 | 0.2652% | 123.4573 | 2.014% | 695 | 6113.744 | 6006.5427 | 1.785% | 0.2706%
2017-03-30 | 7 | 6133 | 107.2122 | 1.748% | 16.2625 | 0.2652% | 123.4747 | 2.013% | 696 | 6116.7375 | 6009.5253 | 1.784% | 0.2706%
2017-05-08 | 23 | 6133 | 107.2122 | 1.748% | 16.2625 | 0.2652% | 123.4747 | 2.013% | 697 | 6116.7375 | 6009.5253 | 1.784% | 0.2706%
2017-03-25 | 9 | 6140 | 107.2379 | 1.747% | 16.2774 | 0.2651% | 123.5153 | 2.012% | 698 | 6123.7226 | 6016.4847 | 1.782% | 0.2705%
2017-03-28 | 8 | 6142 | 107.2452 | 1.746% | 16.2817 | 0.2651% | 123.5269 | 2.011% | 699 | 6125.7183 | 6018.4731 | 1.782% | 0.2705%
2017-05-24 | 7 | 6143 | 107.2489 | 1.746% | 16.2839 | 0.2651% | 123.5327 | 2.011% | 700 | 6126.7161 | 6019.4673 | 1.782% | 0.2705%
2017-03-24 | 19 | 6145 | 107.2562 | 1.745% | 16.2881 | 0.2651% | 123.5444 | 2.01% | 701 | 6128.7119 | 6021.4556 | 1.781% | 0.2705%
2017-05-13 | 19 | 6145 | 107.2562 | 1.745% | 16.2881 | 0.2651% | 123.5444 | 2.01% | 702 | 6128.7119 | 6021.4556 | 1.781% | 0.2705%
2017-05-13 | 16 | 6147 | 107.2635 | 1.745% | 16.2924 | 0.265% | 123.556 | 2.01% | 703 | 6130.7076 | 6023.444 | 1.781% | 0.2705%
2017-04-17 | 9 | 6148 | 107.2672 | 1.745% | 16.2946 | 0.265% | 123.5618 | 2.01% | 704 | 6131.7054 | 6024.4382 | 1.781% | 0.2705%
2017-03-05 | 15 | 6156 | 107.2965 | 1.743% | 16.3117 | 0.265% | 123.6082 | 2.008% | 705 | 6139.6883 | 6032.3918 | 1.779% | 0.2704%
2017-05-12 | 23 | 6156 | 107.2965 | 1.743% | 16.3117 | 0.265% | 123.6082 | 2.008% | 706 | 6139.6883 | 6032.3918 | 1.779% | 0.2704%
2017-04-01 | 16 | 6162 | 107.3185 | 1.742% | 16.3245 | 0.2649% | 123.643 | 2.007% | 707 | 6145.6755 | 6038.357 | 1.777% | 0.2703%
2017-03-02 | 7 | 6163 | 107.3222 | 1.741% | 16.3267 | 0.2649% | 123.6488 | 2.006% | 708 | 6146.6733 | 6039.3512 | 1.777% | 0.2703%
2017-04-08 | 5 | 6163 | 107.3222 | 1.741% | 16.3267 | 0.2649% | 123.6488 | 2.006% | 709 | 6146.6733 | 6039.3512 | 1.777% | 0.2703%
2017-03-25 | 12 | 6165 | 107.3295 | 1.741% | 16.3309 | 0.2649% | 123.6604 | 2.006% | 710 | 6148.6691 | 6041.3396 | 1.777% | 0.2703%
2017-04-07 | 16 | 6165 | 107.3295 | 1.741% | 16.3309 | 0.2649% | 123.6604 | 2.006% | 711 | 6148.6691 | 6041.3396 | 1.777% | 0.2703%
2017-04-07 | 18 | 6165 | 107.3295 | 1.741% | 16.3309 | 0.2649% | 123.6604 | 2.006% | 712 | 6148.6691 | 6041.3396 | 1.777% | 0.2703%
2017-04-07 | 17 | 6167 | 107.3368 | 1.741% | 16.3352 | 0.2649% | 123.672 | 2.005% | 713 | 6150.6648 | 6043.328 | 1.776% | 0.2703%
2017-04-15 | 11 | 6167 | 107.3368 | 1.741% | 16.3352 | 0.2649% | 123.672 | 2.005% | 714 | 6150.6648 | 6043.328 | 1.776% | 0.2703%
2017-03-04 | 16 | 6170 | 107.3478 | 1.74% | 16.3416 | 0.2649% | 123.6894 | 2.005% | 715 | 6153.6584 | 6046.3106 | 1.775% | 0.2703%
2017-04-02 | 19 | 6171 | 107.3515 | 1.74% | 16.3438 | 0.2648% | 123.6952 | 2.004% | 716 | 6154.6562 | 6047.3048 | 1.775% | 0.2703%
2017-04-09 | 7 | 6172 | 107.3551 | 1.739% | 16.3459 | 0.2648% | 123.701 | 2.004% | 717 | 6155.6541 | 6048.299 | 1.775% | 0.2703%
2017-04-23 | 18 | 6172 | 107.3551 | 1.739% | 16.3459 | 0.2648% | 123.701 | 2.004% | 718 | 6155.6541 | 6048.299 | 1.775% | 0.2703%
2017-05-23 | 24 | 6172 | 107.3551 | 1.739% | 16.3459 | 0.2648% | 123.701 | 2.004% | 719 | 6155.6541 | 6048.299 | 1.775% | 0.2703%
2017-05-11 | 7 | 6173 | 107.3588 | 1.739% | 16.3481 | 0.2648% | 123.7068 | 2.004% | 720 | 6156.6519 | 6049.2932 | 1.775% | 0.2702%
2017-03-25 | 20 | 6174 | 107.3624 | 1.739% | 16.3502 | 0.2648% | 123.7126 | 2.004% | 721 | 6157.6498 | 6050.2874 | 1.775% | 0.2702%
2017-03-25 | 22 | 6174 | 107.3624 | 1.739% | 16.3502 | 0.2648% | 123.7126 | 2.004% | 722 | 6157.6498 | 6050.2874 | 1.775% | 0.2702%
2017-05-07 | 19 | 6174 | 107.3624 | 1.739% | 16.3502 | 0.2648% | 123.7126 | 2.004% | 723 | 6157.6498 | 6050.2874 | 1.775% | 0.2702%
2017-04-05 | 23 | 6176 | 107.3698 | 1.739% | 16.3545 | 0.2648% | 123.7243 | 2.003% | 724 | 6159.6455 | 6052.2757 | 1.774% | 0.2702%
2017-03-29 | 23 | 6177 | 107.3734 | 1.738% | 16.3566 | 0.2648% | 123.7301 | 2.003% | 725 | 6160.6434 | 6053.2699 | 1.774% | 0.2702%
2017-04-11 | 8 | 6180 | 107.3844 | 1.738% | 16.363 | 0.2648% | 123.7475 | 2.002% | 726 | 6163.637 | 6056.2525 | 1.773% | 0.2702%
2017-04-14 | 12 | 6180 | 107.3844 | 1.738% | 16.363 | 0.2648% | 123.7475 | 2.002% | 727 | 6163.637 | 6056.2525 | 1.773% | 0.2702%
2017-05-07 | 20 | 6180 | 107.3844 | 1.738% | 16.363 | 0.2648% | 123.7475 | 2.002% | 728 | 6163.637 | 6056.2525 | 1.773% | 0.2702%
2017-03-04 | 17 | 6181 | 107.3881 | 1.737% | 16.3652 | 0.2648% | 123.7533 | 2.002% | 729 | 6164.6348 | 6057.2467 | 1.773% | 0.2702%
2017-04-20 | 8 | 6183 | 107.3954 | 1.737% | 16.3695 | 0.2647% | 123.7649 | 2.002% | 730 | 6166.6305 | 6059.2351 | 1.772% | 0.2702%
2017-03-09 | 5 | 6185 | 107.4027 | 1.737% | 16.3737 | 0.2647% | 123.7765 | 2.001% | 731 | 6168.6263 | 6061.2235 | 1.772% | 0.2701%
2017-04-09 | 19 | 6187 | 107.4101 | 1.736% | 16.378 | 0.2647% | 123.7881 | 2.001% | 732 | 6170.622 | 6063.2119 | 1.772% | 0.2701%
2017-04-16 | 11 | 6188 | 107.4137 | 1.736% | 16.3802 | 0.2647% | 123.7939 | 2.001% | 733 | 6171.6198 | 6064.2061 | 1.771% | 0.2701%
2017-04-08 | 21 | 6189 | 107.4174 | 1.736% | 16.3823 | 0.2647% | 123.7997 | 2% | 734 | 6172.6177 | 6065.2003 | 1.771% | 0.2701%
2017-04-26 | 24 | 6192 | 107.4284 | 1.735% | 16.3887 | 0.2647% | 123.8171 | 2% | 735 | 6175.6113 | 6068.1829 | 1.77% | 0.2701%
2017-04-25 | 7 | 6195 | 107.4394 | 1.734% | 16.3951 | 0.2647% | 123.8345 | 1.999% | 736 | 6178.6049 | 6071.1655 | 1.77% | 0.27%
2017-04-10 | 7 | 6201 | 107.4614 | 1.733% | 16.408 | 0.2646% | 123.8693 | 1.998% | 737 | 6184.592 | 6077.1307 | 1.768% | 0.27%
2017-05-13 | 22 | 6202 | 107.465 | 1.733% | 16.4101 | 0.2646% | 123.8751 | 1.997% | 738 | 6185.5899 | 6078.1249 | 1.768% | 0.27%
2017-03-01 | 23 | 6204 | 107.4724 | 1.732% | 16.4144 | 0.2646% | 123.8867 | 1.997% | 739 | 6187.5856 | 6080.1133 | 1.768% | 0.27%
2017-04-24 | 23 | 6204 | 107.4724 | 1.732% | 16.4144 | 0.2646% | 123.8867 | 1.997% | 740 | 6187.5856 | 6080.1133 | 1.768% | 0.27%
2017-03-18 | 6 | 6205 | 107.476 | 1.732% | 16.4165 | 0.2646% | 123.8925 | 1.997% | 741 | 6188.5835 | 6081.1075 | 1.767% | 0.27%
2017-04-08 | 13 | 6205 | 107.476 | 1.732% | 16.4165 | 0.2646% | 123.8925 | 1.997% | 742 | 6188.5835 | 6081.1075 | 1.767% | 0.27%
2017-05-13 | 18 | 6210 | 107.4943 | 1.731% | 16.4272 | 0.2645% | 123.9216 | 1.996% | 743 | 6193.5728 | 6086.0784 | 1.766% | 0.2699%
2017-03-24 | 18 | 6211 | 107.498 | 1.731% | 16.4294 | 0.2645% | 123.9274 | 1.995% | 744 | 6194.5706 | 6087.0726 | 1.766% | 0.2699%
2017-05-03 | 8 | 6212 | 107.5017 | 1.731% | 16.4315 | 0.2645% | 123.9332 | 1.995% | 745 | 6195.5685 | 6088.0668 | 1.766% | 0.2699%
2017-03-18 | 19 | 6213 | 107.5053 | 1.73% | 16.4337 | 0.2645% | 123.939 | 1.995% | 746 | 6196.5663 | 6089.061 | 1.766% | 0.2699%
2017-05-06 | 21 | 6213 | 107.5053 | 1.73% | 16.4337 | 0.2645% | 123.939 | 1.995% | 747 | 6196.5663 | 6089.061 | 1.766% | 0.2699%
2017-03-23 | 3 | 6214 | 107.509 | 1.73% | 16.4358 | 0.2645% | 123.9448 | 1.995% | 748 | 6197.5642 | 6090.0552 | 1.765% | 0.2699%
2017-05-15 | 8 | 6216 | 107.5163 | 1.73% | 16.4401 | 0.2645% | 123.9564 | 1.994% | 749 | 6199.5599 | 6092.0436 | 1.765% | 0.2699%
2017-05-13 | 17 | 6217 | 107.52 | 1.729% | 16.4422 | 0.2645% | 123.9622 | 1.994% | 750 | 6200.5578 | 6093.0378 | 1.765% | 0.2699%
2017-04-07 | 24 | 6223 | 107.542 | 1.728% | 16.455 | 0.2644% | 123.997 | 1.993% | 751 | 6206.545 | 6099.003 | 1.763% | 0.2698%
2017-05-02 | 1 | 6223 | 107.542 | 1.728% | 16.455 | 0.2644% | 123.997 | 1.993% | 752 | 6206.545 | 6099.003 | 1.763% | 0.2698%
2017-03-01 | 7 | 6226 | 107.5529 | 1.727% | 16.4615 | 0.2644% | 124.0144 | 1.992% | 753 | 6209.5385 | 6101.9856 | 1.763% | 0.2698%
2017-03-31 | 23 | 6227 | 107.5566 | 1.727% | 16.4636 | 0.2644% | 124.0202 | 1.992% | 754 | 6210.5364 | 6102.9798 | 1.762% | 0.2698%
2017-03-26 | 17 | 6229 | 107.5639 | 1.727% | 16.4679 | 0.2644% | 124.0318 | 1.991% | 755 | 6212.5321 | 6104.9682 | 1.762% | 0.2697%
2017-04-07 | 19 | 6229 | 107.5639 | 1.727% | 16.4679 | 0.2644% | 124.0318 | 1.991% | 756 | 6212.5321 | 6104.9682 | 1.762% | 0.2697%
2017-04-09 | 20 | 6229 | 107.5639 | 1.727% | 16.4679 | 0.2644% | 124.0318 | 1.991% | 757 | 6212.5321 | 6104.9682 | 1.762% | 0.2697%
2017-04-19 | 9 | 6229 | 107.5639 | 1.727% | 16.4679 | 0.2644% | 124.0318 | 1.991% | 758 | 6212.5321 | 6104.9682 | 1.762% | 0.2697%
2017-04-05 | 8 | 6232 | 107.5749 | 1.726% | 16.4743 | 0.2644% | 124.0492 | 1.991% | 759 | 6215.5257 | 6107.9508 | 1.761% | 0.2697%
2017-04-06 | 23 | 6235 | 107.5859 | 1.726% | 16.4807 | 0.2643% | 124.0666 | 1.99% | 760 | 6218.5193 | 6110.9334 | 1.761% | 0.2697%
2017-04-12 | 9 | 6236 | 107.5896 | 1.725% | 16.4829 | 0.2643% | 124.0725 | 1.99% | 761 | 6219.5171 | 6111.9275 | 1.76% | 0.2697%
2017-05-04 | 8 | 6237 | 107.5932 | 1.725% | 16.485 | 0.2643% | 124.0783 | 1.989% | 762 | 6220.515 | 6112.9217 | 1.76% | 0.2697%
2017-05-10 | 8 | 6238 | 107.5969 | 1.725% | 16.4871 | 0.2643% | 124.0841 | 1.989% | 763 | 6221.5129 | 6113.9159 | 1.76% | 0.2697%
2017-03-10 | 16 | 6242 | 107.6116 | 1.724% | 16.4957 | 0.2643% | 124.1073 | 1.988% | 764 | 6225.5043 | 6117.8927 | 1.759% | 0.2696%
2017-03-25 | 11 | 6242 | 107.6116 | 1.724% | 16.4957 | 0.2643% | 124.1073 | 1.988% | 765 | 6225.5043 | 6117.8927 | 1.759% | 0.2696%
2017-03-08 | 7 | 6246 | 107.6262 | 1.723% | 16.5043 | 0.2642% | 124.1305 | 1.987% | 766 | 6229.4957 | 6121.8695 | 1.758% | 0.2696%
2017-05-26 | 24 | 6246 | 107.6262 | 1.723% | 16.5043 | 0.2642% | 124.1305 | 1.987% | 767 | 6229.4957 | 6121.8695 | 1.758% | 0.2696%
2017-03-10 | 17 | 6248 | 107.6335 | 1.723% | 16.5085 | 0.2642% | 124.1421 | 1.987% | 768 | 6231.4915 | 6123.8579 | 1.758% | 0.2696%
2017-05-07 | 22 | 6248 | 107.6335 | 1.723% | 16.5085 | 0.2642% | 124.1421 | 1.987% | 769 | 6231.4915 | 6123.8579 | 1.758% | 0.2696%
2017-03-07 | 12 | 6249 | 107.6372 | 1.722% | 16.5107 | 0.2642% | 124.1479 | 1.987% | 770 | 6232.4893 | 6124.8521 | 1.757% | 0.2696%
2017-04-01 | 22 | 6250 | 107.6409 | 1.722% | 16.5128 | 0.2642% | 124.1537 | 1.986% | 771 | 6233.4872 | 6125.8463 | 1.757% | 0.2696%
2017-04-26 | 8 | 6258 | 107.6702 | 1.721% | 16.5299 | 0.2641% | 124.2001 | 1.985% | 772 | 6241.4701 | 6133.7999 | 1.755% | 0.2695%
2017-03-08 | 23 | 6259 | 107.6738 | 1.72% | 16.5321 | 0.2641% | 124.2059 | 1.984% | 773 | 6242.4679 | 6134.7941 | 1.755% | 0.2695%
2017-04-10 | 23 | 6259 | 107.6738 | 1.72% | 16.5321 | 0.2641% | 124.2059 | 1.984% | 774 | 6242.4679 | 6134.7941 | 1.755% | 0.2695%
2017-03-24 | 16 | 6261 | 107.6812 | 1.72% | 16.5364 | 0.2641% | 124.2175 | 1.984% | 775 | 6244.4636 | 6136.7825 | 1.755% | 0.2695%
2017-03-25 | 10 | 6262 | 107.6848 | 1.72% | 16.5385 | 0.2641% | 124.2233 | 1.984% | 776 | 6245.4615 | 6137.7767 | 1.754% | 0.2695%
2017-04-03 | 7 | 6264 | 107.6922 | 1.719% | 16.5428 | 0.2641% | 124.2349 | 1.983% | 777 | 6247.4572 | 6139.7651 | 1.754% | 0.2694%
2017-04-16 | 23 | 6264 | 107.6922 | 1.719% | 16.5428 | 0.2641% | 124.2349 | 1.983% | 778 | 6247.4572 | 6139.7651 | 1.754% | 0.2694%
2017-04-25 | 23 | 6264 | 107.6922 | 1.719% | 16.5428 | 0.2641% | 124.2349 | 1.983% | 779 | 6247.4572 | 6139.7651 | 1.754% | 0.2694%
2017-04-07 | 15 | 6267 | 107.7032 | 1.719% | 16.5492 | 0.2641% | 124.2524 | 1.983% | 780 | 6250.4508 | 6142.7476 | 1.753% | 0.2694%
2017-04-11 | 9 | 6267 | 107.7032 | 1.719% | 16.5492 | 0.2641% | 124.2524 | 1.983% | 781 | 6250.4508 | 6142.7476 | 1.753% | 0.2694%
2017-04-23 | 19 | 6267 | 107.7032 | 1.719% | 16.5492 | 0.2641% | 124.2524 | 1.983% | 782 | 6250.4508 | 6142.7476 | 1.753% | 0.2694%
2017-04-13 | 9 | 6268 | 107.7068 | 1.718% | 16.5513 | 0.2641% | 124.2582 | 1.982% | 783 | 6251.4487 | 6143.7418 | 1.753% | 0.2694%
2017-04-14 | 23 | 6269 | 107.7105 | 1.718% | 16.5535 | 0.2641% | 124.264 | 1.982% | 784 | 6252.4465 | 6144.736 | 1.753% | 0.2694%
2017-03-18 | 1 | 6271 | 107.7178 | 1.718% | 16.5578 | 0.264% | 124.2756 | 1.982% | 785 | 6254.4422 | 6146.7244 | 1.752% | 0.2694%
2017-05-12 | 8 | 6271 | 107.7178 | 1.718% | 16.5578 | 0.264% | 124.2756 | 1.982% | 786 | 6254.4422 | 6146.7244 | 1.752% | 0.2694%
2017-05-24 | 24 | 6272 | 107.7215 | 1.717% | 16.5599 | 0.264% | 124.2814 | 1.982% | 787 | 6255.4401 | 6147.7186 | 1.752% | 0.2694%
2017-04-09 | 22 | 6275 | 107.7325 | 1.717% | 16.5663 | 0.264% | 124.2988 | 1.981% | 788 | 6258.4337 | 6150.7012 | 1.752% | 0.2693%
2017-04-18 | 8 | 6276 | 107.7361 | 1.717% | 16.5685 | 0.264% | 124.3046 | 1.981% | 789 | 6259.4315 | 6151.6954 | 1.751% | 0.2693%
2017-05-08 | 9 | 6277 | 107.7398 | 1.716% | 16.5706 | 0.264% | 124.3104 | 1.98% | 790 | 6260.4294 | 6152.6896 | 1.751% | 0.2693%
2017-03-22 | 16 | 6279 | 107.7471 | 1.716% | 16.5749 | 0.264% | 124.322 | 1.98% | 791 | 6262.4251 | 6154.678 | 1.751% | 0.2693%
2017-03-28 | 23 | 6279 | 107.7471 | 1.716% | 16.5749 | 0.264% | 124.322 | 1.98% | 792 | 6262.4251 | 6154.678 | 1.751% | 0.2693%
2017-03-04 | 15 | 6284 | 107.7654 | 1.715% | 16.5856 | 0.2639% | 124.351 | 1.979% | 793 | 6267.4144 | 6159.649 | 1.75% | 0.2693%
2017-05-09 | 23 | 6284 | 107.7654 | 1.715% | 16.5856 | 0.2639% | 124.351 | 1.979% | 794 | 6267.4144 | 6159.649 | 1.75% | 0.2693%
2017-03-09 | 16 | 6285 | 107.7691 | 1.715% | 16.5877 | 0.2639% | 124.3568 | 1.979% | 795 | 6268.4123 | 6160.6432 | 1.749% | 0.2693%
2017-03-10 | 15 | 6285 | 107.7691 | 1.715% | 16.5877 | 0.2639% | 124.3568 | 1.979% | 796 | 6268.4123 | 6160.6432 | 1.749% | 0.2693%
2017-03-11 | 16 | 6286 | 107.7728 | 1.714% | 16.5899 | 0.2639% | 124.3626 | 1.978% | 797 | 6269.4101 | 6161.6374 | 1.749% | 0.2692%
2017-03-02 | 16 | 6288 | 107.7801 | 1.714% | 16.5941 | 0.2639% | 124.3742 | 1.978% | 798 | 6271.4059 | 6163.6258 | 1.749% | 0.2692%
2017-05-17 | 7 | 6291 | 107.7911 | 1.713% | 16.6006 | 0.2639% | 124.3916 | 1.977% | 799 | 6274.3994 | 6166.6084 | 1.748% | 0.2692%
2017-05-21 | 10 | 6291 | 107.7911 | 1.713% | 16.6006 | 0.2639% | 124.3916 | 1.977% | 800 | 6274.3994 | 6166.6084 | 1.748% | 0.2692%
2017-03-19 | 6 | 6294 | 107.8021 | 1.713% | 16.607 | 0.2639% | 124.409 | 1.977% | 801 | 6277.393 | 6169.591 | 1.747% | 0.2692%
2017-04-05 | 9 | 6295 | 107.8057 | 1.713% | 16.6091 | 0.2638% | 124.4148 | 1.976% | 802 | 6278.3909 | 6170.5852 | 1.747% | 0.2692%
2017-04-02 | 20 | 6296 | 107.8094 | 1.712% | 16.6113 | 0.2638% | 124.4206 | 1.976% | 803 | 6279.3887 | 6171.5794 | 1.747% | 0.2692%
2017-03-02 | 15 | 6299 | 107.8204 | 1.712% | 16.6177 | 0.2638% | 124.4381 | 1.976% | 804 | 6282.3823 | 6174.5619 | 1.746% | 0.2691%
2017-03-31 | 9 | 6300 | 107.824 | 1.711% | 16.6198 | 0.2638% | 124.4439 | 1.975% | 805 | 6283.3802 | 6175.5561 | 1.746% | 0.2691%
2017-03-22 | 17 | 6301 | 107.8277 | 1.711% | 16.622 | 0.2638% | 124.4497 | 1.975% | 806 | 6284.378 | 6176.5503 | 1.746% | 0.2691%
2017-05-05 | 7 | 6301 | 107.8277 | 1.711% | 16.622 | 0.2638% | 124.4497 | 1.975% | 807 | 6284.378 | 6176.5503 | 1.746% | 0.2691%
2017-04-23 | 22 | 6302 | 107.8314 | 1.711% | 16.6241 | 0.2638% | 124.4555 | 1.975% | 808 | 6285.3759 | 6177.5445 | 1.746% | 0.2691%
2017-04-02 | 22 | 6306 | 107.846 | 1.71% | 16.6327 | 0.2638% | 124.4787 | 1.974% | 809 | 6289.3673 | 6181.5213 | 1.745% | 0.2691%
2017-03-26 | 19 | 6308 | 107.8534 | 1.71% | 16.6369 | 0.2637% | 124.4903 | 1.974% | 810 | 6291.3631 | 6183.5097 | 1.744% | 0.2691%
2017-03-11 | 2 | 6310 | 107.8607 | 1.709% | 16.6412 | 0.2637% | 124.5019 | 1.973% | 811 | 6293.3588 | 6185.4981 | 1.744% | 0.269%
2017-03-09 | 17 | 6314 | 107.8753 | 1.709% | 16.6498 | 0.2637% | 124.5251 | 1.972% | 812 | 6297.3502 | 6189.4749 | 1.743% | 0.269%
2017-04-11 | 10 | 6314 | 107.8753 | 1.709% | 16.6498 | 0.2637% | 124.5251 | 1.972% | 813 | 6297.3502 | 6189.4749 | 1.743% | 0.269%
2017-03-29 | 8 | 6317 | 107.8863 | 1.708% | 16.6562 | 0.2637% | 124.5425 | 1.972% | 814 | 6300.3438 | 6192.4575 | 1.742% | 0.269%
2017-04-01 | 17 | 6320 | 107.8973 | 1.707% | 16.6626 | 0.2636% | 124.5599 | 1.971% | 815 | 6303.3374 | 6195.4401 | 1.742% | 0.2689%
2017-03-10 | 18 | 6321 | 107.901 | 1.707% | 16.6648 | 0.2636% | 124.5657 | 1.971% | 816 | 6304.3352 | 6196.4343 | 1.741% | 0.2689%
2017-03-11 | 1 | 6322 | 107.9046 | 1.707% | 16.6669 | 0.2636% | 124.5715 | 1.97% | 817 | 6305.3331 | 6197.4285 | 1.741% | 0.2689%
2017-04-18 | 23 | 6322 | 107.9046 | 1.707% | 16.6669 | 0.2636% | 124.5715 | 1.97% | 818 | 6305.3331 | 6197.4285 | 1.741% | 0.2689%
2017-04-14 | 13 | 6325 | 107.9156 | 1.706% | 16.6733 | 0.2636% | 124.5889 | 1.97% | 819 | 6308.3267 | 6200.4111 | 1.74% | 0.2689%
2017-04-29 | 8 | 6328 | 107.9266 | 1.706% | 16.6797 | 0.2636% | 124.6064 | 1.969% | 820 | 6311.3203 | 6203.3936 | 1.74% | 0.2689%
2017-03-02 | 17 | 6329 | 107.9303 | 1.705% | 16.6819 | 0.2636% | 124.6122 | 1.969% | 821 | 6312.3181 | 6204.3878 | 1.74% | 0.2689%
2017-03-07 | 16 | 6329 | 107.9303 | 1.705% | 16.6819 | 0.2636% | 124.6122 | 1.969% | 822 | 6312.3181 | 6204.3878 | 1.74% | 0.2689%
2017-03-27 | 8 | 6329 | 107.9303 | 1.705% | 16.6819 | 0.2636% | 124.6122 | 1.969% | 823 | 6312.3181 | 6204.3878 | 1.74% | 0.2689%
2017-05-09 | 8 | 6330 | 107.9339 | 1.705% | 16.684 | 0.2636% | 124.618 | 1.969% | 824 | 6313.316 | 6205.382 | 1.739% | 0.2689%
2017-05-03 | 9 | 6332 | 107.9413 | 1.705% | 16.6883 | 0.2636% | 124.6296 | 1.968% | 825 | 6315.3117 | 6207.3704 | 1.739% | 0.2688%
2017-03-22 | 15 | 6333 | 107.9449 | 1.704% | 16.6904 | 0.2635% | 124.6354 | 1.968% | 826 | 6316.3096 | 6208.3646 | 1.739% | 0.2688%
2017-05-08 | 10 | 6333 | 107.9449 | 1.704% | 16.6904 | 0.2635% | 124.6354 | 1.968% | 827 | 6316.3096 | 6208.3646 | 1.739% | 0.2688%
2017-03-18 | 23 | 6336 | 107.9559 | 1.704% | 16.6968 | 0.2635% | 124.6528 | 1.967% | 828 | 6319.3032 | 6211.3472 | 1.738% | 0.2688%
2017-03-28 | 9 | 6339 | 107.9669 | 1.703% | 16.7033 | 0.2635% | 124.6702 | 1.967% | 829 | 6322.2967 | 6214.3298 | 1.737% | 0.2688%
2017-04-08 | 12 | 6339 | 107.9669 | 1.703% | 16.7033 | 0.2635% | 124.6702 | 1.967% | 830 | 6322.2967 | 6214.3298 | 1.737% | 0.2688%
2017-03-24 | 15 | 6341 | 107.9742 | 1.703% | 16.7075 | 0.2635% | 124.6818 | 1.966% | 831 | 6324.2925 | 6216.3182 | 1.737% | 0.2688%
2017-03-03 | 2 | 6343 | 107.9816 | 1.702% | 16.7118 | 0.2635% | 124.6934 | 1.966% | 832 | 6326.2882 | 6218.3066 | 1.737% | 0.2688%
2017-05-17 | 1 | 6343 | 107.9816 | 1.702% | 16.7118 | 0.2635% | 124.6934 | 1.966% | 833 | 6326.2882 | 6218.3066 | 1.737% | 0.2688%
2017-03-22 | 24 | 6344 | 107.9852 | 1.702% | 16.714 | 0.2635% | 124.6992 | 1.966% | 834 | 6327.286 | 6219.3008 | 1.736% | 0.2687%
2017-04-19 | 10 | 6344 | 107.9852 | 1.702% | 16.714 | 0.2635% | 124.6992 | 1.966% | 835 | 6327.286 | 6219.3008 | 1.736% | 0.2687%
2017-04-20 | 9 | 6345 | 107.9889 | 1.702% | 16.7161 | 0.2635% | 124.705 | 1.965% | 836 | 6328.2839 | 6220.295 | 1.736% | 0.2687%
2017-03-07 | 17 | 6346 | 107.9926 | 1.702% | 16.7182 | 0.2634% | 124.7108 | 1.965% | 837 | 6329.2818 | 6221.2892 | 1.736% | 0.2687%
2017-03-31 | 8 | 6346 | 107.9926 | 1.702% | 16.7182 | 0.2634% | 124.7108 | 1.965% | 838 | 6329.2818 | 6221.2892 | 1.736% | 0.2687%
2017-03-25 | 21 | 6349 | 108.0036 | 1.701% | 16.7247 | 0.2634% | 124.7282 | 1.965% | 839 | 6332.2753 | 6224.2718 | 1.735% | 0.2687%
2017-03-29 | 9 | 6351 | 108.0109 | 1.701% | 16.7289 | 0.2634% | 124.7398 | 1.964% | 840 | 6334.2711 | 6226.2602 | 1.735% | 0.2687%
2017-03-11 | 17 | 6352 | 108.0145 | 1.7% | 16.7311 | 0.2634% | 124.7456 | 1.964% | 841 | 6335.2689 | 6227.2544 | 1.735% | 0.2687%
2017-03-09 | 15 | 6355 | 108.0255 | 1.7% | 16.7375 | 0.2634% | 124.763 | 1.963% | 842 | 6338.2625 | 6230.237 | 1.734% | 0.2686%
2017-05-02 | 7 | 6355 | 108.0255 | 1.7% | 16.7375 | 0.2634% | 124.763 | 1.963% | 843 | 6338.2625 | 6230.237 | 1.734% | 0.2686%
2017-03-27 | 9 | 6356 | 108.0292 | 1.7% | 16.7396 | 0.2634% | 124.7688 | 1.963% | 844 | 6339.2604 | 6231.2312 | 1.734% | 0.2686%
2017-05-08 | 8 | 6356 | 108.0292 | 1.7% | 16.7396 | 0.2634% | 124.7688 | 1.963% | 845 | 6339.2604 | 6231.2312 | 1.734% | 0.2686%
2017-05-14 | 14 | 6356 | 108.0292 | 1.7% | 16.7396 | 0.2634% | 124.7688 | 1.963% | 846 | 6339.2604 | 6231.2312 | 1.734% | 0.2686%
2017-03-22 | 18 | 6357 | 108.0329 | 1.699% | 16.7418 | 0.2634% | 124.7746 | 1.963% | 847 | 6340.2582 | 6232.2254 | 1.733% | 0.2686%
2017-03-27 | 12 | 6358 | 108.0365 | 1.699% | 16.7439 | 0.2634% | 124.7805 | 1.963% | 848 | 6341.2561 | 6233.2195 | 1.733% | 0.2686%
2017-05-08 | 11 | 6360 | 108.0439 | 1.699% | 16.7482 | 0.2633% | 124.7921 | 1.962% | 849 | 6343.2518 | 6235.2079 | 1.733% | 0.2686%
2017-03-11 | 15 | 6362 | 108.0512 | 1.698% | 16.7525 | 0.2633% | 124.8037 | 1.962% | 850 | 6345.2475 | 6237.1963 | 1.732% | 0.2686%
2017-04-12 | 10 | 6362 | 108.0512 | 1.698% | 16.7525 | 0.2633% | 124.8037 | 1.962% | 851 | 6345.2475 | 6237.1963 | 1.732% | 0.2686%
2017-05-09 | 11 | 6362 | 108.0512 | 1.698% | 16.7525 | 0.2633% | 124.8037 | 1.962% | 852 | 6345.2475 | 6237.1963 | 1.732% | 0.2686%
2017-05-09 | 10 | 6363 | 108.0548 | 1.698% | 16.7546 | 0.2633% | 124.8095 | 1.961% | 853 | 6346.2454 | 6238.1905 | 1.732% | 0.2686%
2017-04-13 | 23 | 6364 | 108.0585 | 1.698% | 16.7568 | 0.2633% | 124.8153 | 1.961% | 854 | 6347.2432 | 6239.1847 | 1.732% | 0.2686%
2017-04-26 | 9 | 6365 | 108.0622 | 1.698% | 16.7589 | 0.2633% | 124.8211 | 1.961% | 855 | 6348.2411 | 6240.1789 | 1.732% | 0.2686%
2017-05-10 | 9 | 6367 | 108.0695 | 1.697% | 16.7632 | 0.2633% | 124.8327 | 1.961% | 856 | 6350.2368 | 6242.1673 | 1.731% | 0.2685%
2017-03-07 | 15 | 6368 | 108.0732 | 1.697% | 16.7653 | 0.2633% | 124.8385 | 1.96% | 857 | 6351.2347 | 6243.1615 | 1.731% | 0.2685%
2017-03-26 | 18 | 6368 | 108.0732 | 1.697% | 16.7653 | 0.2633% | 124.8385 | 1.96% | 858 | 6351.2347 | 6243.1615 | 1.731% | 0.2685%
2017-04-27 | 8 | 6368 | 108.0732 | 1.697% | 16.7653 | 0.2633% | 124.8385 | 1.96% | 859 | 6351.2347 | 6243.1615 | 1.731% | 0.2685%
2017-04-29 | 2 | 6368 | 108.0732 | 1.697% | 16.7653 | 0.2633% | 124.8385 | 1.96% | 860 | 6351.2347 | 6243.1615 | 1.731% | 0.2685%
2017-03-03 | 1 | 6371 | 108.0842 | 1.697% | 16.7717 | 0.2633% | 124.8559 | 1.96% | 861 | 6354.2283 | 6246.1441 | 1.73% | 0.2685%
2017-03-10 | 14 | 6371 | 108.0842 | 1.697% | 16.7717 | 0.2633% | 124.8559 | 1.96% | 862 | 6354.2283 | 6246.1441 | 1.73% | 0.2685%
2017-04-21 | 8 | 6372 | 108.0878 | 1.696% | 16.7739 | 0.2632% | 124.8617 | 1.96% | 863 | 6355.2261 | 6247.1383 | 1.73% | 0.2685%
2017-05-28 | 1 | 6373 | 108.0915 | 1.696% | 16.776 | 0.2632% | 124.8675 | 1.959% | 864 | 6356.224 | 6248.1325 | 1.73% | 0.2685%
2017-03-24 | 20 | 6374 | 108.0951 | 1.696% | 16.7782 | 0.2632% | 124.8733 | 1.959% | 865 | 6357.2218 | 6249.1267 | 1.73% | 0.2685%
2017-05-07 | 21 | 6376 | 108.1025 | 1.695% | 16.7824 | 0.2632% | 124.8849 | 1.959% | 866 | 6359.2176 | 6251.1151 | 1.729% | 0.2685%
2017-03-09 | 18 | 6379 | 108.1135 | 1.695% | 16.7889 | 0.2632% | 124.9023 | 1.958% | 867 | 6362.2111 | 6254.0977 | 1.729% | 0.2684%
2017-05-09 | 9 | 6379 | 108.1135 | 1.695% | 16.7889 | 0.2632% | 124.9023 | 1.958% | 868 | 6362.2111 | 6254.0977 | 1.729% | 0.2684%
2017-05-28 | 9 | 6380 | 108.1171 | 1.695% | 16.791 | 0.2632% | 124.9081 | 1.958% | 869 | 6363.209 | 6255.0919 | 1.728% | 0.2684%
2017-03-05 | 14 | 6382 | 108.1244 | 1.694% | 16.7953 | 0.2632% | 124.9197 | 1.957% | 870 | 6365.2047 | 6257.0803 | 1.728% | 0.2684%
2017-04-03 | 11 | 6384 | 108.1318 | 1.694% | 16.7996 | 0.2632% | 124.9313 | 1.957% | 871 | 6367.2004 | 6259.0687 | 1.728% | 0.2684%
2017-03-02 | 14 | 6388 | 108.1464 | 1.693% | 16.8081 | 0.2631% | 124.9546 | 1.956% | 872 | 6371.1919 | 6263.0454 | 1.727% | 0.2684%
2017-03-22 | 14 | 6389 | 108.1501 | 1.693% | 16.8103 | 0.2631% | 124.9604 | 1.956% | 873 | 6372.1897 | 6264.0396 | 1.727% | 0.2684%
2017-05-08 | 12 | 6389 | 108.1501 | 1.693% | 16.8103 | 0.2631% | 124.9604 | 1.956% | 874 | 6372.1897 | 6264.0396 | 1.727% | 0.2684%
2017-05-29 | 1 | 6389 | 108.1501 | 1.693% | 16.8103 | 0.2631% | 124.9604 | 1.956% | 875 | 6372.1897 | 6264.0396 | 1.727% | 0.2684%
2017-03-30 | 18 | 6390 | 108.1538 | 1.693% | 16.8124 | 0.2631% | 124.9662 | 1.956% | 876 | 6373.1876 | 6265.0338 | 1.726% | 0.2684%
2017-05-26 | 9 | 6390 | 108.1538 | 1.693% | 16.8124 | 0.2631% | 124.9662 | 1.956% | 877 | 6373.1876 | 6265.0338 | 1.726% | 0.2684%
2017-04-04 | 8 | 6392 | 108.1611 | 1.692% | 16.8167 | 0.2631% | 124.9778 | 1.955% | 878 | 6375.1833 | 6267.0222 | 1.726% | 0.2683%
2017-03-18 | 16 | 6396 | 108.1757 | 1.691% | 16.8252 | 0.2631% | 125.001 | 1.954% | 879 | 6379.1748 | 6270.999 | 1.725% | 0.2683%
2017-03-21 | 6 | 6397 | 108.1794 | 1.691% | 16.8274 | 0.2631% | 125.0068 | 1.954% | 880 | 6380.1726 | 6271.9932 | 1.725% | 0.2683%
2017-04-06 | 16 | 6397 | 108.1794 | 1.691% | 16.8274 | 0.2631% | 125.0068 | 1.954% | 881 | 6380.1726 | 6271.9932 | 1.725% | 0.2683%
2017-04-16 | 12 | 6397 | 108.1794 | 1.691% | 16.8274 | 0.2631% | 125.0068 | 1.954% | 882 | 6380.1726 | 6271.9932 | 1.725% | 0.2683%
2017-05-08 | 13 | 6397 | 108.1794 | 1.691% | 16.8274 | 0.2631% | 125.0068 | 1.954% | 883 | 6380.1726 | 6271.9932 | 1.725% | 0.2683%
2017-03-30 | 17 | 6399 | 108.1867 | 1.691% | 16.8317 | 0.263% | 125.0184 | 1.954% | 884 | 6382.1683 | 6273.9816 | 1.724% | 0.2683%
2017-03-19 | 18 | 6403 | 108.2014 | 1.69% | 16.8402 | 0.263% | 125.0416 | 1.953% | 885 | 6386.1598 | 6277.9584 | 1.724% | 0.2682%
2017-03-30 | 19 | 6403 | 108.2014 | 1.69% | 16.8402 | 0.263% | 125.0416 | 1.953% | 886 | 6386.1598 | 6277.9584 | 1.724% | 0.2682%
2017-04-19 | 23 | 6405 | 108.2087 | 1.689% | 16.8445 | 0.263% | 125.0532 | 1.952% | 887 | 6388.1555 | 6279.9468 | 1.723% | 0.2682%
2017-04-10 | 11 | 6406 | 108.2124 | 1.689% | 16.8466 | 0.263% | 125.059 | 1.952% | 888 | 6389.1534 | 6280.941 | 1.723% | 0.2682%
2017-05-30 | 1 | 6406 | 108.2124 | 1.689% | 16.8466 | 0.263% | 125.059 | 1.952% | 889 | 6389.1534 | 6280.941 | 1.723% | 0.2682%
2017-03-30 | 13 | 6408 | 108.2197 | 1.689% | 16.8509 | 0.263% | 125.0706 | 1.952% | 890 | 6391.1491 | 6282.9294 | 1.722% | 0.2682%
2017-04-06 | 15 | 6408 | 108.2197 | 1.689% | 16.8509 | 0.263% | 125.0706 | 1.952% | 891 | 6391.1491 | 6282.9294 | 1.722% | 0.2682%
2017-03-06 | 17 | 6409 | 108.2234 | 1.689% | 16.8531 | 0.263% | 125.0764 | 1.952% | 892 | 6392.1469 | 6283.9236 | 1.722% | 0.2682%
2017-03-08 | 13 | 6409 | 108.2234 | 1.689% | 16.8531 | 0.263% | 125.0764 | 1.952% | 893 | 6392.1469 | 6283.9236 | 1.722% | 0.2682%
2017-05-21 | 1 | 6416 | 108.249 | 1.687% | 16.868 | 0.2629% | 125.117 | 1.95% | 894 | 6399.132 | 6290.883 | 1.721% | 0.2681%
2017-03-03 | 16 | 6417 | 108.2527 | 1.687% | 16.8702 | 0.2629% | 125.1228 | 1.95% | 895 | 6400.1298 | 6291.8772 | 1.721% | 0.2681%
2017-03-08 | 12 | 6417 | 108.2527 | 1.687% | 16.8702 | 0.2629% | 125.1228 | 1.95% | 896 | 6400.1298 | 6291.8772 | 1.721% | 0.2681%
2017-03-06 | 16 | 6418 | 108.2563 | 1.687% | 16.8723 | 0.2629% | 125.1286 | 1.95% | 897 | 6401.1277 | 6292.8714 | 1.72% | 0.2681%
2017-03-27 | 10 | 6418 | 108.2563 | 1.687% | 16.8723 | 0.2629% | 125.1286 | 1.95% | 898 | 6401.1277 | 6292.8714 | 1.72% | 0.2681%
2017-04-01 | 20 | 6418 | 108.2563 | 1.687% | 16.8723 | 0.2629% | 125.1286 | 1.95% | 899 | 6401.1277 | 6292.8714 | 1.72% | 0.2681%
2017-05-12 | 9 | 6418 | 108.2563 | 1.687% | 16.8723 | 0.2629% | 125.1286 | 1.95% | 900 | 6401.1277 | 6292.8714 | 1.72% | 0.2681%
2017-05-21 | 24 | 6418 | 108.2563 | 1.687% | 16.8723 | 0.2629% | 125.1286 | 1.95% | 901 | 6401.1277 | 6292.8714 | 1.72% | 0.2681%
2017-04-04 | 9 | 6419 | 108.26 | 1.687% | 16.8745 | 0.2629% | 125.1345 | 1.949% | 902 | 6402.1255 | 6293.8655 | 1.72% | 0.2681%
2017-03-07 | 18 | 6420 | 108.2637 | 1.686% | 16.8766 | 0.2629% | 125.1403 | 1.949% | 903 | 6403.1234 | 6294.8597 | 1.72% | 0.2681%
2017-03-19 | 17 | 6420 | 108.2637 | 1.686% | 16.8766 | 0.2629% | 125.1403 | 1.949% | 904 | 6403.1234 | 6294.8597 | 1.72% | 0.2681%
2017-04-17 | 10 | 6421 | 108.2673 | 1.686% | 16.8787 | 0.2629% | 125.1461 | 1.949% | 905 | 6404.1213 | 6295.8539 | 1.72% | 0.2681%
2017-05-04 | 24 | 6422 | 108.271 | 1.686% | 16.8809 | 0.2629% | 125.1519 | 1.949% | 906 | 6405.1191 | 6296.8481 | 1.719% | 0.2681%
2017-03-22 | 19 | 6423 | 108.2747 | 1.686% | 16.883 | 0.2629% | 125.1577 | 1.949% | 907 | 6406.117 | 6297.8423 | 1.719% | 0.2681%
2017-04-26 | 10 | 6423 | 108.2747 | 1.686% | 16.883 | 0.2629% | 125.1577 | 1.949% | 908 | 6406.117 | 6297.8423 | 1.719% | 0.2681%
2017-03-30 | 15 | 6424 | 108.2783 | 1.686% | 16.8852 | 0.2628% | 125.1635 | 1.948% | 909 | 6407.1148 | 6298.8365 | 1.719% | 0.2681%
2017-03-24 | 22 | 6425 | 108.282 | 1.685% | 16.8873 | 0.2628% | 125.1693 | 1.948% | 910 | 6408.1127 | 6299.8307 | 1.719% | 0.2681%
2017-04-03 | 10 | 6426 | 108.2856 | 1.685% | 16.8894 | 0.2628% | 125.1751 | 1.948% | 911 | 6409.1106 | 6300.8249 | 1.719% | 0.2681%
2017-04-18 | 9 | 6426 | 108.2856 | 1.685% | 16.8894 | 0.2628% | 125.1751 | 1.948% | 912 | 6409.1106 | 6300.8249 | 1.719% | 0.2681%
2017-04-30 | 9 | 6426 | 108.2856 | 1.685% | 16.8894 | 0.2628% | 125.1751 | 1.948% | 913 | 6409.1106 | 6300.8249 | 1.719% | 0.2681%
2017-05-16 | 8 | 6426 | 108.2856 | 1.685% | 16.8894 | 0.2628% | 125.1751 | 1.948% | 914 | 6409.1106 | 6300.8249 | 1.719% | 0.2681%
2017-03-05 | 18 | 6429 | 108.2966 | 1.685% | 16.8959 | 0.2628% | 125.1925 | 1.947% | 915 | 6412.1041 | 6303.8075 | 1.718% | 0.268%
2017-03-08 | 16 | 6430 | 108.3003 | 1.684% | 16.898 | 0.2628% | 125.1983 | 1.947% | 916 | 6413.102 | 6304.8017 | 1.718% | 0.268%
2017-03-28 | 10 | 6430 | 108.3003 | 1.684% | 16.898 | 0.2628% | 125.1983 | 1.947% | 917 | 6413.102 | 6304.8017 | 1.718% | 0.268%
2017-03-08 | 14 | 6432 | 108.3076 | 1.684% | 16.9023 | 0.2628% | 125.2099 | 1.947% | 918 | 6415.0977 | 6306.7901 | 1.717% | 0.268%
2017-04-24 | 8 | 6432 | 108.3076 | 1.684% | 16.9023 | 0.2628% | 125.2099 | 1.947% | 919 | 6415.0977 | 6306.7901 | 1.717% | 0.268%
2017-04-06 | 17 | 6433 | 108.3113 | 1.684% | 16.9044 | 0.2628% | 125.2157 | 1.946% | 920 | 6416.0956 | 6307.7843 | 1.717% | 0.268%
2017-03-22 | 13 | 6434 | 108.315 | 1.683% | 16.9066 | 0.2628% | 125.2215 | 1.946% | 921 | 6417.0934 | 6308.7785 | 1.717% | 0.268%
2017-04-13 | 10 | 6434 | 108.315 | 1.683% | 16.9066 | 0.2628% | 125.2215 | 1.946% | 922 | 6417.0934 | 6308.7785 | 1.717% | 0.268%
2017-03-30 | 8 | 6435 | 108.3186 | 1.683% | 16.9087 | 0.2628% | 125.2273 | 1.946% | 923 | 6418.0913 | 6309.7727 | 1.717% | 0.268%
2017-03-30 | 12 | 6435 | 108.3186 | 1.683% | 16.9087 | 0.2628% | 125.2273 | 1.946% | 924 | 6418.0913 | 6309.7727 | 1.717% | 0.268%
2017-04-10 | 10 | 6435 | 108.3186 | 1.683% | 16.9087 | 0.2628% | 125.2273 | 1.946% | 925 | 6418.0913 | 6309.7727 | 1.717% | 0.268%
2017-03-03 | 17 | 6436 | 108.3223 | 1.683% | 16.9108 | 0.2628% | 125.2331 | 1.946% | 926 | 6419.0892 | 6310.7669 | 1.716% | 0.268%
2017-04-23 | 20 | 6436 | 108.3223 | 1.683% | 16.9108 | 0.2628% | 125.2331 | 1.946% | 927 | 6419.0892 | 6310.7669 | 1.716% | 0.268%
2017-03-30 | 16 | 6438 | 108.3296 | 1.683% | 16.9151 | 0.2627% | 125.2447 | 1.945% | 928 | 6421.0849 | 6312.7553 | 1.716% | 0.268%
2017-05-09 | 12 | 6438 | 108.3296 | 1.683% | 16.9151 | 0.2627% | 125.2447 | 1.945% | 929 | 6421.0849 | 6312.7553 | 1.716% | 0.268%
2017-03-03 | 3 | 6439 | 108.3333 | 1.682% | 16.9173 | 0.2627% | 125.2505 | 1.945% | 930 | 6422.0827 | 6313.7495 | 1.716% | 0.2679%
2017-03-20 | 17 | 6440 | 108.3369 | 1.682% | 16.9194 | 0.2627% | 125.2563 | 1.945% | 931 | 6423.0806 | 6314.7437 | 1.716% | 0.2679%
2017-03-11 | 3 | 6441 | 108.3406 | 1.682% | 16.9215 | 0.2627% | 125.2621 | 1.945% | 932 | 6424.0785 | 6315.7379 | 1.715% | 0.2679%
2017-03-27 | 11 | 6441 | 108.3406 | 1.682% | 16.9215 | 0.2627% | 125.2621 | 1.945% | 933 | 6424.0785 | 6315.7379 | 1.715% | 0.2679%
2017-04-10 | 12 | 6441 | 108.3406 | 1.682% | 16.9215 | 0.2627% | 125.2621 | 1.945% | 934 | 6424.0785 | 6315.7379 | 1.715% | 0.2679%
2017-04-05 | 10 | 6443 | 108.3479 | 1.682% | 16.9258 | 0.2627% | 125.2737 | 1.944% | 935 | 6426.0742 | 6317.7263 | 1.715% | 0.2679%
2017-05-10 | 10 | 6443 | 108.3479 | 1.682% | 16.9258 | 0.2627% | 125.2737 | 1.944% | 936 | 6426.0742 | 6317.7263 | 1.715% | 0.2679%
2017-03-07 | 13 | 6444 | 108.3516 | 1.681% | 16.9279 | 0.2627% | 125.2795 | 1.944% | 937 | 6427.0721 | 6318.7205 | 1.715% | 0.2679%
2017-04-15 | 12 | 6444 | 108.3516 | 1.681% | 16.9279 | 0.2627% | 125.2795 | 1.944% | 938 | 6427.0721 | 6318.7205 | 1.715% | 0.2679%
2017-04-20 | 24 | 6446 | 108.3589 | 1.681% | 16.9322 | 0.2627% | 125.2911 | 1.944% | 939 | 6429.0678 | 6320.7089 | 1.714% | 0.2679%
2017-05-04 | 9 | 6448 | 108.3662 | 1.681% | 16.9365 | 0.2627% | 125.3027 | 1.943% | 940 | 6431.0635 | 6322.6973 | 1.714% | 0.2679%
2017-03-08 | 11 | 6450 | 108.3736 | 1.68% | 16.9408 | 0.2626% | 125.3144 | 1.943% | 941 | 6433.0592 | 6324.6856 | 1.714% | 0.2679%
2017-03-08 | 15 | 6450 | 108.3736 | 1.68% | 16.9408 | 0.2626% | 125.3144 | 1.943% | 942 | 6433.0592 | 6324.6856 | 1.714% | 0.2679%
2017-03-04 | 18 | 6451 | 108.3772 | 1.68% | 16.9429 | 0.2626% | 125.3202 | 1.943% | 943 | 6434.0571 | 6325.6798 | 1.713% | 0.2678%
2017-03-07 | 14 | 6452 | 108.3809 | 1.68% | 16.9451 | 0.2626% | 125.326 | 1.942% | 944 | 6435.0549 | 6326.674 | 1.713% | 0.2678%
2017-03-08 | 17 | 6452 | 108.3809 | 1.68% | 16.9451 | 0.2626% | 125.326 | 1.942% | 945 | 6435.0549 | 6326.674 | 1.713% | 0.2678%
2017-03-18 | 22 | 6452 | 108.3809 | 1.68% | 16.9451 | 0.2626% | 125.326 | 1.942% | 946 | 6435.0549 | 6326.674 | 1.713% | 0.2678%
2017-04-11 | 11 | 6452 | 108.3809 | 1.68% | 16.9451 | 0.2626% | 125.326 | 1.942% | 947 | 6435.0549 | 6326.674 | 1.713% | 0.2678%
2017-03-10 | 24 | 6453 | 108.3846 | 1.68% | 16.9472 | 0.2626% | 125.3318 | 1.942% | 948 | 6436.0528 | 6327.6682 | 1.713% | 0.2678%
2017-03-30 | 9 | 6453 | 108.3846 | 1.68% | 16.9472 | 0.2626% | 125.3318 | 1.942% | 949 | 6436.0528 | 6327.6682 | 1.713% | 0.2678%
2017-05-13 | 21 | 6454 | 108.3882 | 1.679% | 16.9493 | 0.2626% | 125.3376 | 1.942% | 950 | 6437.0507 | 6328.6624 | 1.713% | 0.2678%
2017-04-09 | 10 | 6455 | 108.3919 | 1.679% | 16.9515 | 0.2626% | 125.3434 | 1.942% | 951 | 6438.0485 | 6329.6566 | 1.712% | 0.2678%
2017-05-30 | 7 | 6455 | 108.3919 | 1.679% | 16.9515 | 0.2626% | 125.3434 | 1.942% | 952 | 6438.0485 | 6329.6566 | 1.712% | 0.2678%
2017-04-07 | 14 | 6456 | 108.3955 | 1.679% | 16.9536 | 0.2626% | 125.3492 | 1.942% | 953 | 6439.0464 | 6330.6508 | 1.712% | 0.2678%
2017-04-08 | 6 | 6456 | 108.3955 | 1.679% | 16.9536 | 0.2626% | 125.3492 | 1.942% | 954 | 6439.0464 | 6330.6508 | 1.712% | 0.2678%
2017-05-20 | 1 | 6456 | 108.3955 | 1.679% | 16.9536 | 0.2626% | 125.3492 | 1.942% | 955 | 6439.0464 | 6330.6508 | 1.712% | 0.2678%
2017-03-02 | 13 | 6457 | 108.3992 | 1.679% | 16.9558 | 0.2626% | 125.355 | 1.941% | 956 | 6440.0442 | 6331.645 | 1.712% | 0.2678%
2017-05-22 | 7 | 6459 | 108.4065 | 1.678% | 16.96 | 0.2626% | 125.3666 | 1.941% | 957 | 6442.04 | 6333.6334 | 1.712% | 0.2678%
2017-03-06 | 23 | 6461 | 108.4139 | 1.678% | 16.9643 | 0.2626% | 125.3782 | 1.941% | 958 | 6444.0357 | 6335.6218 | 1.711% | 0.2678%
2017-03-09 | 14 | 6461 | 108.4139 | 1.678% | 16.9643 | 0.2626% | 125.3782 | 1.941% | 959 | 6444.0357 | 6335.6218 | 1.711% | 0.2678%
2017-04-07 | 20 | 6461 | 108.4139 | 1.678% | 16.9643 | 0.2626% | 125.3782 | 1.941% | 960 | 6444.0357 | 6335.6218 | 1.711% | 0.2678%
2017-05-27 | 10 | 6463 | 108.4212 | 1.678% | 16.9686 | 0.2625% | 125.3898 | 1.94% | 961 | 6446.0314 | 6337.6102 | 1.711% | 0.2677%
2017-04-06 | 14 | 6464 | 108.4249 | 1.677% | 16.9707 | 0.2625% | 125.3956 | 1.94% | 962 | 6447.0293 | 6338.6044 | 1.711% | 0.2677%
2017-03-29 | 10 | 6466 | 108.4322 | 1.677% | 16.975 | 0.2625% | 125.4072 | 1.939% | 963 | 6449.025 | 6340.5928 | 1.71% | 0.2677%
2017-03-30 | 14 | 6467 | 108.4358 | 1.677% | 16.9772 | 0.2625% | 125.413 | 1.939% | 964 | 6450.0228 | 6341.587 | 1.71% | 0.2677%
2017-05-10 | 24 | 6468 | 108.4395 | 1.677% | 16.9793 | 0.2625% | 125.4188 | 1.939% | 965 | 6451.0207 | 6342.5812 | 1.71% | 0.2677%
2017-04-06 | 18 | 6469 | 108.4432 | 1.676% | 16.9814 | 0.2625% | 125.4246 | 1.939% | 966 | 6452.0186 | 6343.5754 | 1.709% | 0.2677%
2017-03-24 | 14 | 6471 | 108.4505 | 1.676% | 16.9857 | 0.2625% | 125.4362 | 1.938% | 967 | 6454.0143 | 6345.5638 | 1.709% | 0.2677%
2017-04-19 | 11 | 6471 | 108.4505 | 1.676% | 16.9857 | 0.2625% | 125.4362 | 1.938% | 968 | 6454.0143 | 6345.5638 | 1.709% | 0.2677%
2017-05-09 | 13 | 6471 | 108.4505 | 1.676% | 16.9857 | 0.2625% | 125.4362 | 1.938% | 969 | 6454.0143 | 6345.5638 | 1.709% | 0.2677%
2017-04-01 | 18 | 6473 | 108.4578 | 1.676% | 16.99 | 0.2625% | 125.4478 | 1.938% | 970 | 6456.01 | 6347.5522 | 1.709% | 0.2677%
2017-03-30 | 11 | 6474 | 108.4615 | 1.675% | 16.9921 | 0.2625% | 125.4536 | 1.938% | 971 | 6457.0079 | 6348.5464 | 1.708% | 0.2677%
2017-03-28 | 12 | 6475 | 108.4652 | 1.675% | 16.9943 | 0.2625% | 125.4594 | 1.938% | 972 | 6458.0057 | 6349.5406 | 1.708% | 0.2676%
2017-04-06 | 8 | 6476 | 108.4688 | 1.675% | 16.9964 | 0.2625% | 125.4652 | 1.937% | 973 | 6459.0036 | 6350.5348 | 1.708% | 0.2676%
2017-05-09 | 15 | 6477 | 108.4725 | 1.675% | 16.9986 | 0.2624% | 125.471 | 1.937% | 974 | 6460.0014 | 6351.529 | 1.708% | 0.2676%
2017-03-23 | 4 | 6478 | 108.4761 | 1.675% | 17.0007 | 0.2624% | 125.4768 | 1.937% | 975 | 6460.9993 | 6352.5232 | 1.708% | 0.2676%
2017-03-08 | 18 | 6479 | 108.4798 | 1.674% | 17.0028 | 0.2624% | 125.4826 | 1.937% | 976 | 6461.9972 | 6353.5174 | 1.707% | 0.2676%
2017-04-25 | 8 | 6479 | 108.4798 | 1.674% | 17.0028 | 0.2624% | 125.4826 | 1.937% | 977 | 6461.9972 | 6353.5174 | 1.707% | 0.2676%
2017-05-09 | 14 | 6479 | 108.4798 | 1.674% | 17.0028 | 0.2624% | 125.4826 | 1.937% | 978 | 6461.9972 | 6353.5174 | 1.707% | 0.2676%
2017-04-06 | 13 | 6481 | 108.4871 | 1.674% | 17.0071 | 0.2624% | 125.4943 | 1.936% | 979 | 6463.9929 | 6355.5057 | 1.707% | 0.2676%
2017-05-25 | 23 | 6481 | 108.4871 | 1.674% | 17.0071 | 0.2624% | 125.4943 | 1.936% | 980 | 6463.9929 | 6355.5057 | 1.707% | 0.2676%
2017-03-10 | 13 | 6482 | 108.4908 | 1.674% | 17.0093 | 0.2624% | 125.5001 | 1.936% | 981 | 6464.9907 | 6356.4999 | 1.707% | 0.2676%
2017-04-01 | 19 | 6482 | 108.4908 | 1.674% | 17.0093 | 0.2624% | 125.5001 | 1.936% | 982 | 6464.9907 | 6356.4999 | 1.707% | 0.2676%
2017-04-15 | 23 | 6482 | 108.4908 | 1.674% | 17.0093 | 0.2624% | 125.5001 | 1.936% | 983 | 6464.9907 | 6356.4999 | 1.707% | 0.2676%
2017-05-19 | 7 | 6483 | 108.4945 | 1.674% | 17.0114 | 0.2624% | 125.5059 | 1.936% | 984 | 6465.9886 | 6357.4941 | 1.707% | 0.2676%
2017-05-31 | 1 | 6484 | 108.4981 | 1.673% | 17.0135 | 0.2624% | 125.5117 | 1.936% | 985 | 6466.9865 | 6358.4883 | 1.706% | 0.2676%
2017-03-22 | 9 | 6485 | 108.5018 | 1.673% | 17.0157 | 0.2624% | 125.5175 | 1.936% | 986 | 6467.9843 | 6359.4825 | 1.706% | 0.2676%
2017-03-08 | 10 | 6486 | 108.5055 | 1.673% | 17.0178 | 0.2624% | 125.5233 | 1.935% | 987 | 6468.9822 | 6360.4767 | 1.706% | 0.2676%
2017-05-23 | 7 | 6486 | 108.5055 | 1.673% | 17.0178 | 0.2624% | 125.5233 | 1.935% | 988 | 6468.9822 | 6360.4767 | 1.706% | 0.2676%
2017-03-30 | 10 | 6488 | 108.5128 | 1.673% | 17.0221 | 0.2624% | 125.5349 | 1.935% | 989 | 6470.9779 | 6362.4651 | 1.706% | 0.2675%
2017-03-21 | 23 | 6489 | 108.5164 | 1.672% | 17.0242 | 0.2624% | 125.5407 | 1.935% | 990 | 6471.9758 | 6363.4593 | 1.705% | 0.2675%
2017-03-08 | 9 | 6490 | 108.5201 | 1.672% | 17.0264 | 0.2623% | 125.5465 | 1.934% | 991 | 6472.9736 | 6364.4535 | 1.705% | 0.2675%
2017-03-20 | 16 | 6490 | 108.5201 | 1.672% | 17.0264 | 0.2623% | 125.5465 | 1.934% | 992 | 6472.9736 | 6364.4535 | 1.705% | 0.2675%
2017-03-03 | 15 | 6491 | 108.5238 | 1.672% | 17.0285 | 0.2623% | 125.5523 | 1.934% | 993 | 6473.9715 | 6365.4477 | 1.705% | 0.2675%
2017-05-08 | 14 | 6491 | 108.5238 | 1.672% | 17.0285 | 0.2623% | 125.5523 | 1.934% | 994 | 6473.9715 | 6365.4477 | 1.705% | 0.2675%
2017-03-08 | 8 | 6493 | 108.5311 | 1.672% | 17.0328 | 0.2623% | 125.5639 | 1.934% | 995 | 6475.9672 | 6367.4361 | 1.704% | 0.2675%
2017-03-18 | 7 | 6494 | 108.5348 | 1.671% | 17.0349 | 0.2623% | 125.5697 | 1.934% | 996 | 6476.9651 | 6368.4303 | 1.704% | 0.2675%
2017-03-19 | 16 | 6494 | 108.5348 | 1.671% | 17.0349 | 0.2623% | 125.5697 | 1.934% | 997 | 6476.9651 | 6368.4303 | 1.704% | 0.2675%
2017-03-20 | 18 | 6494 | 108.5348 | 1.671% | 17.0349 | 0.2623% | 125.5697 | 1.934% | 998 | 6476.9651 | 6368.4303 | 1.704% | 0.2675%
2017-05-29 | 9 | 6495 | 108.5384 | 1.671% | 17.0371 | 0.2623% | 125.5755 | 1.933% | 999 | 6477.9629 | 6369.4245 | 1.704% | 0.2675%
2017-03-18 | 20 | 6499 | 108.5531 | 1.67% | 17.0456 | 0.2623% | 125.5987 | 1.933% | 1000 | 6481.9544 | 6373.4013 | 1.703% | 0.2674%
2017-03-09 | 13 | 6503 | 108.5677 | 1.67% | 17.0542 | 0.2623% | 125.6219 | 1.932% | 1001 | 6485.9458 | 6377.3781 | 1.702% | 0.2674%
2017-03-24 | 21 | 6503 | 108.5677 | 1.67% | 17.0542 | 0.2623% | 125.6219 | 1.932% | 1002 | 6485.9458 | 6377.3781 | 1.702% | 0.2674%
2017-04-03 | 12 | 6503 | 108.5677 | 1.67% | 17.0542 | 0.2623% | 125.6219 | 1.932% | 1003 | 6485.9458 | 6377.3781 | 1.702% | 0.2674%
2017-05-03 | 10 | 6503 | 108.5677 | 1.67% | 17.0542 | 0.2623% | 125.6219 | 1.932% | 1004 | 6485.9458 | 6377.3781 | 1.702% | 0.2674%
2017-03-01 | 8 | 6504 | 108.5714 | 1.669% | 17.0563 | 0.2622% | 125.6277 | 1.932% | 1005 | 6486.9437 | 6378.3723 | 1.702% | 0.2674%
2017-05-18 | 7 | 6504 | 108.5714 | 1.669% | 17.0563 | 0.2622% | 125.6277 | 1.932% | 1006 | 6486.9437 | 6378.3723 | 1.702% | 0.2674%
2017-04-03 | 9 | 6506 | 108.5787 | 1.669% | 17.0606 | 0.2622% | 125.6393 | 1.931% | 1007 | 6488.9394 | 6380.3607 | 1.702% | 0.2674%
2017-04-25 | 9 | 6507 | 108.5824 | 1.669% | 17.0628 | 0.2622% | 125.6451 | 1.931% | 1008 | 6489.9372 | 6381.3549 | 1.702% | 0.2674%
2017-03-19 | 19 | 6508 | 108.586 | 1.669% | 17.0649 | 0.2622% | 125.6509 | 1.931% | 1009 | 6490.9351 | 6382.3491 | 1.701% | 0.2674%
2017-03-06 | 15 | 6513 | 108.6044 | 1.668% | 17.0756 | 0.2622% | 125.68 | 1.93% | 1010 | 6495.9244 | 6387.32 | 1.7% | 0.2673%
2017-05-12 | 10 | 6514 | 108.608 | 1.667% | 17.0777 | 0.2622% | 125.6858 | 1.929% | 1011 | 6496.9223 | 6388.3142 | 1.7% | 0.2673%
2017-03-28 | 11 | 6515 | 108.6117 | 1.667% | 17.0799 | 0.2622% | 125.6916 | 1.929% | 1012 | 6497.9201 | 6389.3084 | 1.7% | 0.2673%
2017-03-22 | 10 | 6516 | 108.6154 | 1.667% | 17.082 | 0.2622% | 125.6974 | 1.929% | 1013 | 6498.918 | 6390.3026 | 1.7% | 0.2673%
2017-03-23 | 17 | 6517 | 108.619 | 1.667% | 17.0842 | 0.2621% | 125.7032 | 1.929% | 1014 | 6499.9158 | 6391.2968 | 1.699% | 0.2673%
2017-03-02 | 18 | 6518 | 108.6227 | 1.667% | 17.0863 | 0.2621% | 125.709 | 1.929% | 1015 | 6500.9137 | 6392.291 | 1.699% | 0.2673%
2017-05-09 | 16 | 6520 | 108.63 | 1.666% | 17.0906 | 0.2621% | 125.7206 | 1.928% | 1016 | 6502.9094 | 6394.2794 | 1.699% | 0.2673%
2017-04-11 | 23 | 6522 | 108.6373 | 1.666% | 17.0949 | 0.2621% | 125.7322 | 1.928% | 1017 | 6504.9051 | 6396.2678 | 1.698% | 0.2673%
2017-03-26 | 20 | 6523 | 108.641 | 1.666% | 17.097 | 0.2621% | 125.738 | 1.928% | 1018 | 6505.903 | 6397.262 | 1.698% | 0.2673%
2017-04-09 | 21 | 6523 | 108.641 | 1.666% | 17.097 | 0.2621% | 125.738 | 1.928% | 1019 | 6505.903 | 6397.262 | 1.698% | 0.2673%
2017-05-12 | 13 | 6523 | 108.641 | 1.666% | 17.097 | 0.2621% | 125.738 | 1.928% | 1020 | 6505.903 | 6397.262 | 1.698% | 0.2673%
2017-03-20 | 19 | 6524 | 108.6447 | 1.665% | 17.0991 | 0.2621% | 125.7438 | 1.927% | 1021 | 6506.9009 | 6398.2562 | 1.698% | 0.2672%
2017-03-22 | 8 | 6524 | 108.6447 | 1.665% | 17.0991 | 0.2621% | 125.7438 | 1.927% | 1022 | 6506.9009 | 6398.2562 | 1.698% | 0.2672%
2017-05-15 | 9 | 6526 | 108.652 | 1.665% | 17.1034 | 0.2621% | 125.7554 | 1.927% | 1023 | 6508.8966 | 6400.2446 | 1.698% | 0.2672%
2017-05-19 | 1 | 6526 | 108.652 | 1.665% | 17.1034 | 0.2621% | 125.7554 | 1.927% | 1024 | 6508.8966 | 6400.2446 | 1.698% | 0.2672%
2017-04-30 | 1 | 6527 | 108.6557 | 1.665% | 17.1056 | 0.2621% | 125.7612 | 1.927% | 1025 | 6509.8944 | 6401.2388 | 1.697% | 0.2672%
2017-05-11 | 8 | 6529 | 108.663 | 1.664% | 17.1098 | 0.2621% | 125.7728 | 1.926% | 1026 | 6511.8902 | 6403.2272 | 1.697% | 0.2672%
2017-04-06 | 19 | 6530 | 108.6666 | 1.664% | 17.112 | 0.2621% | 125.7786 | 1.926% | 1027 | 6512.888 | 6404.2214 | 1.697% | 0.2672%
2017-03-29 | 11 | 6531 | 108.6703 | 1.664% | 17.1141 | 0.262% | 125.7844 | 1.926% | 1028 | 6513.8859 | 6405.2156 | 1.697% | 0.2672%
2017-04-04 | 10 | 6531 | 108.6703 | 1.664% | 17.1141 | 0.262% | 125.7844 | 1.926% | 1029 | 6513.8859 | 6405.2156 | 1.697% | 0.2672%
2017-04-10 | 13 | 6532 | 108.674 | 1.664% | 17.1163 | 0.262% | 125.7902 | 1.926% | 1030 | 6514.8837 | 6406.2098 | 1.696% | 0.2672%
2017-05-05 | 22 | 6533 | 108.6776 | 1.664% | 17.1184 | 0.262% | 125.796 | 1.926% | 1031 | 6515.8816 | 6407.204 | 1.696% | 0.2672%
2017-03-23 | 16 | 6534 | 108.6813 | 1.663% | 17.1205 | 0.262% | 125.8018 | 1.925% | 1032 | 6516.8795 | 6408.1982 | 1.696% | 0.2672%
2017-04-20 | 10 | 6535 | 108.685 | 1.663% | 17.1227 | 0.262% | 125.8076 | 1.925% | 1033 | 6517.8773 | 6409.1924 | 1.696% | 0.2672%
2017-05-11 | 24 | 6536 | 108.6886 | 1.663% | 17.1248 | 0.262% | 125.8134 | 1.925% | 1034 | 6518.8752 | 6410.1866 | 1.696% | 0.2671%
2017-03-31 | 11 | 6538 | 108.696 | 1.663% | 17.1291 | 0.262% | 125.825 | 1.925% | 1035 | 6520.8709 | 6412.175 | 1.695% | 0.2671%
2017-05-12 | 14 | 6538 | 108.696 | 1.663% | 17.1291 | 0.262% | 125.825 | 1.925% | 1036 | 6520.8709 | 6412.175 | 1.695% | 0.2671%
2017-04-24 | 9 | 6540 | 108.7033 | 1.662% | 17.1334 | 0.262% | 125.8366 | 1.924% | 1037 | 6522.8666 | 6414.1634 | 1.695% | 0.2671%
2017-03-31 | 22 | 6541 | 108.7069 | 1.662% | 17.1355 | 0.262% | 125.8425 | 1.924% | 1038 | 6523.8645 | 6415.1575 | 1.695% | 0.2671%
2017-04-22 | 10 | 6544 | 108.7179 | 1.661% | 17.1419 | 0.2619% | 125.8599 | 1.923% | 1039 | 6526.8581 | 6418.1401 | 1.694% | 0.2671%
2017-05-08 | 15 | 6545 | 108.7216 | 1.661% | 17.1441 | 0.2619% | 125.8657 | 1.923% | 1040 | 6527.8559 | 6419.1343 | 1.694% | 0.2671%
2017-03-02 | 8 | 6546 | 108.7253 | 1.661% | 17.1462 | 0.2619% | 125.8715 | 1.923% | 1041 | 6528.8538 | 6420.1285 | 1.694% | 0.2671%
2017-04-10 | 9 | 6546 | 108.7253 | 1.661% | 17.1462 | 0.2619% | 125.8715 | 1.923% | 1042 | 6528.8538 | 6420.1285 | 1.694% | 0.2671%
2017-05-12 | 22 | 6547 | 108.7289 | 1.661% | 17.1484 | 0.2619% | 125.8773 | 1.923% | 1043 | 6529.8516 | 6421.1227 | 1.693% | 0.2671%
2017-03-21 | 13 | 6548 | 108.7326 | 1.661% | 17.1505 | 0.2619% | 125.8831 | 1.922% | 1044 | 6530.8495 | 6422.1169 | 1.693% | 0.2671%
2017-05-18 | 1 | 6550 | 108.7399 | 1.66% | 17.1548 | 0.2619% | 125.8947 | 1.922% | 1045 | 6532.8452 | 6424.1053 | 1.693% | 0.267%
2017-03-26 | 22 | 6551 | 108.7436 | 1.66% | 17.1569 | 0.2619% | 125.9005 | 1.922% | 1046 | 6533.8431 | 6425.0995 | 1.692% | 0.267%
2017-04-06 | 9 | 6551 | 108.7436 | 1.66% | 17.1569 | 0.2619% | 125.9005 | 1.922% | 1047 | 6533.8431 | 6425.0995 | 1.692% | 0.267%
2017-04-10 | 14 | 6552 | 108.7472 | 1.66% | 17.159 | 0.2619% | 125.9063 | 1.922% | 1048 | 6534.841 | 6426.0937 | 1.692% | 0.267%
2017-03-07 | 11 | 6553 | 108.7509 | 1.66% | 17.1612 | 0.2619% | 125.9121 | 1.921% | 1049 | 6535.8388 | 6427.0879 | 1.692% | 0.267%
2017-05-14 | 23 | 6553 | 108.7509 | 1.66% | 17.1612 | 0.2619% | 125.9121 | 1.921% | 1050 | 6535.8388 | 6427.0879 | 1.692% | 0.267%
2017-04-14 | 14 | 6554 | 108.7546 | 1.659% | 17.1633 | 0.2619% | 125.9179 | 1.921% | 1051 | 6536.8367 | 6428.0821 | 1.692% | 0.267%
2017-04-19 | 12 | 6554 | 108.7546 | 1.659% | 17.1633 | 0.2619% | 125.9179 | 1.921% | 1052 | 6536.8367 | 6428.0821 | 1.692% | 0.267%
2017-04-01 | 21 | 6555 | 108.7582 | 1.659% | 17.1655 | 0.2619% | 125.9237 | 1.921% | 1053 | 6537.8345 | 6429.0763 | 1.692% | 0.267%
2017-05-21 | 11 | 6557 | 108.7656 | 1.659% | 17.1697 | 0.2619% | 125.9353 | 1.921% | 1054 | 6539.8303 | 6431.0647 | 1.691% | 0.267%
2017-04-23 | 21 | 6558 | 108.7692 | 1.659% | 17.1719 | 0.2618% | 125.9411 | 1.92% | 1055 | 6540.8281 | 6432.0589 | 1.691% | 0.267%
2017-04-10 | 8 | 6560 | 108.7765 | 1.658% | 17.1762 | 0.2618% | 125.9527 | 1.92% | 1056 | 6542.8238 | 6434.0473 | 1.691% | 0.267%
2017-04-27 | 24 | 6560 | 108.7765 | 1.658% | 17.1762 | 0.2618% | 125.9527 | 1.92% | 1057 | 6542.8238 | 6434.0473 | 1.691% | 0.267%
2017-03-02 | 12 | 6561 | 108.7802 | 1.658% | 17.1783 | 0.2618% | 125.9585 | 1.92% | 1058 | 6543.8217 | 6435.0415 | 1.69% | 0.2669%
2017-04-28 | 7 | 6562 | 108.7839 | 1.658% | 17.1804 | 0.2618% | 125.9643 | 1.92% | 1059 | 6544.8196 | 6436.0357 | 1.69% | 0.2669%
2017-03-23 | 18 | 6563 | 108.7875 | 1.658% | 17.1826 | 0.2618% | 125.9701 | 1.919% | 1060 | 6545.8174 | 6437.0299 | 1.69% | 0.2669%
2017-04-27 | 9 | 6563 | 108.7875 | 1.658% | 17.1826 | 0.2618% | 125.9701 | 1.919% | 1061 | 6545.8174 | 6437.0299 | 1.69% | 0.2669%
2017-04-03 | 8 | 6565 | 108.7949 | 1.657% | 17.1869 | 0.2618% | 125.9817 | 1.919% | 1062 | 6547.8131 | 6439.0183 | 1.69% | 0.2669%
2017-05-12 | 12 | 6565 | 108.7949 | 1.657% | 17.1869 | 0.2618% | 125.9817 | 1.919% | 1063 | 6547.8131 | 6439.0183 | 1.69% | 0.2669%
2017-03-20 | 23 | 6566 | 108.7985 | 1.657% | 17.189 | 0.2618% | 125.9875 | 1.919% | 1064 | 6548.811 | 6440.0125 | 1.689% | 0.2669%
2017-04-03 | 13 | 6567 | 108.8022 | 1.657% | 17.1911 | 0.2618% | 125.9933 | 1.919% | 1065 | 6549.8089 | 6441.0067 | 1.689% | 0.2669%
2017-05-12 | 20 | 6567 | 108.8022 | 1.657% | 17.1911 | 0.2618% | 125.9933 | 1.919% | 1066 | 6549.8089 | 6441.0067 | 1.689% | 0.2669%
2017-03-02 | 24 | 6568 | 108.8059 | 1.657% | 17.1933 | 0.2618% | 125.9991 | 1.918% | 1067 | 6550.8067 | 6442.0009 | 1.689% | 0.2669%
2017-03-03 | 14 | 6568 | 108.8059 | 1.657% | 17.1933 | 0.2618% | 125.9991 | 1.918% | 1068 | 6550.8067 | 6442.0009 | 1.689% | 0.2669%
2017-04-18 | 10 | 6569 | 108.8095 | 1.656% | 17.1954 | 0.2618% | 126.0049 | 1.918% | 1069 | 6551.8046 | 6442.9951 | 1.689% | 0.2669%
2017-03-01 | 9 | 6570 | 108.8132 | 1.656% | 17.1976 | 0.2618% | 126.0107 | 1.918% | 1070 | 6552.8024 | 6443.9893 | 1.689% | 0.2669%
2017-03-21 | 14 | 6570 | 108.8132 | 1.656% | 17.1976 | 0.2618% | 126.0107 | 1.918% | 1071 | 6552.8024 | 6443.9893 | 1.689% | 0.2669%
2017-03-04 | 14 | 6572 | 108.8205 | 1.656% | 17.2018 | 0.2617% | 126.0224 | 1.918% | 1072 | 6554.7982 | 6445.9776 | 1.688% | 0.2669%
2017-04-30 | 24 | 6574 | 108.8278 | 1.655% | 17.2061 | 0.2617% | 126.034 | 1.917% | 1073 | 6556.7939 | 6447.966 | 1.688% | 0.2668%
2017-04-12 | 11 | 6576 | 108.8352 | 1.655% | 17.2104 | 0.2617% | 126.0456 | 1.917% | 1074 | 6558.7896 | 6449.9544 | 1.687% | 0.2668%
2017-03-03 | 4 | 6577 | 108.8388 | 1.655% | 17.2125 | 0.2617% | 126.0514 | 1.917% | 1075 | 6559.7875 | 6450.9486 | 1.687% | 0.2668%
2017-03-10 | 12 | 6577 | 108.8388 | 1.655% | 17.2125 | 0.2617% | 126.0514 | 1.917% | 1076 | 6559.7875 | 6450.9486 | 1.687% | 0.2668%
2017-04-07 | 13 | 6578 | 108.8425 | 1.655% | 17.2147 | 0.2617% | 126.0572 | 1.916% | 1077 | 6560.7853 | 6451.9428 | 1.687% | 0.2668%
2017-04-26 | 11 | 6579 | 108.8462 | 1.654% | 17.2168 | 0.2617% | 126.063 | 1.916% | 1078 | 6561.7832 | 6452.937 | 1.687% | 0.2668%
2017-03-11 | 14 | 6581 | 108.8535 | 1.654% | 17.2211 | 0.2617% | 126.0746 | 1.916% | 1079 | 6563.7789 | 6454.9254 | 1.686% | 0.2668%
2017-03-18 | 21 | 6581 | 108.8535 | 1.654% | 17.2211 | 0.2617% | 126.0746 | 1.916% | 1080 | 6563.7789 | 6454.9254 | 1.686% | 0.2668%
2017-05-01 | 7 | 6581 | 108.8535 | 1.654% | 17.2211 | 0.2617% | 126.0746 | 1.916% | 1081 | 6563.7789 | 6454.9254 | 1.686% | 0.2668%
2017-04-04 | 23 | 6583 | 108.8608 | 1.654% | 17.2254 | 0.2617% | 126.0862 | 1.915% | 1082 | 6565.7746 | 6456.9138 | 1.686% | 0.2668%
2017-04-25 | 10 | 6583 | 108.8608 | 1.654% | 17.2254 | 0.2617% | 126.0862 | 1.915% | 1083 | 6565.7746 | 6456.9138 | 1.686% | 0.2668%
2017-05-25 | 8 | 6583 | 108.8608 | 1.654% | 17.2254 | 0.2617% | 126.0862 | 1.915% | 1084 | 6565.7746 | 6456.9138 | 1.686% | 0.2668%
2017-03-21 | 12 | 6585 | 108.8681 | 1.653% | 17.2297 | 0.2617% | 126.0978 | 1.915% | 1085 | 6567.7703 | 6458.9022 | 1.686% | 0.2668%
2017-05-12 | 11 | 6587 | 108.8755 | 1.653% | 17.2339 | 0.2616% | 126.1094 | 1.915% | 1086 | 6569.7661 | 6460.8906 | 1.685% | 0.2667%
2017-03-09 | 12 | 6588 | 108.8791 | 1.653% | 17.2361 | 0.2616% | 126.1152 | 1.914% | 1087 | 6570.7639 | 6461.8848 | 1.685% | 0.2667%
2017-05-15 | 24 | 6588 | 108.8791 | 1.653% | 17.2361 | 0.2616% | 126.1152 | 1.914% | 1088 | 6570.7639 | 6461.8848 | 1.685% | 0.2667%
2017-03-02 | 9 | 6590 | 108.8865 | 1.652% | 17.2404 | 0.2616% | 126.1268 | 1.914% | 1089 | 6572.7596 | 6463.8732 | 1.685% | 0.2667%
2017-04-07 | 23 | 6591 | 108.8901 | 1.652% | 17.2425 | 0.2616% | 126.1326 | 1.914% | 1090 | 6573.7575 | 6464.8674 | 1.684% | 0.2667%
2017-04-22 | 23 | 6595 | 108.9048 | 1.651% | 17.2511 | 0.2616% | 126.1558 | 1.913% | 1091 | 6577.7489 | 6468.8442 | 1.684% | 0.2667%
2017-03-22 | 12 | 6596 | 108.9084 | 1.651% | 17.2532 | 0.2616% | 126.1616 | 1.913% | 1092 | 6578.7468 | 6469.8384 | 1.683% | 0.2667%
2017-04-02 | 21 | 6597 | 108.9121 | 1.651% | 17.2553 | 0.2616% | 126.1674 | 1.912% | 1093 | 6579.7447 | 6470.8326 | 1.683% | 0.2667%
2017-04-09 | 8 | 6600 | 108.9231 | 1.65% | 17.2618 | 0.2615% | 126.1848 | 1.912% | 1094 | 6582.7382 | 6473.8152 | 1.683% | 0.2666%
2017-05-14 | 15 | 6600 | 108.9231 | 1.65% | 17.2618 | 0.2615% | 126.1848 | 1.912% | 1095 | 6582.7382 | 6473.8152 | 1.683% | 0.2666%
2017-03-29 | 12 | 6601 | 108.9267 | 1.65% | 17.2639 | 0.2615% | 126.1907 | 1.912% | 1096 | 6583.7361 | 6474.8093 | 1.682% | 0.2666%
2017-05-12 | 15 | 6603 | 108.9341 | 1.65% | 17.2682 | 0.2615% | 126.2023 | 1.911% | 1097 | 6585.7318 | 6476.7977 | 1.682% | 0.2666%
2017-04-11 | 12 | 6605 | 108.9414 | 1.649% | 17.2725 | 0.2615% | 126.2139 | 1.911% | 1098 | 6587.7275 | 6478.7861 | 1.682% | 0.2666%
2017-03-12 | 4 | 6608 | 108.9524 | 1.649% | 17.2789 | 0.2615% | 126.2313 | 1.91% | 1099 | 6590.7211 | 6481.7687 | 1.681% | 0.2666%
2017-03-20 | 15 | 6609 | 108.9561 | 1.649% | 17.281 | 0.2615% | 126.2371 | 1.91% | 1100 | 6591.719 | 6482.7629 | 1.681% | 0.2666%
2017-03-09 | 22 | 6610 | 108.9597 | 1.648% | 17.2832 | 0.2615% | 126.2429 | 1.91% | 1101 | 6592.7168 | 6483.7571 | 1.681% | 0.2666%
2017-03-29 | 13 | 6610 | 108.9597 | 1.648% | 17.2832 | 0.2615% | 126.2429 | 1.91% | 1102 | 6592.7168 | 6483.7571 | 1.681% | 0.2666%
2017-03-31 | 10 | 6610 | 108.9597 | 1.648% | 17.2832 | 0.2615% | 126.2429 | 1.91% | 1103 | 6592.7168 | 6483.7571 | 1.681% | 0.2666%
2017-04-04 | 11 | 6611 | 108.9634 | 1.648% | 17.2853 | 0.2615% | 126.2487 | 1.91% | 1104 | 6593.7147 | 6484.7513 | 1.68% | 0.2666%
2017-04-05 | 11 | 6611 | 108.9634 | 1.648% | 17.2853 | 0.2615% | 126.2487 | 1.91% | 1105 | 6593.7147 | 6484.7513 | 1.68% | 0.2666%
2017-04-06 | 12 | 6612 | 108.967 | 1.648% | 17.2874 | 0.2615% | 126.2545 | 1.909% | 1106 | 6594.7126 | 6485.7455 | 1.68% | 0.2665%
2017-05-12 | 16 | 6612 | 108.967 | 1.648% | 17.2874 | 0.2615% | 126.2545 | 1.909% | 1107 | 6594.7126 | 6485.7455 | 1.68% | 0.2665%
2017-03-22 | 11 | 6613 | 108.9707 | 1.648% | 17.2896 | 0.2614% | 126.2603 | 1.909% | 1108 | 6595.7104 | 6486.7397 | 1.68% | 0.2665%
2017-05-12 | 19 | 6613 | 108.9707 | 1.648% | 17.2896 | 0.2614% | 126.2603 | 1.909% | 1109 | 6595.7104 | 6486.7397 | 1.68% | 0.2665%
2017-04-10 | 15 | 6614 | 108.9744 | 1.648% | 17.2917 | 0.2614% | 126.2661 | 1.909% | 1110 | 6596.7083 | 6487.7339 | 1.68% | 0.2665%
2017-04-25 | 11 | 6615 | 108.978 | 1.647% | 17.2939 | 0.2614% | 126.2719 | 1.909% | 1111 | 6597.7061 | 6488.7281 | 1.679% | 0.2665%
2017-03-10 | 7 | 6617 | 108.9854 | 1.647% | 17.2981 | 0.2614% | 126.2835 | 1.908% | 1112 | 6599.7019 | 6490.7165 | 1.679% | 0.2665%
2017-03-28 | 13 | 6617 | 108.9854 | 1.647% | 17.2981 | 0.2614% | 126.2835 | 1.908% | 1113 | 6599.7019 | 6490.7165 | 1.679% | 0.2665%
2017-03-06 | 18 | 6619 | 108.9927 | 1.647% | 17.3024 | 0.2614% | 126.2951 | 1.908% | 1114 | 6601.6976 | 6492.7049 | 1.679% | 0.2665%
2017-03-24 | 13 | 6619 | 108.9927 | 1.647% | 17.3024 | 0.2614% | 126.2951 | 1.908% | 1115 | 6601.6976 | 6492.7049 | 1.679% | 0.2665%
2017-04-06 | 10 | 6620 | 108.9964 | 1.646% | 17.3046 | 0.2614% | 126.3009 | 1.908% | 1116 | 6602.6954 | 6493.6991 | 1.678% | 0.2665%
2017-05-24 | 8 | 6621 | 109 | 1.646% | 17.3067 | 0.2614% | 126.3067 | 1.908% | 1117 | 6603.6933 | 6494.6933 | 1.678% | 0.2665%
2017-05-12 | 17 | 6627 | 109.022 | 1.645% | 17.3195 | 0.2613% | 126.3415 | 1.906% | 1118 | 6609.6805 | 6500.6585 | 1.677% | 0.2664%
2017-03-06 | 14 | 6628 | 109.0257 | 1.645% | 17.3217 | 0.2613% | 126.3473 | 1.906% | 1119 | 6610.6783 | 6501.6527 | 1.677% | 0.2664%
2017-03-19 | 15 | 6629 | 109.0293 | 1.645% | 17.3238 | 0.2613% | 126.3531 | 1.906% | 1120 | 6611.6762 | 6502.6469 | 1.677% | 0.2664%
2017-03-11 | 4 | 6632 | 109.0403 | 1.644% | 17.3302 | 0.2613% | 126.3706 | 1.905% | 1121 | 6614.6698 | 6505.6294 | 1.676% | 0.2664%
2017-05-22 | 24 | 6632 | 109.0403 | 1.644% | 17.3302 | 0.2613% | 126.3706 | 1.905% | 1122 | 6614.6698 | 6505.6294 | 1.676% | 0.2664%
2017-03-31 | 13 | 6633 | 109.044 | 1.644% | 17.3324 | 0.2613% | 126.3764 | 1.905% | 1123 | 6615.6676 | 6506.6236 | 1.676% | 0.2664%
2017-05-02 | 8 | 6635 | 109.0513 | 1.644% | 17.3367 | 0.2613% | 126.388 | 1.905% | 1124 | 6617.6633 | 6508.612 | 1.675% | 0.2664%
2017-04-13 | 11 | 6639 | 109.066 | 1.643% | 17.3452 | 0.2613% | 126.4112 | 1.904% | 1125 | 6621.6548 | 6512.5888 | 1.675% | 0.2663%
2017-05-04 | 10 | 6641 | 109.0733 | 1.642% | 17.3495 | 0.2612% | 126.4228 | 1.904% | 1126 | 6623.6505 | 6514.5772 | 1.674% | 0.2663%
2017-03-07 | 22 | 6643 | 109.0806 | 1.642% | 17.3538 | 0.2612% | 126.4344 | 1.903% | 1127 | 6625.6462 | 6516.5656 | 1.674% | 0.2663%
2017-03-17 | 24 | 6643 | 109.0806 | 1.642% | 17.3538 | 0.2612% | 126.4344 | 1.903% | 1128 | 6625.6462 | 6516.5656 | 1.674% | 0.2663%
2017-04-19 | 13 | 6645 | 109.0879 | 1.642% | 17.3581 | 0.2612% | 126.446 | 1.903% | 1129 | 6627.6419 | 6518.554 | 1.673% | 0.2663%
2017-04-25 | 12 | 6645 | 109.0879 | 1.642% | 17.3581 | 0.2612% | 126.446 | 1.903% | 1130 | 6627.6419 | 6518.554 | 1.673% | 0.2663%
2017-03-21 | 11 | 6646 | 109.0916 | 1.641% | 17.3602 | 0.2612% | 126.4518 | 1.903% | 1131 | 6628.6398 | 6519.5482 | 1.673% | 0.2663%
2017-03-02 | 10 | 6647 | 109.0953 | 1.641% | 17.3623 | 0.2612% | 126.4576 | 1.902% | 1132 | 6629.6377 | 6520.5424 | 1.673% | 0.2663%
2017-03-27 | 13 | 6647 | 109.0953 | 1.641% | 17.3623 | 0.2612% | 126.4576 | 1.902% | 1133 | 6629.6377 | 6520.5424 | 1.673% | 0.2663%
2017-03-27 | 23 | 6649 | 109.1026 | 1.641% | 17.3666 | 0.2612% | 126.4692 | 1.902% | 1134 | 6631.6334 | 6522.5308 | 1.673% | 0.2663%
2017-03-12 | 5 | 6650 | 109.1063 | 1.641% | 17.3688 | 0.2612% | 126.475 | 1.902% | 1135 | 6632.6312 | 6523.525 | 1.673% | 0.2662%
2017-03-02 | 11 | 6652 | 109.1136 | 1.64% | 17.373 | 0.2612% | 126.4866 | 1.901% | 1136 | 6634.627 | 6525.5134 | 1.672% | 0.2662%
2017-04-25 | 13 | 6653 | 109.1173 | 1.64% | 17.3752 | 0.2612% | 126.4924 | 1.901% | 1137 | 6635.6248 | 6526.5076 | 1.672% | 0.2662%
2017-05-09 | 17 | 6659 | 109.1392 | 1.639% | 17.388 | 0.2611% | 126.5272 | 1.9% | 1138 | 6641.612 | 6532.4728 | 1.671% | 0.2662%
2017-03-21 | 15 | 6660 | 109.1429 | 1.639% | 17.3901 | 0.2611% | 126.533 | 1.9% | 1139 | 6642.6099 | 6533.467 | 1.671% | 0.2662%
2017-04-24 | 10 | 6662 | 109.1502 | 1.638% | 17.3944 | 0.2611% | 126.5447 | 1.899% | 1140 | 6644.6056 | 6535.4553 | 1.67% | 0.2662%
2017-05-05 | 8 | 6665 | 109.1612 | 1.638% | 17.4008 | 0.2611% | 126.5621 | 1.899% | 1141 | 6647.5992 | 6538.4379 | 1.67% | 0.2661%
2017-03-05 | 13 | 6666 | 109.1649 | 1.638% | 17.403 | 0.2611% | 126.5679 | 1.899% | 1142 | 6648.597 | 6539.4321 | 1.669% | 0.2661%
2017-03-10 | 23 | 6668 | 109.1722 | 1.637% | 17.4073 | 0.2611% | 126.5795 | 1.898% | 1143 | 6650.5927 | 6541.4205 | 1.669% | 0.2661%
2017-03-01 | 10 | 6670 | 109.1795 | 1.637% | 17.4115 | 0.261% | 126.5911 | 1.898% | 1144 | 6652.5885 | 6543.4089 | 1.669% | 0.2661%
2017-03-07 | 6 | 6671 | 109.1832 | 1.637% | 17.4137 | 0.261% | 126.5969 | 1.898% | 1145 | 6653.5863 | 6544.4031 | 1.668% | 0.2661%
2017-05-12 | 18 | 6672 | 109.1869 | 1.636% | 17.4158 | 0.261% | 126.6027 | 1.898% | 1146 | 6654.5842 | 6545.3973 | 1.668% | 0.2661%
2017-05-12 | 21 | 6672 | 109.1869 | 1.636% | 17.4158 | 0.261% | 126.6027 | 1.898% | 1147 | 6654.5842 | 6545.3973 | 1.668% | 0.2661%
2017-04-03 | 14 | 6674 | 109.1942 | 1.636% | 17.4201 | 0.261% | 126.6143 | 1.897% | 1148 | 6656.5799 | 6547.3857 | 1.668% | 0.2661%
2017-04-06 | 11 | 6676 | 109.2015 | 1.636% | 17.4244 | 0.261% | 126.6259 | 1.897% | 1149 | 6658.5756 | 6549.3741 | 1.667% | 0.266%
2017-04-12 | 23 | 6676 | 109.2015 | 1.636% | 17.4244 | 0.261% | 126.6259 | 1.897% | 1150 | 6658.5756 | 6549.3741 | 1.667% | 0.266%
2017-05-20 | 9 | 6676 | 109.2015 | 1.636% | 17.4244 | 0.261% | 126.6259 | 1.897% | 1151 | 6658.5756 | 6549.3741 | 1.667% | 0.266%
2017-03-17 | 17 | 6679 | 109.2125 | 1.635% | 17.4308 | 0.261% | 126.6433 | 1.896% | 1152 | 6661.5692 | 6552.3567 | 1.667% | 0.266%
2017-03-17 | 18 | 6679 | 109.2125 | 1.635% | 17.4308 | 0.261% | 126.6433 | 1.896% | 1153 | 6661.5692 | 6552.3567 | 1.667% | 0.266%
2017-03-18 | 15 | 6679 | 109.2125 | 1.635% | 17.4308 | 0.261% | 126.6433 | 1.896% | 1154 | 6661.5692 | 6552.3567 | 1.667% | 0.266%
2017-03-09 | 19 | 6682 | 109.2235 | 1.635% | 17.4372 | 0.261% | 126.6607 | 1.896% | 1155 | 6664.5628 | 6555.3393 | 1.666% | 0.266%
2017-03-08 | 22 | 6687 | 109.2418 | 1.634% | 17.4479 | 0.2609% | 126.6897 | 1.895% | 1156 | 6669.5521 | 6560.3103 | 1.665% | 0.266%
2017-04-08 | 11 | 6691 | 109.2565 | 1.633% | 17.4565 | 0.2609% | 126.7129 | 1.894% | 1157 | 6673.5435 | 6564.2871 | 1.664% | 0.2659%
2017-05-08 | 16 | 6692 | 109.2601 | 1.633% | 17.4586 | 0.2609% | 126.7187 | 1.894% | 1158 | 6674.5414 | 6565.2813 | 1.664% | 0.2659%
2017-04-03 | 22 | 6693 | 109.2638 | 1.633% | 17.4608 | 0.2609% | 126.7246 | 1.893% | 1159 | 6675.5392 | 6566.2754 | 1.664% | 0.2659%
2017-04-07 | 12 | 6693 | 109.2638 | 1.633% | 17.4608 | 0.2609% | 126.7246 | 1.893% | 1160 | 6675.5392 | 6566.2754 | 1.664% | 0.2659%
2017-03-11 | 18 | 6694 | 109.2675 | 1.632% | 17.4629 | 0.2609% | 126.7304 | 1.893% | 1161 | 6676.5371 | 6567.2696 | 1.664% | 0.2659%
2017-03-29 | 14 | 6695 | 109.2711 | 1.632% | 17.465 | 0.2609% | 126.7362 | 1.893% | 1162 | 6677.535 | 6568.2638 | 1.664% | 0.2659%
2017-03-30 | 22 | 6698 | 109.2821 | 1.632% | 17.4715 | 0.2608% | 126.7536 | 1.892% | 1163 | 6680.5285 | 6571.2464 | 1.663% | 0.2659%
2017-05-02 | 23 | 6698 | 109.2821 | 1.632% | 17.4715 | 0.2608% | 126.7536 | 1.892% | 1164 | 6680.5285 | 6571.2464 | 1.663% | 0.2659%
2017-04-21 | 24 | 6699 | 109.2858 | 1.631% | 17.4736 | 0.2608% | 126.7594 | 1.892% | 1165 | 6681.5264 | 6572.2406 | 1.663% | 0.2659%
2017-04-03 | 15 | 6700 | 109.2894 | 1.631% | 17.4757 | 0.2608% | 126.7652 | 1.892% | 1166 | 6682.5243 | 6573.2348 | 1.663% | 0.2659%
2017-03-31 | 20 | 6701 | 109.2931 | 1.631% | 17.4779 | 0.2608% | 126.771 | 1.892% | 1167 | 6683.5221 | 6574.229 | 1.662% | 0.2659%
2017-04-15 | 13 | 6701 | 109.2931 | 1.631% | 17.4779 | 0.2608% | 126.771 | 1.892% | 1168 | 6683.5221 | 6574.229 | 1.662% | 0.2659%
2017-04-24 | 16 | 6709 | 109.3224 | 1.629% | 17.495 | 0.2608% | 126.8174 | 1.89% | 1169 | 6691.505 | 6582.1826 | 1.661% | 0.2658%
2017-04-18 | 11 | 6711 | 109.3297 | 1.629% | 17.4993 | 0.2608% | 126.829 | 1.89% | 1170 | 6693.5007 | 6584.171 | 1.66% | 0.2658%
2017-04-21 | 9 | 6711 | 109.3297 | 1.629% | 17.4993 | 0.2608% | 126.829 | 1.89% | 1171 | 6693.5007 | 6584.171 | 1.66% | 0.2658%
2017-03-23 | 15 | 6716 | 109.348 | 1.628% | 17.51 | 0.2607% | 126.858 | 1.889% | 1172 | 6698.49 | 6589.142 | 1.66% | 0.2657%
2017-05-16 | 9 | 6716 | 109.348 | 1.628% | 17.51 | 0.2607% | 126.858 | 1.889% | 1173 | 6698.49 | 6589.142 | 1.66% | 0.2657%
2017-03-31 | 14 | 6718 | 109.3554 | 1.628% | 17.5143 | 0.2607% | 126.8696 | 1.889% | 1174 | 6700.4857 | 6591.1304 | 1.659% | 0.2657%
2017-04-19 | 14 | 6718 | 109.3554 | 1.628% | 17.5143 | 0.2607% | 126.8696 | 1.889% | 1175 | 6700.4857 | 6591.1304 | 1.659% | 0.2657%
2017-05-08 | 22 | 6718 | 109.3554 | 1.628% | 17.5143 | 0.2607% | 126.8696 | 1.889% | 1176 | 6700.4857 | 6591.1304 | 1.659% | 0.2657%
2017-05-26 | 10 | 6718 | 109.3554 | 1.628% | 17.5143 | 0.2607% | 126.8696 | 1.889% | 1177 | 6700.4857 | 6591.1304 | 1.659% | 0.2657%
2017-03-19 | 7 | 6721 | 109.3664 | 1.627% | 17.5207 | 0.2607% | 126.887 | 1.888% | 1178 | 6703.4793 | 6594.113 | 1.659% | 0.2657%
2017-04-05 | 22 | 6723 | 109.3737 | 1.627% | 17.525 | 0.2607% | 126.8987 | 1.888% | 1179 | 6705.475 | 6596.1013 | 1.658% | 0.2657%
2017-04-20 | 11 | 6724 | 109.3774 | 1.627% | 17.5271 | 0.2607% | 126.9045 | 1.887% | 1180 | 6706.4729 | 6597.0955 | 1.658% | 0.2657%
2017-04-16 | 13 | 6727 | 109.3883 | 1.626% | 17.5335 | 0.2606% | 126.9219 | 1.887% | 1181 | 6709.4665 | 6600.0781 | 1.657% | 0.2657%
2017-03-31 | 12 | 6728 | 109.392 | 1.626% | 17.5357 | 0.2606% | 126.9277 | 1.887% | 1182 | 6710.4643 | 6601.0723 | 1.657% | 0.2656%
2017-03-03 | 18 | 6729 | 109.3957 | 1.626% | 17.5378 | 0.2606% | 126.9335 | 1.886% | 1183 | 6711.4622 | 6602.0665 | 1.657% | 0.2656%
2017-04-17 | 11 | 6730 | 109.3993 | 1.626% | 17.5399 | 0.2606% | 126.9393 | 1.886% | 1184 | 6712.4601 | 6603.0607 | 1.657% | 0.2656%
2017-04-24 | 15 | 6730 | 109.3993 | 1.626% | 17.5399 | 0.2606% | 126.9393 | 1.886% | 1185 | 6712.4601 | 6603.0607 | 1.657% | 0.2656%
2017-03-23 | 19 | 6731 | 109.403 | 1.625% | 17.5421 | 0.2606% | 126.9451 | 1.886% | 1186 | 6713.4579 | 6604.0549 | 1.657% | 0.2656%
2017-05-31 | 7 | 6741 | 109.4396 | 1.623% | 17.5635 | 0.2605% | 127.0031 | 1.884% | 1187 | 6723.4365 | 6613.9969 | 1.655% | 0.2656%
2017-03-27 | 14 | 6744 | 109.4506 | 1.623% | 17.5699 | 0.2605% | 127.0205 | 1.883% | 1188 | 6726.4301 | 6616.9795 | 1.654% | 0.2655%
2017-04-10 | 16 | 6744 | 109.4506 | 1.623% | 17.5699 | 0.2605% | 127.0205 | 1.883% | 1189 | 6726.4301 | 6616.9795 | 1.654% | 0.2655%
2017-03-27 | 16 | 6745 | 109.4543 | 1.623% | 17.572 | 0.2605% | 127.0263 | 1.883% | 1190 | 6727.428 | 6617.9737 | 1.654% | 0.2655%
2017-05-03 | 11 | 6746 | 109.458 | 1.623% | 17.5742 | 0.2605% | 127.0321 | 1.883% | 1191 | 6728.4258 | 6618.9679 | 1.654% | 0.2655%
2017-03-24 | 2 | 6748 | 109.4653 | 1.622% | 17.5785 | 0.2605% | 127.0437 | 1.883% | 1192 | 6730.4215 | 6620.9563 | 1.653% | 0.2655%
2017-04-24 | 13 | 6748 | 109.4653 | 1.622% | 17.5785 | 0.2605% | 127.0437 | 1.883% | 1193 | 6730.4215 | 6620.9563 | 1.653% | 0.2655%
2017-03-12 | 1 | 6749 | 109.4689 | 1.622% | 17.5806 | 0.2605% | 127.0495 | 1.882% | 1194 | 6731.4194 | 6621.9505 | 1.653% | 0.2655%
2017-04-25 | 15 | 6752 | 109.4799 | 1.621% | 17.587 | 0.2605% | 127.0669 | 1.882% | 1195 | 6734.413 | 6624.9331 | 1.653% | 0.2655%
2017-04-06 | 22 | 6755 | 109.4909 | 1.621% | 17.5934 | 0.2605% | 127.0844 | 1.881% | 1196 | 6737.4066 | 6627.9156 | 1.652% | 0.2654%
2017-04-25 | 14 | 6756 | 109.4946 | 1.621% | 17.5956 | 0.2604% | 127.0902 | 1.881% | 1197 | 6738.4044 | 6628.9098 | 1.652% | 0.2654%
2017-03-10 | 19 | 6757 | 109.4983 | 1.621% | 17.5977 | 0.2604% | 127.096 | 1.881% | 1198 | 6739.4023 | 6629.904 | 1.652% | 0.2654%
2017-03-29 | 15 | 6758 | 109.5019 | 1.62% | 17.5999 | 0.2604% | 127.1018 | 1.881% | 1199 | 6740.4001 | 6630.8982 | 1.651% | 0.2654%
2017-03-24 | 1 | 6761 | 109.5129 | 1.62% | 17.6063 | 0.2604% | 127.1192 | 1.88% | 1200 | 6743.3937 | 6633.8808 | 1.651% | 0.2654%
2017-04-12 | 12 | 6765 | 109.5276 | 1.619% | 17.6148 | 0.2604% | 127.1424 | 1.879% | 1201 | 6747.3852 | 6637.8576 | 1.65% | 0.2654%
2017-03-22 | 23 | 6766 | 109.5312 | 1.619% | 17.617 | 0.2604% | 127.1482 | 1.879% | 1202 | 6748.383 | 6638.8518 | 1.65% | 0.2654%
2017-03-31 | 19 | 6766 | 109.5312 | 1.619% | 17.617 | 0.2604% | 127.1482 | 1.879% | 1203 | 6748.383 | 6638.8518 | 1.65% | 0.2654%
2017-04-03 | 16 | 6767 | 109.5349 | 1.619% | 17.6191 | 0.2604% | 127.154 | 1.879% | 1204 | 6749.3809 | 6639.846 | 1.65% | 0.2654%
2017-04-24 | 14 | 6767 | 109.5349 | 1.619% | 17.6191 | 0.2604% | 127.154 | 1.879% | 1205 | 6749.3809 | 6639.846 | 1.65% | 0.2654%
2017-03-30 | 20 | 6768 | 109.5385 | 1.618% | 17.6212 | 0.2604% | 127.1598 | 1.879% | 1206 | 6750.3788 | 6640.8402 | 1.649% | 0.2653%
2017-04-04 | 12 | 6769 | 109.5422 | 1.618% | 17.6234 | 0.2604% | 127.1656 | 1.879% | 1207 | 6751.3766 | 6641.8344 | 1.649% | 0.2653%
2017-04-06 | 20 | 6769 | 109.5422 | 1.618% | 17.6234 | 0.2604% | 127.1656 | 1.879% | 1208 | 6751.3766 | 6641.8344 | 1.649% | 0.2653%
2017-03-17 | 16 | 6770 | 109.5459 | 1.618% | 17.6255 | 0.2603% | 127.1714 | 1.878% | 1209 | 6752.3745 | 6642.8286 | 1.649% | 0.2653%
2017-05-10 | 11 | 6772 | 109.5532 | 1.618% | 17.6298 | 0.2603% | 127.183 | 1.878% | 1210 | 6754.3702 | 6644.817 | 1.649% | 0.2653%
2017-05-09 | 18 | 6773 | 109.5569 | 1.618% | 17.6319 | 0.2603% | 127.1888 | 1.878% | 1211 | 6755.3681 | 6645.8112 | 1.649% | 0.2653%
2017-04-11 | 13 | 6774 | 109.5605 | 1.617% | 17.6341 | 0.2603% | 127.1946 | 1.878% | 1212 | 6756.3659 | 6646.8054 | 1.648% | 0.2653%
2017-05-21 | 12 | 6774 | 109.5605 | 1.617% | 17.6341 | 0.2603% | 127.1946 | 1.878% | 1213 | 6756.3659 | 6646.8054 | 1.648% | 0.2653%
2017-05-11 | 9 | 6775 | 109.5642 | 1.617% | 17.6362 | 0.2603% | 127.2004 | 1.877% | 1214 | 6757.3638 | 6647.7996 | 1.648% | 0.2653%
2017-03-17 | 19 | 6777 | 109.5715 | 1.617% | 17.6405 | 0.2603% | 127.212 | 1.877% | 1215 | 6759.3595 | 6649.788 | 1.648% | 0.2653%
2017-03-31 | 16 | 6777 | 109.5715 | 1.617% | 17.6405 | 0.2603% | 127.212 | 1.877% | 1216 | 6759.3595 | 6649.788 | 1.648% | 0.2653%
2017-04-17 | 23 | 6778 | 109.5752 | 1.617% | 17.6426 | 0.2603% | 127.2178 | 1.877% | 1217 | 6760.3574 | 6650.7822 | 1.648% | 0.2653%
2017-05-05 | 9 | 6778 | 109.5752 | 1.617% | 17.6426 | 0.2603% | 127.2178 | 1.877% | 1218 | 6760.3574 | 6650.7822 | 1.648% | 0.2653%
2017-04-24 | 11 | 6779 | 109.5788 | 1.616% | 17.6448 | 0.2603% | 127.2236 | 1.877% | 1219 | 6761.3552 | 6651.7764 | 1.647% | 0.2653%
2017-03-27 | 15 | 6780 | 109.5825 | 1.616% | 17.6469 | 0.2603% | 127.2294 | 1.877% | 1220 | 6762.3531 | 6652.7706 | 1.647% | 0.2653%
2017-05-02 | 9 | 6782 | 109.5898 | 1.616% | 17.6512 | 0.2603% | 127.241 | 1.876% | 1221 | 6764.3488 | 6654.759 | 1.647% | 0.2652%
2017-03-09 | 11 | 6783 | 109.5935 | 1.616% | 17.6533 | 0.2603% | 127.2468 | 1.876% | 1222 | 6765.3467 | 6655.7532 | 1.647% | 0.2652%
2017-04-26 | 12 | 6785 | 109.6008 | 1.615% | 17.6576 | 0.2602% | 127.2585 | 1.876% | 1223 | 6767.3424 | 6657.7415 | 1.646% | 0.2652%
2017-05-23 | 23 | 6785 | 109.6008 | 1.615% | 17.6576 | 0.2602% | 127.2585 | 1.876% | 1224 | 6767.3424 | 6657.7415 | 1.646% | 0.2652%
2017-04-19 | 15 | 6786 | 109.6045 | 1.615% | 17.6598 | 0.2602% | 127.2643 | 1.875% | 1225 | 6768.3402 | 6658.7357 | 1.646% | 0.2652%
2017-03-21 | 16 | 6789 | 109.6155 | 1.615% | 17.6662 | 0.2602% | 127.2817 | 1.875% | 1226 | 6771.3338 | 6661.7183 | 1.645% | 0.2652%
2017-04-05 | 12 | 6789 | 109.6155 | 1.615% | 17.6662 | 0.2602% | 127.2817 | 1.875% | 1227 | 6771.3338 | 6661.7183 | 1.645% | 0.2652%
2017-05-05 | 21 | 6790 | 109.6191 | 1.614% | 17.6683 | 0.2602% | 127.2875 | 1.875% | 1228 | 6772.3317 | 6662.7125 | 1.645% | 0.2652%
2017-05-17 | 8 | 6790 | 109.6191 | 1.614% | 17.6683 | 0.2602% | 127.2875 | 1.875% | 1229 | 6772.3317 | 6662.7125 | 1.645% | 0.2652%
2017-03-31 | 15 | 6791 | 109.6228 | 1.614% | 17.6705 | 0.2602% | 127.2933 | 1.874% | 1230 | 6773.3295 | 6663.7067 | 1.645% | 0.2652%
2017-04-18 | 12 | 6792 | 109.6265 | 1.614% | 17.6726 | 0.2602% | 127.2991 | 1.874% | 1231 | 6774.3274 | 6664.7009 | 1.645% | 0.2652%
2017-04-24 | 22 | 6793 | 109.6301 | 1.614% | 17.6747 | 0.2602% | 127.3049 | 1.874% | 1232 | 6775.3253 | 6665.6951 | 1.645% | 0.2652%
2017-04-13 | 12 | 6795 | 109.6375 | 1.614% | 17.679 | 0.2602% | 127.3165 | 1.874% | 1233 | 6777.321 | 6667.6835 | 1.644% | 0.2651%
2017-04-09 | 9 | 6797 | 109.6448 | 1.613% | 17.6833 | 0.2602% | 127.3281 | 1.873% | 1234 | 6779.3167 | 6669.6719 | 1.644% | 0.2651%
2017-04-24 | 12 | 6797 | 109.6448 | 1.613% | 17.6833 | 0.2602% | 127.3281 | 1.873% | 1235 | 6779.3167 | 6669.6719 | 1.644% | 0.2651%
2017-03-31 | 21 | 6799 | 109.6521 | 1.613% | 17.6876 | 0.2601% | 127.3397 | 1.873% | 1236 | 6781.3124 | 6671.6603 | 1.644% | 0.2651%
2017-03-10 | 11 | 6803 | 109.6668 | 1.612% | 17.6961 | 0.2601% | 127.3629 | 1.872% | 1237 | 6785.3039 | 6675.6371 | 1.643% | 0.2651%
2017-03-23 | 5 | 6803 | 109.6668 | 1.612% | 17.6961 | 0.2601% | 127.3629 | 1.872% | 1238 | 6785.3039 | 6675.6371 | 1.643% | 0.2651%
2017-03-22 | 20 | 6805 | 109.6741 | 1.612% | 17.7004 | 0.2601% | 127.3745 | 1.872% | 1239 | 6787.2996 | 6677.6255 | 1.642% | 0.2651%
2017-05-25 | 9 | 6807 | 109.6814 | 1.611% | 17.7047 | 0.2601% | 127.3861 | 1.871% | 1240 | 6789.2953 | 6679.6139 | 1.642% | 0.2651%
2017-05-08 | 17 | 6808 | 109.6851 | 1.611% | 17.7068 | 0.2601% | 127.3919 | 1.871% | 1241 | 6790.2932 | 6680.6081 | 1.642% | 0.265%
2017-05-05 | 20 | 6809 | 109.6888 | 1.611% | 17.709 | 0.2601% | 127.3977 | 1.871% | 1242 | 6791.291 | 6681.6023 | 1.642% | 0.265%
2017-03-03 | 13 | 6810 | 109.6924 | 1.611% | 17.7111 | 0.2601% | 127.4035 | 1.871% | 1243 | 6792.2889 | 6682.5965 | 1.641% | 0.265%
2017-05-24 | 9 | 6813 | 109.7034 | 1.61% | 17.7175 | 0.2601% | 127.4209 | 1.87% | 1244 | 6795.2825 | 6685.5791 | 1.641% | 0.265%
2017-04-24 | 17 | 6817 | 109.7181 | 1.609% | 17.7261 | 0.26% | 127.4442 | 1.87% | 1245 | 6799.2739 | 6689.5558 | 1.64% | 0.265%
2017-03-20 | 14 | 6818 | 109.7217 | 1.609% | 17.7282 | 0.26% | 127.45 | 1.869% | 1246 | 6800.2718 | 6690.55 | 1.64% | 0.265%
2017-03-24 | 3 | 6825 | 109.7474 | 1.608% | 17.7432 | 0.26% | 127.4906 | 1.868% | 1247 | 6807.2568 | 6697.5094 | 1.639% | 0.2649%
2017-03-29 | 16 | 6825 | 109.7474 | 1.608% | 17.7432 | 0.26% | 127.4906 | 1.868% | 1248 | 6807.2568 | 6697.5094 | 1.639% | 0.2649%
2017-04-25 | 16 | 6826 | 109.751 | 1.608% | 17.7454 | 0.26% | 127.4964 | 1.868% | 1249 | 6808.2546 | 6698.5036 | 1.638% | 0.2649%
2017-03-18 | 8 | 6827 | 109.7547 | 1.608% | 17.7475 | 0.26% | 127.5022 | 1.868% | 1250 | 6809.2525 | 6699.4978 | 1.638% | 0.2649%
2017-04-27 | 10 | 6828 | 109.7584 | 1.607% | 17.7496 | 0.26% | 127.508 | 1.867% | 1251 | 6810.2504 | 6700.492 | 1.638% | 0.2649%
2017-03-06 | 13 | 6829 | 109.762 | 1.607% | 17.7518 | 0.2599% | 127.5138 | 1.867% | 1252 | 6811.2482 | 6701.4862 | 1.638% | 0.2649%
2017-05-01 | 24 | 6829 | 109.762 | 1.607% | 17.7518 | 0.2599% | 127.5138 | 1.867% | 1253 | 6811.2482 | 6701.4862 | 1.638% | 0.2649%
2017-05-09 | 22 | 6829 | 109.762 | 1.607% | 17.7518 | 0.2599% | 127.5138 | 1.867% | 1254 | 6811.2482 | 6701.4862 | 1.638% | 0.2649%
2017-03-01 | 11 | 6830 | 109.7657 | 1.607% | 17.7539 | 0.2599% | 127.5196 | 1.867% | 1255 | 6812.2461 | 6702.4804 | 1.638% | 0.2649%
2017-04-29 | 1 | 6832 | 109.773 | 1.607% | 17.7582 | 0.2599% | 127.5312 | 1.867% | 1256 | 6814.2418 | 6704.4688 | 1.637% | 0.2649%
2017-03-26 | 21 | 6835 | 109.784 | 1.606% | 17.7646 | 0.2599% | 127.5486 | 1.866% | 1257 | 6817.2354 | 6707.4514 | 1.637% | 0.2648%
2017-04-14 | 15 | 6835 | 109.784 | 1.606% | 17.7646 | 0.2599% | 127.5486 | 1.866% | 1258 | 6817.2354 | 6707.4514 | 1.637% | 0.2648%
2017-04-03 | 17 | 6836 | 109.7877 | 1.606% | 17.7668 | 0.2599% | 127.5544 | 1.866% | 1259 | 6818.2332 | 6708.4456 | 1.637% | 0.2648%
2017-04-18 | 13 | 6842 | 109.8096 | 1.605% | 17.7796 | 0.2599% | 127.5892 | 1.865% | 1260 | 6824.2204 | 6714.4108 | 1.635% | 0.2648%
2017-04-25 | 17 | 6842 | 109.8096 | 1.605% | 17.7796 | 0.2599% | 127.5892 | 1.865% | 1261 | 6824.2204 | 6714.4108 | 1.635% | 0.2648%
2017-03-11 | 13 | 6844 | 109.817 | 1.605% | 17.7839 | 0.2598% | 127.6008 | 1.864% | 1262 | 6826.2161 | 6716.3992 | 1.635% | 0.2648%
2017-04-14 | 22 | 6844 | 109.817 | 1.605% | 17.7839 | 0.2598% | 127.6008 | 1.864% | 1263 | 6826.2161 | 6716.3992 | 1.635% | 0.2648%
2017-04-07 | 7 | 6845 | 109.8206 | 1.604% | 17.786 | 0.2598% | 127.6067 | 1.864% | 1264 | 6827.214 | 6717.3933 | 1.635% | 0.2648%
2017-04-18 | 22 | 6849 | 109.8353 | 1.604% | 17.7946 | 0.2598% | 127.6299 | 1.863% | 1265 | 6831.2054 | 6721.3701 | 1.634% | 0.2647%
2017-03-01 | 22 | 6850 | 109.839 | 1.603% | 17.7967 | 0.2598% | 127.6357 | 1.863% | 1266 | 6832.2033 | 6722.3643 | 1.634% | 0.2647%
2017-03-29 | 22 | 6851 | 109.8426 | 1.603% | 17.7989 | 0.2598% | 127.6415 | 1.863% | 1267 | 6833.2011 | 6723.3585 | 1.634% | 0.2647%
2017-04-07 | 11 | 6853 | 109.8499 | 1.603% | 17.8031 | 0.2598% | 127.6531 | 1.863% | 1268 | 6835.1969 | 6725.3469 | 1.633% | 0.2647%
2017-05-03 | 23 | 6853 | 109.8499 | 1.603% | 17.8031 | 0.2598% | 127.6531 | 1.863% | 1269 | 6835.1969 | 6725.3469 | 1.633% | 0.2647%
2017-05-09 | 19 | 6853 | 109.8499 | 1.603% | 17.8031 | 0.2598% | 127.6531 | 1.863% | 1270 | 6835.1969 | 6725.3469 | 1.633% | 0.2647%
2017-04-07 | 22 | 6854 | 109.8536 | 1.603% | 17.8053 | 0.2598% | 127.6589 | 1.863% | 1271 | 6836.1947 | 6726.3411 | 1.633% | 0.2647%
2017-04-16 | 22 | 6855 | 109.8573 | 1.603% | 17.8074 | 0.2598% | 127.6647 | 1.862% | 1272 | 6837.1926 | 6727.3353 | 1.633% | 0.2647%
2017-05-08 | 20 | 6858 | 109.8683 | 1.602% | 17.8138 | 0.2598% | 127.6821 | 1.862% | 1273 | 6840.1862 | 6730.3179 | 1.632% | 0.2647%
2017-03-08 | 19 | 6861 | 109.8793 | 1.602% | 17.8203 | 0.2597% | 127.6995 | 1.861% | 1274 | 6843.1797 | 6733.3005 | 1.632% | 0.2647%
2017-03-28 | 14 | 6862 | 109.8829 | 1.601% | 17.8224 | 0.2597% | 127.7053 | 1.861% | 1275 | 6844.1776 | 6734.2947 | 1.632% | 0.2647%
2017-03-19 | 14 | 6869 | 109.9086 | 1.6% | 17.8374 | 0.2597% | 127.7459 | 1.86% | 1276 | 6851.1626 | 6741.2541 | 1.63% | 0.2646%
2017-04-25 | 22 | 6873 | 109.9232 | 1.599% | 17.8459 | 0.2597% | 127.7691 | 1.859% | 1277 | 6855.1541 | 6745.2309 | 1.63% | 0.2646%
2017-03-28 | 15 | 6876 | 109.9342 | 1.599% | 17.8523 | 0.2596% | 127.7866 | 1.858% | 1278 | 6858.1477 | 6748.2134 | 1.629% | 0.2645%
2017-04-28 | 8 | 6877 | 109.9379 | 1.599% | 17.8545 | 0.2596% | 127.7924 | 1.858% | 1279 | 6859.1455 | 6749.2076 | 1.629% | 0.2645%
2017-05-22 | 8 | 6879 | 109.9452 | 1.598% | 17.8588 | 0.2596% | 127.804 | 1.858% | 1280 | 6861.1412 | 6751.196 | 1.629% | 0.2645%
2017-03-31 | 17 | 6880 | 109.9489 | 1.598% | 17.8609 | 0.2596% | 127.8098 | 1.858% | 1281 | 6862.1391 | 6752.1902 | 1.628% | 0.2645%
2017-03-31 | 18 | 6881 | 109.9525 | 1.598% | 17.863 | 0.2596% | 127.8156 | 1.858% | 1282 | 6863.137 | 6753.1844 | 1.628% | 0.2645%
2017-05-24 | 23 | 6882 | 109.9562 | 1.598% | 17.8652 | 0.2596% | 127.8214 | 1.857% | 1283 | 6864.1348 | 6754.1786 | 1.628% | 0.2645%
2017-04-08 | 7 | 6883 | 109.9598 | 1.598% | 17.8673 | 0.2596% | 127.8272 | 1.857% | 1284 | 6865.1327 | 6755.1728 | 1.628% | 0.2645%
2017-03-10 | 10 | 6886 | 109.9708 | 1.597% | 17.8737 | 0.2596% | 127.8446 | 1.857% | 1285 | 6868.1263 | 6758.1554 | 1.627% | 0.2645%
2017-05-09 | 20 | 6886 | 109.9708 | 1.597% | 17.8737 | 0.2596% | 127.8446 | 1.857% | 1286 | 6868.1263 | 6758.1554 | 1.627% | 0.2645%
2017-03-12 | 6 | 6888 | 109.9782 | 1.597% | 17.878 | 0.2596% | 127.8562 | 1.856% | 1287 | 6870.122 | 6760.1438 | 1.627% | 0.2645%
2017-04-05 | 13 | 6889 | 109.9818 | 1.596% | 17.8802 | 0.2595% | 127.862 | 1.856% | 1288 | 6871.1198 | 6761.138 | 1.627% | 0.2645%
2017-05-15 | 10 | 6890 | 109.9855 | 1.596% | 17.8823 | 0.2595% | 127.8678 | 1.856% | 1289 | 6872.1177 | 6762.1322 | 1.626% | 0.2644%
2017-03-11 | 5 | 6891 | 109.9892 | 1.596% | 17.8844 | 0.2595% | 127.8736 | 1.856% | 1290 | 6873.1156 | 6763.1264 | 1.626% | 0.2644%
2017-05-19 | 8 | 6892 | 109.9928 | 1.596% | 17.8866 | 0.2595% | 127.8794 | 1.855% | 1291 | 6874.1134 | 6764.1206 | 1.626% | 0.2644%
2017-03-10 | 22 | 6894 | 110.0001 | 1.596% | 17.8909 | 0.2595% | 127.891 | 1.855% | 1292 | 6876.1091 | 6766.109 | 1.626% | 0.2644%
2017-05-08 | 18 | 6894 | 110.0001 | 1.596% | 17.8909 | 0.2595% | 127.891 | 1.855% | 1293 | 6876.1091 | 6766.109 | 1.626% | 0.2644%
2017-03-23 | 14 | 6897 | 110.0111 | 1.595% | 17.8973 | 0.2595% | 127.9084 | 1.855% | 1294 | 6879.1027 | 6769.0916 | 1.625% | 0.2644%
2017-05-23 | 8 | 6897 | 110.0111 | 1.595% | 17.8973 | 0.2595% | 127.9084 | 1.855% | 1295 | 6879.1027 | 6769.0916 | 1.625% | 0.2644%
2017-03-07 | 19 | 6898 | 110.0148 | 1.595% | 17.8994 | 0.2595% | 127.9142 | 1.854% | 1296 | 6880.1006 | 6770.0858 | 1.625% | 0.2644%
2017-04-25 | 18 | 6898 | 110.0148 | 1.595% | 17.8994 | 0.2595% | 127.9142 | 1.854% | 1297 | 6880.1006 | 6770.0858 | 1.625% | 0.2644%
2017-05-14 | 16 | 6902 | 110.0295 | 1.594% | 17.908 | 0.2595% | 127.9374 | 1.854% | 1298 | 6884.092 | 6774.0626 | 1.624% | 0.2644%
2017-03-21 | 17 | 6906 | 110.0441 | 1.593% | 17.9165 | 0.2594% | 127.9607 | 1.853% | 1299 | 6888.0835 | 6778.0393 | 1.624% | 0.2643%
2017-03-07 | 10 | 6907 | 110.0478 | 1.593% | 17.9187 | 0.2594% | 127.9665 | 1.853% | 1300 | 6889.0813 | 6779.0335 | 1.623% | 0.2643%
2017-04-10 | 22 | 6909 | 110.0551 | 1.593% | 17.923 | 0.2594% | 127.9781 | 1.852% | 1301 | 6891.077 | 6781.0219 | 1.623% | 0.2643%
2017-04-19 | 16 | 6910 | 110.0588 | 1.593% | 17.9251 | 0.2594% | 127.9839 | 1.852% | 1302 | 6892.0749 | 6782.0161 | 1.623% | 0.2643%
2017-03-09 | 6 | 6911 | 110.0624 | 1.593% | 17.9272 | 0.2594% | 127.9897 | 1.852% | 1303 | 6893.0728 | 6783.0103 | 1.623% | 0.2643%
2017-04-07 | 21 | 6916 | 110.0807 | 1.592% | 17.9379 | 0.2594% | 128.0187 | 1.851% | 1304 | 6898.0621 | 6787.9813 | 1.622% | 0.2643%
2017-05-24 | 10 | 6918 | 110.0881 | 1.591% | 17.9422 | 0.2594% | 128.0303 | 1.851% | 1305 | 6900.0578 | 6789.9697 | 1.621% | 0.2642%
2017-03-01 | 12 | 6920 | 110.0954 | 1.591% | 17.9465 | 0.2593% | 128.0419 | 1.85% | 1306 | 6902.0535 | 6791.9581 | 1.621% | 0.2642%
2017-04-03 | 18 | 6920 | 110.0954 | 1.591% | 17.9465 | 0.2593% | 128.0419 | 1.85% | 1307 | 6902.0535 | 6791.9581 | 1.621% | 0.2642%
2017-05-02 | 10 | 6922 | 110.1027 | 1.591% | 17.9508 | 0.2593% | 128.0535 | 1.85% | 1308 | 6904.0492 | 6793.9465 | 1.621% | 0.2642%
2017-04-25 | 19 | 6930 | 110.132 | 1.589% | 17.9679 | 0.2593% | 128.0999 | 1.848% | 1309 | 6912.0321 | 6801.9001 | 1.619% | 0.2642%
2017-03-04 | 13 | 6931 | 110.1357 | 1.589% | 17.97 | 0.2593% | 128.1057 | 1.848% | 1310 | 6913.03 | 6802.8943 | 1.619% | 0.2642%
2017-05-08 | 19 | 6934 | 110.1467 | 1.589% | 17.9765 | 0.2593% | 128.1231 | 1.848% | 1311 | 6916.0235 | 6805.8769 | 1.618% | 0.2641%
2017-03-20 | 2 | 6935 | 110.1503 | 1.588% | 17.9786 | 0.2592% | 128.1289 | 1.848% | 1312 | 6917.0214 | 6806.8711 | 1.618% | 0.2641%
2017-03-28 | 16 | 6935 | 110.1503 | 1.588% | 17.9786 | 0.2592% | 128.1289 | 1.848% | 1313 | 6917.0214 | 6806.8711 | 1.618% | 0.2641%
2017-04-07 | 10 | 6937 | 110.1577 | 1.588% | 17.9829 | 0.2592% | 128.1406 | 1.847% | 1314 | 6919.0171 | 6808.8594 | 1.618% | 0.2641%
2017-05-04 | 11 | 6937 | 110.1577 | 1.588% | 17.9829 | 0.2592% | 128.1406 | 1.847% | 1315 | 6919.0171 | 6808.8594 | 1.618% | 0.2641%
2017-03-09 | 21 | 6938 | 110.1613 | 1.588% | 17.985 | 0.2592% | 128.1464 | 1.847% | 1316 | 6920.015 | 6809.8536 | 1.618% | 0.2641%
2017-03-01 | 13 | 6939 | 110.165 | 1.588% | 17.9872 | 0.2592% | 128.1522 | 1.847% | 1317 | 6921.0128 | 6810.8478 | 1.617% | 0.2641%
2017-04-18 | 14 | 6940 | 110.1687 | 1.587% | 17.9893 | 0.2592% | 128.158 | 1.847% | 1318 | 6922.0107 | 6811.842 | 1.617% | 0.2641%
2017-03-24 | 12 | 6941 | 110.1723 | 1.587% | 17.9914 | 0.2592% | 128.1638 | 1.846% | 1319 | 6923.0086 | 6812.8362 | 1.617% | 0.2641%
2017-04-25 | 20 | 6942 | 110.176 | 1.587% | 17.9936 | 0.2592% | 128.1696 | 1.846% | 1320 | 6924.0064 | 6813.8304 | 1.617% | 0.2641%
2017-05-08 | 21 | 6942 | 110.176 | 1.587% | 17.9936 | 0.2592% | 128.1696 | 1.846% | 1321 | 6924.0064 | 6813.8304 | 1.617% | 0.2641%
2017-03-02 | 23 | 6946 | 110.1906 | 1.586% | 18.0021 | 0.2592% | 128.1928 | 1.846% | 1322 | 6927.9979 | 6817.8072 | 1.616% | 0.264%
2017-03-10 | 9 | 6946 | 110.1906 | 1.586% | 18.0021 | 0.2592% | 128.1928 | 1.846% | 1323 | 6927.9979 | 6817.8072 | 1.616% | 0.264%
2017-04-16 | 14 | 6947 | 110.1943 | 1.586% | 18.0043 | 0.2592% | 128.1986 | 1.845% | 1324 | 6928.9957 | 6818.8014 | 1.616% | 0.264%
2017-03-17 | 23 | 6951 | 110.209 | 1.586% | 18.0128 | 0.2591% | 128.2218 | 1.845% | 1325 | 6932.9872 | 6822.7782 | 1.615% | 0.264%
2017-03-03 | 5 | 6953 | 110.2163 | 1.585% | 18.0171 | 0.2591% | 128.2334 | 1.844% | 1326 | 6934.9829 | 6824.7666 | 1.615% | 0.264%
2017-03-20 | 1 | 6953 | 110.2163 | 1.585% | 18.0171 | 0.2591% | 128.2334 | 1.844% | 1327 | 6934.9829 | 6824.7666 | 1.615% | 0.264%
2017-05-03 | 12 | 6953 | 110.2163 | 1.585% | 18.0171 | 0.2591% | 128.2334 | 1.844% | 1328 | 6934.9829 | 6824.7666 | 1.615% | 0.264%
2017-04-15 | 22 | 6954 | 110.22 | 1.585% | 18.0193 | 0.2591% | 128.2392 | 1.844% | 1329 | 6935.9807 | 6825.7608 | 1.615% | 0.264%
2017-04-04 | 13 | 6955 | 110.2236 | 1.585% | 18.0214 | 0.2591% | 128.245 | 1.844% | 1330 | 6936.9786 | 6826.755 | 1.615% | 0.264%
2017-03-07 | 21 | 6958 | 110.2346 | 1.584% | 18.0278 | 0.2591% | 128.2624 | 1.843% | 1331 | 6939.9722 | 6829.7376 | 1.614% | 0.264%
2017-03-08 | 21 | 6959 | 110.2383 | 1.584% | 18.03 | 0.2591% | 128.2682 | 1.843% | 1332 | 6940.97 | 6830.7318 | 1.614% | 0.264%
2017-03-21 | 18 | 6959 | 110.2383 | 1.584% | 18.03 | 0.2591% | 128.2682 | 1.843% | 1333 | 6940.97 | 6830.7318 | 1.614% | 0.264%
2017-03-06 | 1 | 6961 | 110.2456 | 1.584% | 18.0342 | 0.2591% | 128.2798 | 1.843% | 1334 | 6942.9658 | 6832.7202 | 1.613% | 0.2639%
2017-04-10 | 17 | 6961 | 110.2456 | 1.584% | 18.0342 | 0.2591% | 128.2798 | 1.843% | 1335 | 6942.9658 | 6832.7202 | 1.613% | 0.2639%
2017-05-31 | 24 | 6962 | 110.2493 | 1.584% | 18.0364 | 0.2591% | 128.2856 | 1.843% | 1336 | 6943.9636 | 6833.7144 | 1.613% | 0.2639%
2017-05-30 | 8 | 6963 | 110.2529 | 1.583% | 18.0385 | 0.2591% | 128.2914 | 1.842% | 1337 | 6944.9615 | 6834.7086 | 1.613% | 0.2639%
2017-03-29 | 18 | 6966 | 110.2639 | 1.583% | 18.0449 | 0.259% | 128.3088 | 1.842% | 1338 | 6947.9551 | 6837.6912 | 1.613% | 0.2639%
2017-05-05 | 10 | 6967 | 110.2676 | 1.583% | 18.0471 | 0.259% | 128.3147 | 1.842% | 1339 | 6948.9529 | 6838.6853 | 1.612% | 0.2639%
2017-03-20 | 20 | 6968 | 110.2712 | 1.583% | 18.0492 | 0.259% | 128.3205 | 1.842% | 1340 | 6949.9508 | 6839.6795 | 1.612% | 0.2639%
2017-04-15 | 14 | 6968 | 110.2712 | 1.583% | 18.0492 | 0.259% | 128.3205 | 1.842% | 1341 | 6949.9508 | 6839.6795 | 1.612% | 0.2639%
2017-03-10 | 8 | 6970 | 110.2786 | 1.582% | 18.0535 | 0.259% | 128.3321 | 1.841% | 1342 | 6951.9465 | 6841.6679 | 1.612% | 0.2639%
2017-03-29 | 19 | 6975 | 110.2969 | 1.581% | 18.0642 | 0.259% | 128.3611 | 1.84% | 1343 | 6956.9358 | 6846.6389 | 1.611% | 0.2638%
2017-05-18 | 8 | 6975 | 110.2969 | 1.581% | 18.0642 | 0.259% | 128.3611 | 1.84% | 1344 | 6956.9358 | 6846.6389 | 1.611% | 0.2638%
2017-04-03 | 19 | 6976 | 110.3006 | 1.581% | 18.0663 | 0.259% | 128.3669 | 1.84% | 1345 | 6957.9337 | 6847.6331 | 1.611% | 0.2638%
2017-04-13 | 13 | 6976 | 110.3006 | 1.581% | 18.0663 | 0.259% | 128.3669 | 1.84% | 1346 | 6957.9337 | 6847.6331 | 1.611% | 0.2638%
2017-03-17 | 15 | 6977 | 110.3042 | 1.581% | 18.0685 | 0.259% | 128.3727 | 1.84% | 1347 | 6958.9315 | 6848.6273 | 1.611% | 0.2638%
2017-04-24 | 18 | 6978 | 110.3079 | 1.581% | 18.0706 | 0.259% | 128.3785 | 1.84% | 1348 | 6959.9294 | 6849.6215 | 1.61% | 0.2638%
2017-03-19 | 20 | 6980 | 110.3152 | 1.58% | 18.0749 | 0.259% | 128.3901 | 1.839% | 1349 | 6961.9251 | 6851.6099 | 1.61% | 0.2638%
2017-05-23 | 9 | 6982 | 110.3225 | 1.58% | 18.0792 | 0.2589% | 128.4017 | 1.839% | 1350 | 6963.9208 | 6853.5983 | 1.61% | 0.2638%
2017-03-06 | 22 | 6986 | 110.3372 | 1.579% | 18.0877 | 0.2589% | 128.4249 | 1.838% | 1351 | 6967.9123 | 6857.5751 | 1.609% | 0.2638%
2017-04-26 | 13 | 6987 | 110.3408 | 1.579% | 18.0899 | 0.2589% | 128.4307 | 1.838% | 1352 | 6968.9101 | 6858.5693 | 1.609% | 0.2638%
2017-04-29 | 9 | 6987 | 110.3408 | 1.579% | 18.0899 | 0.2589% | 128.4307 | 1.838% | 1353 | 6968.9101 | 6858.5693 | 1.609% | 0.2638%
2017-03-29 | 17 | 6989 | 110.3482 | 1.579% | 18.0941 | 0.2589% | 128.4423 | 1.838% | 1354 | 6970.9059 | 6860.5577 | 1.608% | 0.2637%
2017-05-26 | 23 | 6990 | 110.3518 | 1.579% | 18.0963 | 0.2589% | 128.4481 | 1.838% | 1355 | 6971.9037 | 6861.5519 | 1.608% | 0.2637%
2017-05-10 | 12 | 6993 | 110.3628 | 1.578% | 18.1027 | 0.2589% | 128.4655 | 1.837% | 1356 | 6974.8973 | 6864.5345 | 1.608% | 0.2637%
2017-04-05 | 14 | 6994 | 110.3665 | 1.578% | 18.1048 | 0.2589% | 128.4713 | 1.837% | 1357 | 6975.8952 | 6865.5287 | 1.608% | 0.2637%
2017-03-06 | 2 | 6997 | 110.3775 | 1.577% | 18.1113 | 0.2588% | 128.4888 | 1.836% | 1358 | 6978.8887 | 6868.5112 | 1.607% | 0.2637%
2017-03-24 | 4 | 6997 | 110.3775 | 1.577% | 18.1113 | 0.2588% | 128.4888 | 1.836% | 1359 | 6978.8887 | 6868.5112 | 1.607% | 0.2637%
2017-04-11 | 14 | 6999 | 110.3848 | 1.577% | 18.1155 | 0.2588% | 128.5004 | 1.836% | 1360 | 6980.8845 | 6870.4996 | 1.607% | 0.2637%
2017-03-10 | 20 | 7002 | 110.3958 | 1.577% | 18.122 | 0.2588% | 128.5178 | 1.835% | 1361 | 6983.878 | 6873.4822 | 1.606% | 0.2637%
2017-04-19 | 22 | 7007 | 110.4141 | 1.576% | 18.1327 | 0.2588% | 128.5468 | 1.835% | 1362 | 6988.8673 | 6878.4532 | 1.605% | 0.2636%
2017-04-12 | 13 | 7008 | 110.4178 | 1.576% | 18.1348 | 0.2588% | 128.5526 | 1.834% | 1363 | 6989.8652 | 6879.4474 | 1.605% | 0.2636%
2017-04-19 | 17 | 7008 | 110.4178 | 1.576% | 18.1348 | 0.2588% | 128.5526 | 1.834% | 1364 | 6989.8652 | 6879.4474 | 1.605% | 0.2636%
2017-05-01 | 8 | 7009 | 110.4214 | 1.575% | 18.1369 | 0.2588% | 128.5584 | 1.834% | 1365 | 6990.8631 | 6880.4416 | 1.605% | 0.2636%
2017-03-03 | 12 | 7010 | 110.4251 | 1.575% | 18.1391 | 0.2588% | 128.5642 | 1.834% | 1366 | 6991.8609 | 6881.4358 | 1.605% | 0.2636%
2017-03-30 | 21 | 7010 | 110.4251 | 1.575% | 18.1391 | 0.2588% | 128.5642 | 1.834% | 1367 | 6991.8609 | 6881.4358 | 1.605% | 0.2636%
2017-04-18 | 19 | 7010 | 110.4251 | 1.575% | 18.1391 | 0.2588% | 128.5642 | 1.834% | 1368 | 6991.8609 | 6881.4358 | 1.605% | 0.2636%
2017-04-18 | 15 | 7011 | 110.4288 | 1.575% | 18.1412 | 0.2588% | 128.57 | 1.834% | 1369 | 6992.8588 | 6882.43 | 1.605% | 0.2636%
2017-03-10 | 21 | 7013 | 110.4361 | 1.575% | 18.1455 | 0.2587% | 128.5816 | 1.833% | 1370 | 6994.8545 | 6884.4184 | 1.604% | 0.2636%
2017-03-11 | 24 | 7013 | 110.4361 | 1.575% | 18.1455 | 0.2587% | 128.5816 | 1.833% | 1371 | 6994.8545 | 6884.4184 | 1.604% | 0.2636%
2017-05-04 | 23 | 7013 | 110.4361 | 1.575% | 18.1455 | 0.2587% | 128.5816 | 1.833% | 1372 | 6994.8545 | 6884.4184 | 1.604% | 0.2636%
2017-04-18 | 16 | 7014 | 110.4398 | 1.575% | 18.1476 | 0.2587% | 128.5874 | 1.833% | 1373 | 6995.8524 | 6885.4126 | 1.604% | 0.2636%
2017-04-26 | 23 | 7017 | 110.4508 | 1.574% | 18.1541 | 0.2587% | 128.6048 | 1.833% | 1374 | 6998.8459 | 6888.3952 | 1.603% | 0.2635%
2017-03-27 | 17 | 7023 | 110.4727 | 1.573% | 18.1669 | 0.2587% | 128.6396 | 1.832% | 1375 | 7004.8331 | 6894.3604 | 1.602% | 0.2635%
2017-03-27 | 18 | 7024 | 110.4764 | 1.573% | 18.169 | 0.2587% | 128.6454 | 1.832% | 1376 | 7005.831 | 6895.3546 | 1.602% | 0.2635%
2017-03-27 | 22 | 7024 | 110.4764 | 1.573% | 18.169 | 0.2587% | 128.6454 | 1.832% | 1377 | 7005.831 | 6895.3546 | 1.602% | 0.2635%
2017-03-23 | 24 | 7027 | 110.4874 | 1.572% | 18.1755 | 0.2587% | 128.6629 | 1.831% | 1378 | 7008.8245 | 6898.3371 | 1.602% | 0.2635%
2017-04-21 | 10 | 7030 | 110.4984 | 1.572% | 18.1819 | 0.2586% | 128.6803 | 1.83% | 1379 | 7011.8181 | 6901.3197 | 1.601% | 0.2635%
2017-03-29 | 20 | 7032 | 110.5057 | 1.571% | 18.1862 | 0.2586% | 128.6919 | 1.83% | 1380 | 7013.8138 | 6903.3081 | 1.601% | 0.2634%
2017-04-16 | 20 | 7032 | 110.5057 | 1.571% | 18.1862 | 0.2586% | 128.6919 | 1.83% | 1381 | 7013.8138 | 6903.3081 | 1.601% | 0.2634%
2017-05-29 | 24 | 7036 | 110.5204 | 1.571% | 18.1947 | 0.2586% | 128.7151 | 1.829% | 1382 | 7017.8053 | 6907.2849 | 1.6% | 0.2634%
2017-04-22 | 11 | 7038 | 110.5277 | 1.57% | 18.199 | 0.2586% | 128.7267 | 1.829% | 1383 | 7019.801 | 6909.2733 | 1.6% | 0.2634%
2017-04-06 | 21 | 7040 | 110.535 | 1.57% | 18.2033 | 0.2586% | 128.7383 | 1.829% | 1384 | 7021.7967 | 6911.2617 | 1.599% | 0.2634%
2017-05-26 | 11 | 7040 | 110.535 | 1.57% | 18.2033 | 0.2586% | 128.7383 | 1.829% | 1385 | 7021.7967 | 6911.2617 | 1.599% | 0.2634%
2017-04-13 | 22 | 7041 | 110.5387 | 1.57% | 18.2054 | 0.2586% | 128.7441 | 1.828% | 1386 | 7022.7946 | 6912.2559 | 1.599% | 0.2634%
2017-05-16 | 24 | 7044 | 110.5497 | 1.569% | 18.2118 | 0.2585% | 128.7615 | 1.828% | 1387 | 7025.7882 | 6915.2385 | 1.599% | 0.2634%
2017-03-05 | 24 | 7045 | 110.5533 | 1.569% | 18.214 | 0.2585% | 128.7673 | 1.828% | 1388 | 7026.786 | 6916.2327 | 1.598% | 0.2634%
2017-03-21 | 10 | 7045 | 110.5533 | 1.569% | 18.214 | 0.2585% | 128.7673 | 1.828% | 1389 | 7026.786 | 6916.2327 | 1.598% | 0.2634%
2017-05-27 | 24 | 7048 | 110.5643 | 1.569% | 18.2204 | 0.2585% | 128.7847 | 1.827% | 1390 | 7029.7796 | 6919.2153 | 1.598% | 0.2633%
2017-04-17 | 12 | 7049 | 110.568 | 1.569% | 18.2225 | 0.2585% | 128.7905 | 1.827% | 1391 | 7030.7775 | 6920.2095 | 1.598% | 0.2633%
2017-04-05 | 17 | 7050 | 110.5716 | 1.568% | 18.2247 | 0.2585% | 128.7963 | 1.827% | 1392 | 7031.7753 | 6921.2037 | 1.598% | 0.2633%
2017-04-10 | 20 | 7051 | 110.5753 | 1.568% | 18.2268 | 0.2585% | 128.8021 | 1.827% | 1393 | 7032.7732 | 6922.1979 | 1.597% | 0.2633%
2017-04-24 | 19 | 7052 | 110.579 | 1.568% | 18.229 | 0.2585% | 128.8079 | 1.827% | 1394 | 7033.771 | 6923.1921 | 1.597% | 0.2633%
2017-03-21 | 22 | 7053 | 110.5826 | 1.568% | 18.2311 | 0.2585% | 128.8137 | 1.826% | 1395 | 7034.7689 | 6924.1863 | 1.597% | 0.2633%
2017-05-27 | 11 | 7053 | 110.5826 | 1.568% | 18.2311 | 0.2585% | 128.8137 | 1.826% | 1396 | 7034.7689 | 6924.1863 | 1.597% | 0.2633%
2017-03-21 | 7 | 7054 | 110.5863 | 1.568% | 18.2332 | 0.2585% | 128.8195 | 1.826% | 1397 | 7035.7668 | 6925.1805 | 1.597% | 0.2633%
2017-04-10 | 18 | 7055 | 110.59 | 1.568% | 18.2354 | 0.2585% | 128.8253 | 1.826% | 1398 | 7036.7646 | 6926.1747 | 1.597% | 0.2633%
2017-04-14 | 20 | 7055 | 110.59 | 1.568% | 18.2354 | 0.2585% | 128.8253 | 1.826% | 1399 | 7036.7646 | 6926.1747 | 1.597% | 0.2633%
2017-05-28 | 24 | 7057 | 110.5973 | 1.567% | 18.2397 | 0.2585% | 128.8369 | 1.826% | 1400 | 7038.7603 | 6928.1631 | 1.596% | 0.2633%
2017-04-05 | 18 | 7058 | 110.601 | 1.567% | 18.2418 | 0.2585% | 128.8428 | 1.825% | 1401 | 7039.7582 | 6929.1572 | 1.596% | 0.2633%
2017-03-01 | 14 | 7059 | 110.6046 | 1.567% | 18.2439 | 0.2584% | 128.8486 | 1.825% | 1402 | 7040.7561 | 6930.1514 | 1.596% | 0.2633%
2017-03-18 | 14 | 7060 | 110.6083 | 1.567% | 18.2461 | 0.2584% | 128.8544 | 1.825% | 1403 | 7041.7539 | 6931.1456 | 1.596% | 0.2632%
2017-04-08 | 10 | 7063 | 110.6193 | 1.566% | 18.2525 | 0.2584% | 128.8718 | 1.825% | 1404 | 7044.7475 | 6934.1282 | 1.595% | 0.2632%
2017-05-25 | 10 | 7063 | 110.6193 | 1.566% | 18.2525 | 0.2584% | 128.8718 | 1.825% | 1405 | 7044.7475 | 6934.1282 | 1.595% | 0.2632%
2017-03-19 | 13 | 7065 | 110.6266 | 1.566% | 18.2568 | 0.2584% | 128.8834 | 1.824% | 1406 | 7046.7432 | 6936.1166 | 1.595% | 0.2632%
2017-03-09 | 20 | 7066 | 110.6303 | 1.566% | 18.2589 | 0.2584% | 128.8892 | 1.824% | 1407 | 7047.7411 | 6937.1108 | 1.595% | 0.2632%
2017-03-02 | 19 | 7067 | 110.6339 | 1.566% | 18.2611 | 0.2584% | 128.895 | 1.824% | 1408 | 7048.7389 | 6938.105 | 1.595% | 0.2632%
2017-04-18 | 18 | 7067 | 110.6339 | 1.566% | 18.2611 | 0.2584% | 128.895 | 1.824% | 1409 | 7048.7389 | 6938.105 | 1.595% | 0.2632%
2017-04-05 | 16 | 7069 | 110.6413 | 1.565% | 18.2653 | 0.2584% | 128.9066 | 1.824% | 1410 | 7050.7347 | 6940.0934 | 1.594% | 0.2632%
2017-04-10 | 19 | 7071 | 110.6486 | 1.565% | 18.2696 | 0.2584% | 128.9182 | 1.823% | 1411 | 7052.7304 | 6942.0818 | 1.594% | 0.2632%
2017-03-22 | 22 | 7072 | 110.6522 | 1.565% | 18.2718 | 0.2584% | 128.924 | 1.823% | 1412 | 7053.7282 | 6943.076 | 1.594% | 0.2632%
2017-04-20 | 12 | 7074 | 110.6596 | 1.564% | 18.276 | 0.2584% | 128.9356 | 1.823% | 1413 | 7055.724 | 6945.0644 | 1.593% | 0.2632%
2017-04-18 | 17 | 7075 | 110.6632 | 1.564% | 18.2782 | 0.2583% | 128.9414 | 1.822% | 1414 | 7056.7218 | 6946.0586 | 1.593% | 0.2631%
2017-04-03 | 21 | 7076 | 110.6669 | 1.564% | 18.2803 | 0.2583% | 128.9472 | 1.822% | 1415 | 7057.7197 | 6947.0528 | 1.593% | 0.2631%
2017-03-21 | 19 | 7077 | 110.6706 | 1.564% | 18.2825 | 0.2583% | 128.953 | 1.822% | 1416 | 7058.7175 | 6948.047 | 1.593% | 0.2631%
2017-03-07 | 20 | 7078 | 110.6742 | 1.564% | 18.2846 | 0.2583% | 128.9588 | 1.822% | 1417 | 7059.7154 | 6949.0412 | 1.593% | 0.2631%
2017-03-19 | 24 | 7080 | 110.6816 | 1.563% | 18.2889 | 0.2583% | 128.9704 | 1.822% | 1418 | 7061.7111 | 6951.0296 | 1.592% | 0.2631%
2017-04-14 | 16 | 7080 | 110.6816 | 1.563% | 18.2889 | 0.2583% | 128.9704 | 1.822% | 1419 | 7061.7111 | 6951.0296 | 1.592% | 0.2631%
2017-03-09 | 10 | 7081 | 110.6852 | 1.563% | 18.291 | 0.2583% | 128.9762 | 1.821% | 1420 | 7062.709 | 6952.0238 | 1.592% | 0.2631%
2017-03-20 | 13 | 7081 | 110.6852 | 1.563% | 18.291 | 0.2583% | 128.9762 | 1.821% | 1421 | 7062.709 | 6952.0238 | 1.592% | 0.2631%
2017-05-21 | 13 | 7081 | 110.6852 | 1.563% | 18.291 | 0.2583% | 128.9762 | 1.821% | 1422 | 7062.709 | 6952.0238 | 1.592% | 0.2631%
2017-03-08 | 20 | 7084 | 110.6962 | 1.563% | 18.2974 | 0.2583% | 128.9936 | 1.821% | 1423 | 7065.7026 | 6955.0064 | 1.592% | 0.2631%
2017-04-05 | 19 | 7086 | 110.7035 | 1.562% | 18.3017 | 0.2583% | 129.0052 | 1.821% | 1424 | 7067.6983 | 6956.9948 | 1.591% | 0.2631%
2017-04-07 | 9 | 7091 | 110.7219 | 1.561% | 18.3124 | 0.2582% | 129.0343 | 1.82% | 1425 | 7072.6876 | 6961.9657 | 1.59% | 0.263%
2017-04-05 | 15 | 7095 | 110.7365 | 1.561% | 18.321 | 0.2582% | 129.0575 | 1.819% | 1426 | 7076.679 | 6965.9425 | 1.59% | 0.263%
2017-05-21 | 23 | 7095 | 110.7365 | 1.561% | 18.321 | 0.2582% | 129.0575 | 1.819% | 1427 | 7076.679 | 6965.9425 | 1.59% | 0.263%
2017-03-01 | 17 | 7096 | 110.7402 | 1.561% | 18.3231 | 0.2582% | 129.0633 | 1.819% | 1428 | 7077.6769 | 6966.9367 | 1.59% | 0.263%
2017-04-18 | 20 | 7096 | 110.7402 | 1.561% | 18.3231 | 0.2582% | 129.0633 | 1.819% | 1429 | 7077.6769 | 6966.9367 | 1.59% | 0.263%
2017-05-09 | 21 | 7096 | 110.7402 | 1.561% | 18.3231 | 0.2582% | 129.0633 | 1.819% | 1430 | 7077.6769 | 6966.9367 | 1.59% | 0.263%
2017-05-23 | 10 | 7098 | 110.7475 | 1.56% | 18.3274 | 0.2582% | 129.0749 | 1.818% | 1431 | 7079.6726 | 6968.9251 | 1.589% | 0.263%
2017-05-25 | 22 | 7098 | 110.7475 | 1.56% | 18.3274 | 0.2582% | 129.0749 | 1.818% | 1432 | 7079.6726 | 6968.9251 | 1.589% | 0.263%
2017-03-05 | 12 | 7102 | 110.7621 | 1.56% | 18.3359 | 0.2582% | 129.0981 | 1.818% | 1433 | 7083.6641 | 6972.9019 | 1.588% | 0.263%
2017-03-20 | 22 | 7104 | 110.7695 | 1.559% | 18.3402 | 0.2582% | 129.1097 | 1.817% | 1434 | 7085.6598 | 6974.8903 | 1.588% | 0.2629%
2017-04-27 | 11 | 7107 | 110.7805 | 1.559% | 18.3466 | 0.2581% | 129.1271 | 1.817% | 1435 | 7088.6534 | 6977.8729 | 1.588% | 0.2629%
2017-05-16 | 10 | 7107 | 110.7805 | 1.559% | 18.3466 | 0.2581% | 129.1271 | 1.817% | 1436 | 7088.6534 | 6977.8729 | 1.588% | 0.2629%
2017-04-30 | 10 | 7110 | 110.7915 | 1.558% | 18.3531 | 0.2581% | 129.1445 | 1.816% | 1437 | 7091.6469 | 6980.8555 | 1.587% | 0.2629%
2017-04-03 | 20 | 7111 | 110.7951 | 1.558% | 18.3552 | 0.2581% | 129.1503 | 1.816% | 1438 | 7092.6448 | 6981.8497 | 1.587% | 0.2629%
2017-04-05 | 21 | 7112 | 110.7988 | 1.558% | 18.3573 | 0.2581% | 129.1561 | 1.816% | 1439 | 7093.6427 | 6982.8439 | 1.587% | 0.2629%
2017-03-28 | 22 | 7117 | 110.8171 | 1.557% | 18.368 | 0.2581% | 129.1851 | 1.815% | 1440 | 7098.632 | 6987.8149 | 1.586% | 0.2629%
2017-03-01 | 15 | 7123 | 110.8391 | 1.556% | 18.3809 | 0.258% | 129.22 | 1.814% | 1441 | 7104.6191 | 6993.78 | 1.585% | 0.2628%
2017-05-11 | 10 | 7123 | 110.8391 | 1.556% | 18.3809 | 0.258% | 129.22 | 1.814% | 1442 | 7104.6191 | 6993.78 | 1.585% | 0.2628%
2017-03-18 | 9 | 7124 | 110.8427 | 1.556% | 18.383 | 0.258% | 129.2258 | 1.814% | 1443 | 7105.617 | 6994.7742 | 1.585% | 0.2628%
2017-04-14 | 21 | 7126 | 110.8501 | 1.556% | 18.3873 | 0.258% | 129.2374 | 1.814% | 1444 | 7107.6127 | 6996.7626 | 1.584% | 0.2628%
2017-03-27 | 19 | 7127 | 110.8537 | 1.555% | 18.3894 | 0.258% | 129.2432 | 1.813% | 1445 | 7108.6106 | 6997.7568 | 1.584% | 0.2628%
2017-04-19 | 18 | 7128 | 110.8574 | 1.555% | 18.3916 | 0.258% | 129.249 | 1.813% | 1446 | 7109.6084 | 6998.751 | 1.584% | 0.2628%
2017-03-28 | 17 | 7129 | 110.8611 | 1.555% | 18.3937 | 0.258% | 129.2548 | 1.813% | 1447 | 7110.6063 | 6999.7452 | 1.584% | 0.2628%
2017-04-24 | 20 | 7132 | 110.8721 | 1.555% | 18.4001 | 0.258% | 129.2722 | 1.813% | 1448 | 7113.5999 | 7002.7278 | 1.583% | 0.2628%
2017-03-23 | 13 | 7133 | 110.8757 | 1.554% | 18.4023 | 0.258% | 129.278 | 1.812% | 1449 | 7114.5977 | 7003.722 | 1.583% | 0.2628%
2017-04-16 | 15 | 7133 | 110.8757 | 1.554% | 18.4023 | 0.258% | 129.278 | 1.812% | 1450 | 7114.5977 | 7003.722 | 1.583% | 0.2628%
2017-04-19 | 19 | 7134 | 110.8794 | 1.554% | 18.4044 | 0.258% | 129.2838 | 1.812% | 1451 | 7115.5956 | 7004.7162 | 1.583% | 0.2627%
2017-03-01 | 16 | 7135 | 110.883 | 1.554% | 18.4066 | 0.258% | 129.2896 | 1.812% | 1452 | 7116.5934 | 7005.7104 | 1.583% | 0.2627%
2017-04-04 | 14 | 7137 | 110.8904 | 1.554% | 18.4108 | 0.258% | 129.3012 | 1.812% | 1453 | 7118.5892 | 7007.6988 | 1.582% | 0.2627%
2017-04-05 | 20 | 7137 | 110.8904 | 1.554% | 18.4108 | 0.258% | 129.3012 | 1.812% | 1454 | 7118.5892 | 7007.6988 | 1.582% | 0.2627%
2017-05-22 | 9 | 7137 | 110.8904 | 1.554% | 18.4108 | 0.258% | 129.3012 | 1.812% | 1455 | 7118.5892 | 7007.6988 | 1.582% | 0.2627%
2017-03-06 | 3 | 7138 | 110.894 | 1.554% | 18.413 | 0.258% | 129.307 | 1.812% | 1456 | 7119.587 | 7008.693 | 1.582% | 0.2627%
2017-03-06 | 12 | 7138 | 110.894 | 1.554% | 18.413 | 0.258% | 129.307 | 1.812% | 1457 | 7119.587 | 7008.693 | 1.582% | 0.2627%
2017-04-24 | 21 | 7139 | 110.8977 | 1.553% | 18.4151 | 0.258% | 129.3128 | 1.811% | 1458 | 7120.5849 | 7009.6872 | 1.582% | 0.2627%
2017-05-31 | 8 | 7143 | 110.9124 | 1.553% | 18.4237 | 0.2579% | 129.336 | 1.811% | 1459 | 7124.5763 | 7013.664 | 1.581% | 0.2627%
2017-03-04 | 19 | 7150 | 110.938 | 1.552% | 18.4387 | 0.2579% | 129.3767 | 1.809% | 1460 | 7131.5613 | 7020.6233 | 1.58% | 0.2626%
2017-05-02 | 11 | 7150 | 110.938 | 1.552% | 18.4387 | 0.2579% | 129.3767 | 1.809% | 1461 | 7131.5613 | 7020.6233 | 1.58% | 0.2626%
2017-05-19 | 24 | 7150 | 110.938 | 1.552% | 18.4387 | 0.2579% | 129.3767 | 1.809% | 1462 | 7131.5613 | 7020.6233 | 1.58% | 0.2626%
2017-03-19 | 12 | 7155 | 110.9563 | 1.551% | 18.4494 | 0.2579% | 129.4057 | 1.809% | 1463 | 7136.5506 | 7025.5943 | 1.579% | 0.2626%
2017-04-19 | 20 | 7156 | 110.96 | 1.551% | 18.4515 | 0.2578% | 129.4115 | 1.808% | 1464 | 7137.5485 | 7026.5885 | 1.579% | 0.2626%
2017-05-20 | 24 | 7157 | 110.9636 | 1.55% | 18.4536 | 0.2578% | 129.4173 | 1.808% | 1465 | 7138.5464 | 7027.5827 | 1.579% | 0.2626%
2017-03-01 | 18 | 7162 | 110.982 | 1.55% | 18.4643 | 0.2578% | 129.4463 | 1.807% | 1466 | 7143.5357 | 7032.5537 | 1.578% | 0.2626%
2017-04-25 | 21 | 7163 | 110.9856 | 1.549% | 18.4665 | 0.2578% | 129.4521 | 1.807% | 1467 | 7144.5335 | 7033.5479 | 1.578% | 0.2625%
2017-04-16 | 21 | 7168 | 111.0039 | 1.549% | 18.4772 | 0.2578% | 129.4811 | 1.806% | 1468 | 7149.5228 | 7038.5189 | 1.577% | 0.2625%
2017-03-11 | 12 | 7169 | 111.0076 | 1.548% | 18.4793 | 0.2578% | 129.4869 | 1.806% | 1469 | 7150.5207 | 7039.5131 | 1.577% | 0.2625%
2017-03-20 | 3 | 7169 | 111.0076 | 1.548% | 18.4793 | 0.2578% | 129.4869 | 1.806% | 1470 | 7150.5207 | 7039.5131 | 1.577% | 0.2625%
2017-05-28 | 10 | 7171 | 111.0149 | 1.548% | 18.4836 | 0.2578% | 129.4985 | 1.806% | 1471 | 7152.5164 | 7041.5015 | 1.577% | 0.2625%
2017-05-05 | 11 | 7172 | 111.0186 | 1.548% | 18.4857 | 0.2577% | 129.5043 | 1.806% | 1472 | 7153.5143 | 7042.4957 | 1.576% | 0.2625%
2017-03-17 | 20 | 7174 | 111.0259 | 1.548% | 18.49 | 0.2577% | 129.5159 | 1.805% | 1473 | 7155.51 | 7044.4841 | 1.576% | 0.2625%
2017-04-29 | 24 | 7175 | 111.0296 | 1.547% | 18.4922 | 0.2577% | 129.5217 | 1.805% | 1474 | 7156.5078 | 7045.4783 | 1.576% | 0.2625%
2017-03-23 | 20 | 7176 | 111.0332 | 1.547% | 18.4943 | 0.2577% | 129.5275 | 1.805% | 1475 | 7157.5057 | 7046.4725 | 1.576% | 0.2625%
2017-03-22 | 21 | 7183 | 111.0589 | 1.546% | 18.5093 | 0.2577% | 129.5682 | 1.804% | 1476 | 7164.4907 | 7053.4318 | 1.575% | 0.2624%
2017-05-30 | 24 | 7183 | 111.0589 | 1.546% | 18.5093 | 0.2577% | 129.5682 | 1.804% | 1477 | 7164.4907 | 7053.4318 | 1.575% | 0.2624%
2017-03-28 | 19 | 7185 | 111.0662 | 1.546% | 18.5136 | 0.2577% | 129.5798 | 1.803% | 1478 | 7166.4864 | 7055.4202 | 1.574% | 0.2624%
2017-03-06 | 19 | 7186 | 111.0699 | 1.546% | 18.5157 | 0.2577% | 129.5856 | 1.803% | 1479 | 7167.4843 | 7056.4144 | 1.574% | 0.2624%
2017-03-07 | 9 | 7187 | 111.0735 | 1.545% | 18.5178 | 0.2577% | 129.5914 | 1.803% | 1480 | 7168.4822 | 7057.4086 | 1.574% | 0.2624%
2017-03-21 | 20 | 7189 | 111.0809 | 1.545% | 18.5221 | 0.2576% | 129.603 | 1.803% | 1481 | 7170.4779 | 7059.397 | 1.574% | 0.2624%
2017-03-05 | 19 | 7196 | 111.1065 | 1.544% | 18.5371 | 0.2576% | 129.6436 | 1.802% | 1482 | 7177.4629 | 7066.3564 | 1.572% | 0.2623%
2017-03-14 | 3 | 7196 | 111.1065 | 1.544% | 18.5371 | 0.2576% | 129.6436 | 1.802% | 1483 | 7177.4629 | 7066.3564 | 1.572% | 0.2623%
2017-04-20 | 23 | 7198 | 111.1138 | 1.544% | 18.5414 | 0.2576% | 129.6552 | 1.801% | 1484 | 7179.4586 | 7068.3448 | 1.572% | 0.2623%
2017-05-14 | 17 | 7199 | 111.1175 | 1.544% | 18.5435 | 0.2576% | 129.661 | 1.801% | 1485 | 7180.4565 | 7069.339 | 1.572% | 0.2623%
2017-03-19 | 8 | 7203 | 111.1322 | 1.543% | 18.5521 | 0.2576% | 129.6842 | 1.8% | 1486 | 7184.4479 | 7073.3158 | 1.571% | 0.2623%
2017-04-07 | 8 | 7204 | 111.1358 | 1.543% | 18.5542 | 0.2576% | 129.69 | 1.8% | 1487 | 7185.4458 | 7074.31 | 1.571% | 0.2623%
2017-05-14 | 22 | 7204 | 111.1358 | 1.543% | 18.5542 | 0.2576% | 129.69 | 1.8% | 1488 | 7185.4458 | 7074.31 | 1.571% | 0.2623%
2017-03-14 | 2 | 7209 | 111.1541 | 1.542% | 18.5649 | 0.2575% | 129.719 | 1.799% | 1489 | 7190.4351 | 7079.281 | 1.57% | 0.2622%
2017-04-22 | 22 | 7209 | 111.1541 | 1.542% | 18.5649 | 0.2575% | 129.719 | 1.799% | 1490 | 7190.4351 | 7079.281 | 1.57% | 0.2622%
2017-05-29 | 10 | 7216 | 111.1798 | 1.541% | 18.5799 | 0.2575% | 129.7597 | 1.798% | 1491 | 7197.4201 | 7086.2403 | 1.569% | 0.2622%
2017-04-15 | 15 | 7220 | 111.1944 | 1.54% | 18.5884 | 0.2575% | 129.7829 | 1.798% | 1492 | 7201.4116 | 7090.2171 | 1.568% | 0.2622%
2017-05-30 | 9 | 7222 | 111.2018 | 1.54% | 18.5927 | 0.2574% | 129.7945 | 1.797% | 1493 | 7203.4073 | 7092.2055 | 1.568% | 0.2622%
2017-04-28 | 9 | 7225 | 111.2128 | 1.539% | 18.5991 | 0.2574% | 129.8119 | 1.797% | 1494 | 7206.4009 | 7095.1881 | 1.567% | 0.2621%
2017-05-17 | 9 | 7226 | 111.2164 | 1.539% | 18.6013 | 0.2574% | 129.8177 | 1.797% | 1495 | 7207.3987 | 7096.1823 | 1.567% | 0.2621%
2017-04-11 | 22 | 7228 | 111.2237 | 1.539% | 18.6056 | 0.2574% | 129.8293 | 1.796% | 1496 | 7209.3944 | 7098.1707 | 1.567% | 0.2621%
2017-04-16 | 19 | 7228 | 111.2237 | 1.539% | 18.6056 | 0.2574% | 129.8293 | 1.796% | 1497 | 7209.3944 | 7098.1707 | 1.567% | 0.2621%
2017-05-03 | 13 | 7231 | 111.2347 | 1.538% | 18.612 | 0.2574% | 129.8467 | 1.796% | 1498 | 7212.388 | 7101.1533 | 1.566% | 0.2621%
2017-05-05 | 19 | 7232 | 111.2384 | 1.538% | 18.6141 | 0.2574% | 129.8525 | 1.796% | 1499 | 7213.3859 | 7102.1475 | 1.566% | 0.2621%
2017-03-29 | 21 | 7239 | 111.264 | 1.537% | 18.6291 | 0.2573% | 129.8931 | 1.794% | 1500 | 7220.3709 | 7109.1069 | 1.565% | 0.262%
2017-04-13 | 14 | 7239 | 111.264 | 1.537% | 18.6291 | 0.2573% | 129.8931 | 1.794% | 1501 | 7220.3709 | 7109.1069 | 1.565% | 0.262%
2017-05-04 | 12 | 7239 | 111.264 | 1.537% | 18.6291 | 0.2573% | 129.8931 | 1.794% | 1502 | 7220.3709 | 7109.1069 | 1.565% | 0.262%
2017-04-18 | 21 | 7245 | 111.286 | 1.536% | 18.6419 | 0.2573% | 129.928 | 1.793% | 1503 | 7226.3581 | 7115.072 | 1.564% | 0.262%
2017-05-19 | 9 | 7245 | 111.286 | 1.536% | 18.6419 | 0.2573% | 129.928 | 1.793% | 1504 | 7226.3581 | 7115.072 | 1.564% | 0.262%
2017-05-17 | 24 | 7249 | 111.3007 | 1.535% | 18.6505 | 0.2573% | 129.9512 | 1.793% | 1505 | 7230.3495 | 7119.0488 | 1.563% | 0.262%
2017-05-05 | 12 | 7251 | 111.308 | 1.535% | 18.6548 | 0.2573% | 129.9628 | 1.792% | 1506 | 7232.3452 | 7121.0372 | 1.563% | 0.262%
2017-05-26 | 12 | 7253 | 111.3153 | 1.535% | 18.6591 | 0.2573% | 129.9744 | 1.792% | 1507 | 7234.3409 | 7123.0256 | 1.563% | 0.262%
2017-04-15 | 20 | 7255 | 111.3227 | 1.534% | 18.6633 | 0.2572% | 129.986 | 1.792% | 1508 | 7236.3367 | 7125.014 | 1.562% | 0.2619%
2017-04-27 | 23 | 7255 | 111.3227 | 1.534% | 18.6633 | 0.2572% | 129.986 | 1.792% | 1509 | 7236.3367 | 7125.014 | 1.562% | 0.2619%
2017-04-11 | 15 | 7256 | 111.3263 | 1.534% | 18.6655 | 0.2572% | 129.9918 | 1.792% | 1510 | 7237.3345 | 7126.0082 | 1.562% | 0.2619%
2017-05-24 | 11 | 7256 | 111.3263 | 1.534% | 18.6655 | 0.2572% | 129.9918 | 1.792% | 1511 | 7237.3345 | 7126.0082 | 1.562% | 0.2619%
2017-03-01 | 21 | 7257 | 111.33 | 1.534% | 18.6676 | 0.2572% | 129.9976 | 1.791% | 1512 | 7238.3324 | 7127.0024 | 1.562% | 0.2619%
2017-05-23 | 11 | 7260 | 111.341 | 1.534% | 18.674 | 0.2572% | 130.015 | 1.791% | 1513 | 7241.326 | 7129.985 | 1.562% | 0.2619%
2017-03-12 | 7 | 7272 | 111.3849 | 1.532% | 18.6997 | 0.2571% | 130.0847 | 1.789% | 1514 | 7253.3003 | 7141.9153 | 1.56% | 0.2618%
2017-03-28 | 18 | 7280 | 111.4142 | 1.53% | 18.7168 | 0.2571% | 130.1311 | 1.788% | 1515 | 7261.2832 | 7149.8689 | 1.558% | 0.2618%
2017-04-10 | 21 | 7280 | 111.4142 | 1.53% | 18.7168 | 0.2571% | 130.1311 | 1.788% | 1516 | 7261.2832 | 7149.8689 | 1.558% | 0.2618%
2017-05-14 | 20 | 7281 | 111.4179 | 1.53% | 18.719 | 0.2571% | 130.1369 | 1.787% | 1517 | 7262.281 | 7150.8631 | 1.558% | 0.2618%
2017-05-14 | 21 | 7284 | 111.4289 | 1.53% | 18.7254 | 0.2571% | 130.1543 | 1.787% | 1518 | 7265.2746 | 7153.8457 | 1.558% | 0.2618%
2017-05-05 | 13 | 7285 | 111.4326 | 1.53% | 18.7275 | 0.2571% | 130.1601 | 1.787% | 1519 | 7266.2725 | 7154.8399 | 1.557% | 0.2617%
2017-05-18 | 24 | 7286 | 111.4362 | 1.529% | 18.7297 | 0.2571% | 130.1659 | 1.787% | 1520 | 7267.2703 | 7155.8341 | 1.557% | 0.2617%
2017-04-15 | 21 | 7287 | 111.4399 | 1.529% | 18.7318 | 0.2571% | 130.1717 | 1.786% | 1521 | 7268.2682 | 7156.8283 | 1.557% | 0.2617%
2017-05-10 | 23 | 7291 | 111.4545 | 1.529% | 18.7404 | 0.257% | 130.1949 | 1.786% | 1522 | 7272.2596 | 7160.8051 | 1.556% | 0.2617%
2017-05-25 | 20 | 7291 | 111.4545 | 1.529% | 18.7404 | 0.257% | 130.1949 | 1.786% | 1523 | 7272.2596 | 7160.8051 | 1.556% | 0.2617%
2017-03-06 | 21 | 7295 | 111.4692 | 1.528% | 18.7489 | 0.257% | 130.2181 | 1.785% | 1524 | 7276.2511 | 7164.7819 | 1.556% | 0.2617%
2017-03-14 | 1 | 7295 | 111.4692 | 1.528% | 18.7489 | 0.257% | 130.2181 | 1.785% | 1525 | 7276.2511 | 7164.7819 | 1.556% | 0.2617%
2017-04-12 | 14 | 7296 | 111.4729 | 1.528% | 18.7511 | 0.257% | 130.2239 | 1.785% | 1526 | 7277.2489 | 7165.7761 | 1.556% | 0.2617%
2017-04-26 | 14 | 7296 | 111.4729 | 1.528% | 18.7511 | 0.257% | 130.2239 | 1.785% | 1527 | 7277.2489 | 7165.7761 | 1.556% | 0.2617%
2017-03-11 | 19 | 7297 | 111.4765 | 1.528% | 18.7532 | 0.257% | 130.2297 | 1.785% | 1528 | 7278.2468 | 7166.7703 | 1.555% | 0.2617%
2017-04-08 | 8 | 7298 | 111.4802 | 1.528% | 18.7554 | 0.257% | 130.2355 | 1.785% | 1529 | 7279.2446 | 7167.7645 | 1.555% | 0.2617%
2017-03-14 | 4 | 7299 | 111.4839 | 1.527% | 18.7575 | 0.257% | 130.2413 | 1.784% | 1530 | 7280.2425 | 7168.7587 | 1.555% | 0.2617%
2017-03-17 | 22 | 7301 | 111.4912 | 1.527% | 18.7618 | 0.257% | 130.253 | 1.784% | 1531 | 7282.2382 | 7170.747 | 1.555% | 0.2616%
2017-03-20 | 21 | 7302 | 111.4948 | 1.527% | 18.7639 | 0.257% | 130.2588 | 1.784% | 1532 | 7283.2361 | 7171.7412 | 1.555% | 0.2616%
2017-04-16 | 16 | 7302 | 111.4948 | 1.527% | 18.7639 | 0.257% | 130.2588 | 1.784% | 1533 | 7283.2361 | 7171.7412 | 1.555% | 0.2616%
2017-03-17 | 14 | 7306 | 111.5095 | 1.526% | 18.7725 | 0.2569% | 130.282 | 1.783% | 1534 | 7287.2275 | 7175.718 | 1.554% | 0.2616%
2017-03-24 | 5 | 7307 | 111.5132 | 1.526% | 18.7746 | 0.2569% | 130.2878 | 1.783% | 1535 | 7288.2254 | 7176.7122 | 1.554% | 0.2616%
2017-03-19 | 23 | 7313 | 111.5351 | 1.525% | 18.7874 | 0.2569% | 130.3226 | 1.782% | 1536 | 7294.2126 | 7182.6774 | 1.553% | 0.2616%
2017-05-25 | 21 | 7314 | 111.5388 | 1.525% | 18.7896 | 0.2569% | 130.3284 | 1.782% | 1537 | 7295.2104 | 7183.6716 | 1.553% | 0.2616%
2017-04-04 | 15 | 7315 | 111.5425 | 1.525% | 18.7917 | 0.2569% | 130.3342 | 1.782% | 1538 | 7296.2083 | 7184.6658 | 1.553% | 0.2616%
2017-03-28 | 20 | 7316 | 111.5461 | 1.525% | 18.7939 | 0.2569% | 130.34 | 1.782% | 1539 | 7297.2061 | 7185.66 | 1.552% | 0.2615%
2017-03-11 | 6 | 7321 | 111.5644 | 1.524% | 18.8046 | 0.2569% | 130.369 | 1.781% | 1540 | 7302.1954 | 7190.631 | 1.552% | 0.2615%
2017-04-14 | 19 | 7321 | 111.5644 | 1.524% | 18.8046 | 0.2569% | 130.369 | 1.781% | 1541 | 7302.1954 | 7190.631 | 1.552% | 0.2615%
2017-05-01 | 9 | 7322 | 111.5681 | 1.524% | 18.8067 | 0.2569% | 130.3748 | 1.781% | 1542 | 7303.1933 | 7191.6252 | 1.551% | 0.2615%
2017-04-13 | 20 | 7324 | 111.5754 | 1.523% | 18.811 | 0.2568% | 130.3864 | 1.78% | 1543 | 7305.189 | 7193.6136 | 1.551% | 0.2615%
2017-03-11 | 23 | 7327 | 111.5864 | 1.523% | 18.8174 | 0.2568% | 130.4038 | 1.78% | 1544 | 7308.1826 | 7196.5962 | 1.551% | 0.2615%
2017-05-15 | 11 | 7327 | 111.5864 | 1.523% | 18.8174 | 0.2568% | 130.4038 | 1.78% | 1545 | 7308.1826 | 7196.5962 | 1.551% | 0.2615%
2017-04-14 | 17 | 7329 | 111.5938 | 1.523% | 18.8217 | 0.2568% | 130.4154 | 1.779% | 1546 | 7310.1783 | 7198.5846 | 1.55% | 0.2615%
2017-04-30 | 23 | 7329 | 111.5938 | 1.523% | 18.8217 | 0.2568% | 130.4154 | 1.779% | 1547 | 7310.1783 | 7198.5846 | 1.55% | 0.2615%
2017-03-05 | 23 | 7330 | 111.5974 | 1.522% | 18.8238 | 0.2568% | 130.4212 | 1.779% | 1548 | 7311.1762 | 7199.5788 | 1.55% | 0.2615%
2017-03-27 | 20 | 7330 | 111.5974 | 1.522% | 18.8238 | 0.2568% | 130.4212 | 1.779% | 1549 | 7311.1762 | 7199.5788 | 1.55% | 0.2615%
2017-03-21 | 9 | 7335 | 111.6157 | 1.522% | 18.8345 | 0.2568% | 130.4503 | 1.778% | 1550 | 7316.1655 | 7204.5497 | 1.549% | 0.2614%
2017-05-02 | 12 | 7336 | 111.6194 | 1.522% | 18.8367 | 0.2568% | 130.4561 | 1.778% | 1551 | 7317.1633 | 7205.5439 | 1.549% | 0.2614%
2017-05-25 | 11 | 7338 | 111.6267 | 1.521% | 18.8409 | 0.2568% | 130.4677 | 1.778% | 1552 | 7319.1591 | 7207.5323 | 1.549% | 0.2614%
2017-03-06 | 4 | 7339 | 111.6304 | 1.521% | 18.8431 | 0.2568% | 130.4735 | 1.778% | 1553 | 7320.1569 | 7208.5265 | 1.549% | 0.2614%
2017-05-23 | 22 | 7339 | 111.6304 | 1.521% | 18.8431 | 0.2568% | 130.4735 | 1.778% | 1554 | 7320.1569 | 7208.5265 | 1.549% | 0.2614%
2017-04-12 | 22 | 7341 | 111.6377 | 1.521% | 18.8474 | 0.2567% | 130.4851 | 1.777% | 1555 | 7322.1526 | 7210.5149 | 1.548% | 0.2614%
2017-04-11 | 20 | 7342 | 111.6414 | 1.521% | 18.8495 | 0.2567% | 130.4909 | 1.777% | 1556 | 7323.1505 | 7211.5091 | 1.548% | 0.2614%
2017-03-18 | 13 | 7348 | 111.6634 | 1.52% | 18.8623 | 0.2567% | 130.5257 | 1.776% | 1557 | 7329.1377 | 7217.4743 | 1.547% | 0.2613%
2017-05-18 | 9 | 7348 | 111.6634 | 1.52% | 18.8623 | 0.2567% | 130.5257 | 1.776% | 1558 | 7329.1377 | 7217.4743 | 1.547% | 0.2613%
2017-04-19 | 21 | 7352 | 111.678 | 1.519% | 18.8709 | 0.2567% | 130.5489 | 1.776% | 1559 | 7333.1291 | 7221.4511 | 1.546% | 0.2613%
2017-04-21 | 23 | 7352 | 111.678 | 1.519% | 18.8709 | 0.2567% | 130.5489 | 1.776% | 1560 | 7333.1291 | 7221.4511 | 1.546% | 0.2613%
2017-04-04 | 22 | 7355 | 111.689 | 1.519% | 18.8773 | 0.2567% | 130.5663 | 1.775% | 1561 | 7336.1227 | 7224.4337 | 1.546% | 0.2613%
2017-03-19 | 11 | 7358 | 111.7 | 1.518% | 18.8837 | 0.2566% | 130.5837 | 1.775% | 1562 | 7339.1163 | 7227.4163 | 1.546% | 0.2613%
2017-05-21 | 14 | 7364 | 111.722 | 1.517% | 18.8966 | 0.2566% | 130.6186 | 1.774% | 1563 | 7345.1034 | 7233.3814 | 1.545% | 0.2612%
2017-03-02 | 22 | 7367 | 111.733 | 1.517% | 18.903 | 0.2566% | 130.636 | 1.773% | 1564 | 7348.097 | 7236.364 | 1.544% | 0.2612%
2017-04-16 | 17 | 7367 | 111.733 | 1.517% | 18.903 | 0.2566% | 130.636 | 1.773% | 1565 | 7348.097 | 7236.364 | 1.544% | 0.2612%
2017-04-16 | 18 | 7367 | 111.733 | 1.517% | 18.903 | 0.2566% | 130.636 | 1.773% | 1566 | 7348.097 | 7236.364 | 1.544% | 0.2612%
2017-03-05 | 1 | 7371 | 111.7476 | 1.516% | 18.9116 | 0.2566% | 130.6592 | 1.773% | 1567 | 7352.0884 | 7240.3408 | 1.543% | 0.2612%
2017-03-05 | 2 | 7374 | 111.7586 | 1.516% | 18.918 | 0.2565% | 130.6766 | 1.772% | 1568 | 7355.082 | 7243.3234 | 1.543% | 0.2612%
2017-04-11 | 16 | 7386 | 111.8026 | 1.514% | 18.9437 | 0.2565% | 130.7462 | 1.77% | 1569 | 7367.0563 | 7255.2538 | 1.541% | 0.2611%
2017-04-20 | 13 | 7387 | 111.8062 | 1.514% | 18.9458 | 0.2565% | 130.752 | 1.77% | 1570 | 7368.0542 | 7256.248 | 1.541% | 0.2611%
2017-05-23 | 12 | 7391 | 111.8209 | 1.513% | 18.9544 | 0.2565% | 130.7752 | 1.769% | 1571 | 7372.0456 | 7260.2248 | 1.54% | 0.2611%
2017-03-23 | 23 | 7394 | 111.8319 | 1.512% | 18.9608 | 0.2564% | 130.7927 | 1.769% | 1572 | 7375.0392 | 7263.2073 | 1.54% | 0.2611%
2017-04-08 | 9 | 7394 | 111.8319 | 1.512% | 18.9608 | 0.2564% | 130.7927 | 1.769% | 1573 | 7375.0392 | 7263.2073 | 1.54% | 0.2611%
2017-03-04 | 1 | 7395 | 111.8355 | 1.512% | 18.9629 | 0.2564% | 130.7985 | 1.769% | 1574 | 7376.0371 | 7264.2015 | 1.54% | 0.261%
2017-05-11 | 23 | 7395 | 111.8355 | 1.512% | 18.9629 | 0.2564% | 130.7985 | 1.769% | 1575 | 7376.0371 | 7264.2015 | 1.54% | 0.261%
2017-03-18 | 10 | 7400 | 111.8539 | 1.512% | 18.9736 | 0.2564% | 130.8275 | 1.768% | 1576 | 7381.0264 | 7269.1725 | 1.539% | 0.261%
2017-05-22 | 23 | 7400 | 111.8539 | 1.512% | 18.9736 | 0.2564% | 130.8275 | 1.768% | 1577 | 7381.0264 | 7269.1725 | 1.539% | 0.261%
2017-05-14 | 18 | 7402 | 111.8612 | 1.511% | 18.9779 | 0.2564% | 130.8391 | 1.768% | 1578 | 7383.0221 | 7271.1609 | 1.538% | 0.261%
2017-03-17 | 21 | 7404 | 111.8685 | 1.511% | 18.9822 | 0.2564% | 130.8507 | 1.767% | 1579 | 7385.0178 | 7273.1493 | 1.538% | 0.261%
2017-03-21 | 21 | 7405 | 111.8722 | 1.511% | 18.9843 | 0.2564% | 130.8565 | 1.767% | 1580 | 7386.0157 | 7274.1435 | 1.538% | 0.261%
2017-05-22 | 10 | 7405 | 111.8722 | 1.511% | 18.9843 | 0.2564% | 130.8565 | 1.767% | 1581 | 7386.0157 | 7274.1435 | 1.538% | 0.261%
2017-04-17 | 13 | 7407 | 111.8795 | 1.51% | 18.9886 | 0.2564% | 130.8681 | 1.767% | 1582 | 7388.0114 | 7276.1319 | 1.538% | 0.261%
2017-03-27 | 21 | 7409 | 111.8868 | 1.51% | 18.9929 | 0.2563% | 130.8797 | 1.766% | 1583 | 7390.0071 | 7278.1203 | 1.537% | 0.261%
2017-03-21 | 8 | 7411 | 111.8942 | 1.51% | 18.9972 | 0.2563% | 130.8913 | 1.766% | 1584 | 7392.0028 | 7280.1087 | 1.537% | 0.2609%
2017-04-13 | 21 | 7411 | 111.8942 | 1.51% | 18.9972 | 0.2563% | 130.8913 | 1.766% | 1585 | 7392.0028 | 7280.1087 | 1.537% | 0.2609%
2017-05-10 | 13 | 7416 | 111.9125 | 1.509% | 19.0079 | 0.2563% | 130.9203 | 1.765% | 1586 | 7396.9921 | 7285.0797 | 1.536% | 0.2609%
2017-03-03 | 11 | 7420 | 111.9271 | 1.508% | 19.0164 | 0.2563% | 130.9435 | 1.765% | 1587 | 7400.9836 | 7289.0565 | 1.536% | 0.2609%
2017-05-02 | 22 | 7429 | 111.9601 | 1.507% | 19.0357 | 0.2562% | 130.9958 | 1.763% | 1588 | 7409.9643 | 7298.0042 | 1.534% | 0.2608%
2017-03-02 | 20 | 7442 | 112.0077 | 1.505% | 19.0635 | 0.2562% | 131.0712 | 1.761% | 1589 | 7422.9365 | 7310.9288 | 1.532% | 0.2608%
2017-05-14 | 19 | 7452 | 112.0444 | 1.504% | 19.0849 | 0.2561% | 131.1292 | 1.76% | 1590 | 7432.9151 | 7320.8708 | 1.53% | 0.2607%
2017-03-03 | 19 | 7453 | 112.048 | 1.503% | 19.087 | 0.2561% | 131.1351 | 1.759% | 1591 | 7433.913 | 7321.8649 | 1.53% | 0.2607%
2017-03-04 | 2 | 7453 | 112.048 | 1.503% | 19.087 | 0.2561% | 131.1351 | 1.759% | 1592 | 7433.913 | 7321.8649 | 1.53% | 0.2607%
2017-03-06 | 20 | 7453 | 112.048 | 1.503% | 19.087 | 0.2561% | 131.1351 | 1.759% | 1593 | 7433.913 | 7321.8649 | 1.53% | 0.2607%
2017-05-20 | 10 | 7454 | 112.0517 | 1.503% | 19.0892 | 0.2561% | 131.1409 | 1.759% | 1594 | 7434.9108 | 7322.8591 | 1.53% | 0.2607%
2017-03-07 | 8 | 7456 | 112.059 | 1.503% | 19.0934 | 0.2561% | 131.1525 | 1.759% | 1595 | 7436.9066 | 7324.8475 | 1.53% | 0.2607%
2017-03-28 | 21 | 7456 | 112.059 | 1.503% | 19.0934 | 0.2561% | 131.1525 | 1.759% | 1596 | 7436.9066 | 7324.8475 | 1.53% | 0.2607%
2017-05-23 | 13 | 7456 | 112.059 | 1.503% | 19.0934 | 0.2561% | 131.1525 | 1.759% | 1597 | 7436.9066 | 7324.8475 | 1.53% | 0.2607%
2017-05-15 | 23 | 7460 | 112.0737 | 1.502% | 19.102 | 0.2561% | 131.1757 | 1.758% | 1598 | 7440.898 | 7328.8243 | 1.529% | 0.2606%
2017-03-04 | 24 | 7461 | 112.0773 | 1.502% | 19.1041 | 0.2561% | 131.1815 | 1.758% | 1599 | 7441.8959 | 7329.8185 | 1.529% | 0.2606%
2017-04-14 | 18 | 7461 | 112.0773 | 1.502% | 19.1041 | 0.2561% | 131.1815 | 1.758% | 1600 | 7441.8959 | 7329.8185 | 1.529% | 0.2606%
2017-04-28 | 24 | 7463 | 112.0847 | 1.502% | 19.1084 | 0.256% | 131.1931 | 1.758% | 1601 | 7443.8916 | 7331.8069 | 1.529% | 0.2606%
2017-04-13 | 15 | 7464 | 112.0883 | 1.502% | 19.1106 | 0.256% | 131.1989 | 1.758% | 1602 | 7444.8894 | 7332.8011 | 1.529% | 0.2606%
2017-05-24 | 12 | 7464 | 112.0883 | 1.502% | 19.1106 | 0.256% | 131.1989 | 1.758% | 1603 | 7444.8894 | 7332.8011 | 1.529% | 0.2606%
2017-05-31 | 9 | 7464 | 112.0883 | 1.502% | 19.1106 | 0.256% | 131.1989 | 1.758% | 1604 | 7444.8894 | 7332.8011 | 1.529% | 0.2606%
2017-05-05 | 14 | 7466 | 112.0957 | 1.501% | 19.1148 | 0.256% | 131.2105 | 1.757% | 1605 | 7446.8852 | 7334.7895 | 1.528% | 0.2606%
2017-05-24 | 22 | 7472 | 112.1176 | 1.501% | 19.1277 | 0.256% | 131.2453 | 1.756% | 1606 | 7452.8723 | 7340.7547 | 1.527% | 0.2606%
2017-04-15 | 16 | 7473 | 112.1213 | 1.5% | 19.1298 | 0.256% | 131.2511 | 1.756% | 1607 | 7453.8702 | 7341.7489 | 1.527% | 0.2606%
2017-03-12 | 18 | 7474 | 112.125 | 1.5% | 19.132 | 0.256% | 131.2569 | 1.756% | 1608 | 7454.868 | 7342.7431 | 1.527% | 0.2606%
2017-03-04 | 12 | 7475 | 112.1286 | 1.5% | 19.1341 | 0.256% | 131.2627 | 1.756% | 1609 | 7455.8659 | 7343.7373 | 1.527% | 0.2605%
2017-03-20 | 4 | 7478 | 112.1396 | 1.5% | 19.1405 | 0.256% | 131.2801 | 1.756% | 1610 | 7458.8595 | 7346.7199 | 1.526% | 0.2605%
2017-03-23 | 6 | 7481 | 112.1506 | 1.499% | 19.1469 | 0.2559% | 131.2975 | 1.755% | 1611 | 7461.8531 | 7349.7025 | 1.526% | 0.2605%
2017-03-24 | 11 | 7493 | 112.1946 | 1.497% | 19.1726 | 0.2559% | 131.3672 | 1.753% | 1612 | 7473.8274 | 7361.6328 | 1.524% | 0.2604%
2017-04-17 | 22 | 7493 | 112.1946 | 1.497% | 19.1726 | 0.2559% | 131.3672 | 1.753% | 1613 | 7473.8274 | 7361.6328 | 1.524% | 0.2604%
2017-03-03 | 24 | 7495 | 112.2019 | 1.497% | 19.1769 | 0.2559% | 131.3788 | 1.753% | 1614 | 7475.8231 | 7363.6212 | 1.524% | 0.2604%
2017-03-07 | 7 | 7495 | 112.2019 | 1.497% | 19.1769 | 0.2559% | 131.3788 | 1.753% | 1615 | 7475.8231 | 7363.6212 | 1.524% | 0.2604%
2017-03-18 | 12 | 7496 | 112.2056 | 1.497% | 19.179 | 0.2559% | 131.3846 | 1.753% | 1616 | 7476.821 | 7364.6154 | 1.524% | 0.2604%
2017-03-02 | 21 | 7497 | 112.2092 | 1.497% | 19.1812 | 0.2559% | 131.3904 | 1.753% | 1617 | 7477.8188 | 7365.6096 | 1.523% | 0.2604%
2017-05-25 | 12 | 7498 | 112.2129 | 1.497% | 19.1833 | 0.2558% | 131.3962 | 1.752% | 1618 | 7478.8167 | 7366.6038 | 1.523% | 0.2604%
2017-05-11 | 11 | 7502 | 112.2275 | 1.496% | 19.1919 | 0.2558% | 131.4194 | 1.752% | 1619 | 7482.8081 | 7370.5806 | 1.523% | 0.2604%
2017-04-21 | 11 | 7503 | 112.2312 | 1.496% | 19.194 | 0.2558% | 131.4252 | 1.752% | 1620 | 7483.806 | 7371.5748 | 1.522% | 0.2604%
2017-05-04 | 13 | 7505 | 112.2385 | 1.496% | 19.1983 | 0.2558% | 131.4368 | 1.751% | 1621 | 7485.8017 | 7373.5632 | 1.522% | 0.2604%
2017-03-16 | 18 | 7506 | 112.2422 | 1.495% | 19.2004 | 0.2558% | 131.4426 | 1.751% | 1622 | 7486.7996 | 7374.5574 | 1.522% | 0.2604%
2017-05-30 | 10 | 7506 | 112.2422 | 1.495% | 19.2004 | 0.2558% | 131.4426 | 1.751% | 1623 | 7486.7996 | 7374.5574 | 1.522% | 0.2604%
2017-04-13 | 19 | 7508 | 112.2495 | 1.495% | 19.2047 | 0.2558% | 131.4542 | 1.751% | 1624 | 7488.7953 | 7376.5458 | 1.522% | 0.2603%
2017-05-23 | 14 | 7513 | 112.2678 | 1.494% | 19.2154 | 0.2558% | 131.4832 | 1.75% | 1625 | 7493.7846 | 7381.5168 | 1.521% | 0.2603%
2017-05-03 | 22 | 7515 | 112.2752 | 1.494% | 19.2197 | 0.2558% | 131.4949 | 1.75% | 1626 | 7495.7803 | 7383.5051 | 1.521% | 0.2603%
2017-03-12 | 17 | 7518 | 112.2862 | 1.494% | 19.2261 | 0.2557% | 131.5123 | 1.749% | 1627 | 7498.7739 | 7386.4877 | 1.52% | 0.2603%
2017-04-29 | 10 | 7518 | 112.2862 | 1.494% | 19.2261 | 0.2557% | 131.5123 | 1.749% | 1628 | 7498.7739 | 7386.4877 | 1.52% | 0.2603%
2017-05-23 | 20 | 7520 | 112.2935 | 1.493% | 19.2304 | 0.2557% | 131.5239 | 1.749% | 1629 | 7500.7696 | 7388.4761 | 1.52% | 0.2603%
2017-03-05 | 3 | 7523 | 112.3045 | 1.493% | 19.2368 | 0.2557% | 131.5413 | 1.749% | 1630 | 7503.7632 | 7391.4587 | 1.519% | 0.2603%
2017-03-01 | 19 | 7527 | 112.3191 | 1.492% | 19.2454 | 0.2557% | 131.5645 | 1.748% | 1631 | 7507.7546 | 7395.4355 | 1.519% | 0.2602%
2017-04-27 | 12 | 7528 | 112.3228 | 1.492% | 19.2475 | 0.2557% | 131.5703 | 1.748% | 1632 | 7508.7525 | 7396.4297 | 1.519% | 0.2602%
2017-04-04 | 16 | 7529 | 112.3265 | 1.492% | 19.2497 | 0.2557% | 131.5761 | 1.748% | 1633 | 7509.7503 | 7397.4239 | 1.518% | 0.2602%
2017-04-22 | 12 | 7529 | 112.3265 | 1.492% | 19.2497 | 0.2557% | 131.5761 | 1.748% | 1634 | 7509.7503 | 7397.4239 | 1.518% | 0.2602%
2017-03-14 | 16 | 7530 | 112.3301 | 1.492% | 19.2518 | 0.2557% | 131.5819 | 1.747% | 1635 | 7510.7482 | 7398.4181 | 1.518% | 0.2602%
2017-03-14 | 17 | 7530 | 112.3301 | 1.492% | 19.2518 | 0.2557% | 131.5819 | 1.747% | 1636 | 7510.7482 | 7398.4181 | 1.518% | 0.2602%
2017-05-16 | 11 | 7530 | 112.3301 | 1.492% | 19.2518 | 0.2557% | 131.5819 | 1.747% | 1637 | 7510.7482 | 7398.4181 | 1.518% | 0.2602%
2017-03-16 | 17 | 7531 | 112.3338 | 1.492% | 19.2539 | 0.2557% | 131.5877 | 1.747% | 1638 | 7511.7461 | 7399.4123 | 1.518% | 0.2602%
2017-05-25 | 19 | 7533 | 112.3411 | 1.491% | 19.2582 | 0.2557% | 131.5993 | 1.747% | 1639 | 7513.7418 | 7401.4007 | 1.518% | 0.2602%
2017-03-18 | 11 | 7534 | 112.3448 | 1.491% | 19.2603 | 0.2556% | 131.6051 | 1.747% | 1640 | 7514.7397 | 7402.3949 | 1.518% | 0.2602%
2017-03-19 | 22 | 7534 | 112.3448 | 1.491% | 19.2603 | 0.2556% | 131.6051 | 1.747% | 1641 | 7514.7397 | 7402.3949 | 1.518% | 0.2602%
2017-04-15 | 19 | 7534 | 112.3448 | 1.491% | 19.2603 | 0.2556% | 131.6051 | 1.747% | 1642 | 7514.7397 | 7402.3949 | 1.518% | 0.2602%
2017-04-30 | 11 | 7535 | 112.3484 | 1.491% | 19.2625 | 0.2556% | 131.6109 | 1.747% | 1643 | 7515.7375 | 7403.3891 | 1.518% | 0.2602%
2017-03-01 | 20 | 7538 | 112.3594 | 1.491% | 19.2689 | 0.2556% | 131.6283 | 1.746% | 1644 | 7518.7311 | 7406.3717 | 1.517% | 0.2602%
2017-04-11 | 21 | 7539 | 112.3631 | 1.49% | 19.271 | 0.2556% | 131.6341 | 1.746% | 1645 | 7519.729 | 7407.3659 | 1.517% | 0.2602%
2017-05-23 | 15 | 7546 | 112.3887 | 1.489% | 19.286 | 0.2556% | 131.6748 | 1.745% | 1646 | 7526.714 | 7414.3252 | 1.516% | 0.2601%
2017-03-05 | 11 | 7548 | 112.3961 | 1.489% | 19.2903 | 0.2556% | 131.6864 | 1.745% | 1647 | 7528.7097 | 7416.3136 | 1.516% | 0.2601%
2017-05-02 | 13 | 7548 | 112.3961 | 1.489% | 19.2903 | 0.2556% | 131.6864 | 1.745% | 1648 | 7528.7097 | 7416.3136 | 1.516% | 0.2601%
2017-05-26 | 13 | 7548 | 112.3961 | 1.489% | 19.2903 | 0.2556% | 131.6864 | 1.745% | 1649 | 7528.7097 | 7416.3136 | 1.516% | 0.2601%
2017-03-19 | 10 | 7561 | 112.4437 | 1.487% | 19.3181 | 0.2555% | 131.7618 | 1.743% | 1650 | 7541.6819 | 7429.2382 | 1.514% | 0.26%
2017-05-05 | 18 | 7564 | 112.4547 | 1.487% | 19.3245 | 0.2555% | 131.7792 | 1.742% | 1651 | 7544.6755 | 7432.2208 | 1.513% | 0.26%
2017-04-12 | 15 | 7565 | 112.4583 | 1.487% | 19.3267 | 0.2555% | 131.785 | 1.742% | 1652 | 7545.6733 | 7433.215 | 1.513% | 0.26%
2017-03-03 | 23 | 7566 | 112.462 | 1.486% | 19.3288 | 0.2555% | 131.7908 | 1.742% | 1653 | 7546.6712 | 7434.2092 | 1.513% | 0.26%
2017-03-19 | 9 | 7566 | 112.462 | 1.486% | 19.3288 | 0.2555% | 131.7908 | 1.742% | 1654 | 7546.6712 | 7434.2092 | 1.513% | 0.26%
2017-05-23 | 19 | 7566 | 112.462 | 1.486% | 19.3288 | 0.2555% | 131.7908 | 1.742% | 1655 | 7546.6712 | 7434.2092 | 1.513% | 0.26%
2017-04-13 | 18 | 7567 | 112.4657 | 1.486% | 19.331 | 0.2555% | 131.7966 | 1.742% | 1656 | 7547.669 | 7435.2034 | 1.513% | 0.26%
2017-05-26 | 22 | 7567 | 112.4657 | 1.486% | 19.331 | 0.2555% | 131.7966 | 1.742% | 1657 | 7547.669 | 7435.2034 | 1.513% | 0.26%
2017-05-25 | 13 | 7573 | 112.4876 | 1.485% | 19.3438 | 0.2554% | 131.8314 | 1.741% | 1658 | 7553.6562 | 7441.1686 | 1.512% | 0.26%
2017-05-25 | 17 | 7576 | 112.4986 | 1.485% | 19.3502 | 0.2554% | 131.8489 | 1.74% | 1659 | 7556.6498 | 7444.1511 | 1.511% | 0.2599%
2017-05-03 | 14 | 7581 | 112.517 | 1.484% | 19.3609 | 0.2554% | 131.8779 | 1.74% | 1660 | 7561.6391 | 7449.1221 | 1.51% | 0.2599%
2017-03-11 | 22 | 7582 | 112.5206 | 1.484% | 19.3631 | 0.2554% | 131.8837 | 1.739% | 1661 | 7562.6369 | 7450.1163 | 1.51% | 0.2599%
2017-03-04 | 3 | 7584 | 112.5279 | 1.484% | 19.3673 | 0.2554% | 131.8953 | 1.739% | 1662 | 7564.6327 | 7452.1047 | 1.51% | 0.2599%
2017-03-23 | 12 | 7594 | 112.5646 | 1.482% | 19.3887 | 0.2553% | 131.9533 | 1.738% | 1663 | 7574.6113 | 7462.0467 | 1.508% | 0.2598%
2017-03-06 | 11 | 7595 | 112.5682 | 1.482% | 19.3909 | 0.2553% | 131.9591 | 1.737% | 1664 | 7575.6091 | 7463.0409 | 1.508% | 0.2598%
2017-03-11 | 11 | 7601 | 112.5902 | 1.481% | 19.4037 | 0.2553% | 131.9939 | 1.737% | 1665 | 7581.5963 | 7469.0061 | 1.507% | 0.2598%
2017-03-14 | 5 | 7601 | 112.5902 | 1.481% | 19.4037 | 0.2553% | 131.9939 | 1.737% | 1666 | 7581.5963 | 7469.0061 | 1.507% | 0.2598%
2017-05-23 | 16 | 7601 | 112.5902 | 1.481% | 19.4037 | 0.2553% | 131.9939 | 1.737% | 1667 | 7581.5963 | 7469.0061 | 1.507% | 0.2598%
2017-03-05 | 22 | 7603 | 112.5975 | 1.481% | 19.408 | 0.2553% | 132.0055 | 1.736% | 1668 | 7583.592 | 7470.9945 | 1.507% | 0.2598%
2017-03-04 | 20 | 7604 | 112.6012 | 1.481% | 19.4101 | 0.2553% | 132.0113 | 1.736% | 1669 | 7584.5899 | 7471.9887 | 1.507% | 0.2598%
2017-05-23 | 21 | 7604 | 112.6012 | 1.481% | 19.4101 | 0.2553% | 132.0113 | 1.736% | 1670 | 7584.5899 | 7471.9887 | 1.507% | 0.2598%
2017-04-13 | 16 | 7605 | 112.6049 | 1.481% | 19.4123 | 0.2553% | 132.0171 | 1.736% | 1671 | 7585.5877 | 7472.9829 | 1.507% | 0.2598%
2017-04-26 | 15 | 7607 | 112.6122 | 1.48% | 19.4166 | 0.2552% | 132.0288 | 1.736% | 1672 | 7587.5834 | 7474.9712 | 1.507% | 0.2598%
2017-03-19 | 21 | 7609 | 112.6195 | 1.48% | 19.4208 | 0.2552% | 132.0404 | 1.735% | 1673 | 7589.5792 | 7476.9596 | 1.506% | 0.2597%
2017-05-23 | 18 | 7609 | 112.6195 | 1.48% | 19.4208 | 0.2552% | 132.0404 | 1.735% | 1674 | 7589.5792 | 7476.9596 | 1.506% | 0.2597%
2017-05-01 | 23 | 7613 | 112.6342 | 1.479% | 19.4294 | 0.2552% | 132.0636 | 1.735% | 1675 | 7593.5706 | 7480.9364 | 1.506% | 0.2597%
2017-05-25 | 18 | 7617 | 112.6488 | 1.479% | 19.438 | 0.2552% | 132.0868 | 1.734% | 1676 | 7597.562 | 7484.9132 | 1.505% | 0.2597%
2017-04-28 | 10 | 7620 | 112.6598 | 1.478% | 19.4444 | 0.2552% | 132.1042 | 1.734% | 1677 | 7600.5556 | 7487.8958 | 1.505% | 0.2597%
2017-03-04 | 23 | 7622 | 112.6672 | 1.478% | 19.4487 | 0.2552% | 132.1158 | 1.733% | 1678 | 7602.5513 | 7489.8842 | 1.504% | 0.2597%
2017-03-24 | 6 | 7622 | 112.6672 | 1.478% | 19.4487 | 0.2552% | 132.1158 | 1.733% | 1679 | 7602.5513 | 7489.8842 | 1.504% | 0.2597%
2017-04-13 | 17 | 7622 | 112.6672 | 1.478% | 19.4487 | 0.2552% | 132.1158 | 1.733% | 1680 | 7602.5513 | 7489.8842 | 1.504% | 0.2597%
2017-04-11 | 17 | 7626 | 112.6818 | 1.478% | 19.4572 | 0.2551% | 132.139 | 1.733% | 1681 | 7606.5428 | 7493.861 | 1.504% | 0.2596%
2017-04-11 | 19 | 7628 | 112.6891 | 1.477% | 19.4615 | 0.2551% | 132.1506 | 1.732% | 1682 | 7608.5385 | 7495.8494 | 1.503% | 0.2596%
2017-05-21 | 15 | 7629 | 112.6928 | 1.477% | 19.4636 | 0.2551% | 132.1564 | 1.732% | 1683 | 7609.5364 | 7496.8436 | 1.503% | 0.2596%
2017-05-05 | 15 | 7630 | 112.6965 | 1.477% | 19.4658 | 0.2551% | 132.1622 | 1.732% | 1684 | 7610.5342 | 7497.8378 | 1.503% | 0.2596%
2017-03-11 | 20 | 7631 | 112.7001 | 1.477% | 19.4679 | 0.2551% | 132.168 | 1.732% | 1685 | 7611.5321 | 7498.832 | 1.503% | 0.2596%
2017-04-15 | 17 | 7633 | 112.7075 | 1.477% | 19.4722 | 0.2551% | 132.1796 | 1.732% | 1686 | 7613.5278 | 7500.8204 | 1.503% | 0.2596%
2017-05-23 | 17 | 7635 | 112.7148 | 1.476% | 19.4765 | 0.2551% | 132.1912 | 1.731% | 1687 | 7615.5235 | 7502.8088 | 1.502% | 0.2596%
2017-05-25 | 14 | 7635 | 112.7148 | 1.476% | 19.4765 | 0.2551% | 132.1912 | 1.731% | 1688 | 7615.5235 | 7502.8088 | 1.502% | 0.2596%
2017-03-09 | 9 | 7639 | 112.7294 | 1.476% | 19.485 | 0.2551% | 132.2145 | 1.731% | 1689 | 7619.515 | 7506.7855 | 1.502% | 0.2596%
2017-03-12 | 8 | 7639 | 112.7294 | 1.476% | 19.485 | 0.2551% | 132.2145 | 1.731% | 1690 | 7619.515 | 7506.7855 | 1.502% | 0.2596%
2017-05-25 | 16 | 7639 | 112.7294 | 1.476% | 19.485 | 0.2551% | 132.2145 | 1.731% | 1691 | 7619.515 | 7506.7855 | 1.502% | 0.2596%
2017-03-14 | 15 | 7645 | 112.7514 | 1.475% | 19.4979 | 0.255% | 132.2493 | 1.73% | 1692 | 7625.5021 | 7512.7507 | 1.501% | 0.2595%
2017-04-12 | 20 | 7647 | 112.7587 | 1.475% | 19.5021 | 0.255% | 132.2609 | 1.73% | 1693 | 7627.4979 | 7514.7391 | 1.501% | 0.2595%
2017-05-25 | 15 | 7652 | 112.7771 | 1.474% | 19.5128 | 0.255% | 132.2899 | 1.729% | 1694 | 7632.4872 | 7519.7101 | 1.5% | 0.2595%
2017-05-04 | 22 | 7655 | 112.788 | 1.473% | 19.5193 | 0.255% | 132.3073 | 1.728% | 1695 | 7635.4807 | 7522.6927 | 1.499% | 0.2595%
2017-03-23 | 21 | 7656 | 112.7917 | 1.473% | 19.5214 | 0.255% | 132.3131 | 1.728% | 1696 | 7636.4786 | 7523.6869 | 1.499% | 0.2595%
2017-03-05 | 20 | 7657 | 112.7954 | 1.473% | 19.5235 | 0.255% | 132.3189 | 1.728% | 1697 | 7637.4765 | 7524.6811 | 1.499% | 0.2595%
2017-03-16 | 16 | 7659 | 112.8027 | 1.473% | 19.5278 | 0.255% | 132.3305 | 1.728% | 1698 | 7639.4722 | 7526.6695 | 1.499% | 0.2594%
2017-03-11 | 21 | 7665 | 112.8247 | 1.472% | 19.5407 | 0.2549% | 132.3653 | 1.727% | 1699 | 7645.4593 | 7532.6347 | 1.498% | 0.2594%
2017-04-12 | 21 | 7665 | 112.8247 | 1.472% | 19.5407 | 0.2549% | 132.3653 | 1.727% | 1700 | 7645.4593 | 7532.6347 | 1.498% | 0.2594%
2017-05-01 | 10 | 7665 | 112.8247 | 1.472% | 19.5407 | 0.2549% | 132.3653 | 1.727% | 1701 | 7645.4593 | 7532.6347 | 1.498% | 0.2594%
2017-03-12 | 19 | 7669 | 112.8393 | 1.471% | 19.5492 | 0.2549% | 132.3886 | 1.726% | 1702 | 7649.4508 | 7536.6114 | 1.497% | 0.2594%
2017-05-05 | 17 | 7673 | 112.854 | 1.471% | 19.5578 | 0.2549% | 132.4118 | 1.726% | 1703 | 7653.4422 | 7540.5882 | 1.497% | 0.2594%
2017-05-17 | 10 | 7678 | 112.8723 | 1.47% | 19.5685 | 0.2549% | 132.4408 | 1.725% | 1704 | 7658.4315 | 7545.5592 | 1.496% | 0.2593%
2017-05-18 | 10 | 7683 | 112.8906 | 1.469% | 19.5792 | 0.2548% | 132.4698 | 1.724% | 1705 | 7663.4208 | 7550.5302 | 1.495% | 0.2593%
2017-03-14 | 18 | 7688 | 112.9089 | 1.469% | 19.5899 | 0.2548% | 132.4988 | 1.723% | 1706 | 7668.4101 | 7555.5012 | 1.494% | 0.2593%
2017-04-12 | 16 | 7689 | 112.9126 | 1.468% | 19.592 | 0.2548% | 132.5046 | 1.723% | 1707 | 7669.408 | 7556.4954 | 1.494% | 0.2593%
2017-04-15 | 18 | 7695 | 112.9346 | 1.468% | 19.6049 | 0.2548% | 132.5394 | 1.722% | 1708 | 7675.3951 | 7562.4606 | 1.493% | 0.2592%
2017-03-20 | 12 | 7697 | 112.9419 | 1.467% | 19.6091 | 0.2548% | 132.5511 | 1.722% | 1709 | 7677.3909 | 7564.4489 | 1.493% | 0.2592%
2017-03-05 | 4 | 7698 | 112.9456 | 1.467% | 19.6113 | 0.2548% | 132.5569 | 1.722% | 1710 | 7678.3887 | 7565.4431 | 1.493% | 0.2592%
2017-05-24 | 13 | 7699 | 112.9492 | 1.467% | 19.6134 | 0.2548% | 132.5627 | 1.722% | 1711 | 7679.3866 | 7566.4373 | 1.493% | 0.2592%
2017-03-03 | 6 | 7700 | 112.9529 | 1.467% | 19.6156 | 0.2547% | 132.5685 | 1.722% | 1712 | 7680.3844 | 7567.4315 | 1.493% | 0.2592%
2017-03-13 | 24 | 7701 | 112.9566 | 1.467% | 19.6177 | 0.2547% | 132.5743 | 1.722% | 1713 | 7681.3823 | 7568.4257 | 1.492% | 0.2592%
2017-04-22 | 21 | 7703 | 112.9639 | 1.466% | 19.622 | 0.2547% | 132.5859 | 1.721% | 1714 | 7683.378 | 7570.4141 | 1.492% | 0.2592%
2017-05-05 | 16 | 7708 | 112.9822 | 1.466% | 19.6327 | 0.2547% | 132.6149 | 1.72% | 1715 | 7688.3673 | 7575.3851 | 1.491% | 0.2592%
2017-05-21 | 22 | 7720 | 113.0262 | 1.464% | 19.6584 | 0.2546% | 132.6845 | 1.719% | 1716 | 7700.3416 | 7587.3155 | 1.49% | 0.2591%
2017-04-04 | 20 | 7723 | 113.0372 | 1.464% | 19.6648 | 0.2546% | 132.7019 | 1.718% | 1717 | 7703.3352 | 7590.2981 | 1.489% | 0.2591%
2017-03-04 | 21 | 7724 | 113.0408 | 1.464% | 19.6669 | 0.2546% | 132.7077 | 1.718% | 1718 | 7704.3331 | 7591.2923 | 1.489% | 0.2591%
2017-04-12 | 18 | 7724 | 113.0408 | 1.464% | 19.6669 | 0.2546% | 132.7077 | 1.718% | 1719 | 7704.3331 | 7591.2923 | 1.489% | 0.2591%
2017-05-28 | 23 | 7735 | 113.0811 | 1.462% | 19.6905 | 0.2546% | 132.7716 | 1.717% | 1720 | 7715.3095 | 7602.2284 | 1.487% | 0.259%
2017-03-23 | 22 | 7737 | 113.0885 | 1.462% | 19.6947 | 0.2546% | 132.7832 | 1.716% | 1721 | 7717.3053 | 7604.2168 | 1.487% | 0.259%
2017-04-12 | 17 | 7739 | 113.0958 | 1.461% | 19.699 | 0.2545% | 132.7948 | 1.716% | 1722 | 7719.301 | 7606.2052 | 1.487% | 0.259%
2017-05-19 | 10 | 7740 | 113.0994 | 1.461% | 19.7012 | 0.2545% | 132.8006 | 1.716% | 1723 | 7720.2988 | 7607.1994 | 1.487% | 0.259%
2017-03-05 | 21 | 7741 | 113.1031 | 1.461% | 19.7033 | 0.2545% | 132.8064 | 1.716% | 1724 | 7721.2967 | 7608.1936 | 1.487% | 0.259%
2017-04-26 | 22 | 7743 | 113.1104 | 1.461% | 19.7076 | 0.2545% | 132.818 | 1.715% | 1725 | 7723.2924 | 7610.182 | 1.486% | 0.259%
2017-03-11 | 7 | 7744 | 113.1141 | 1.461% | 19.7097 | 0.2545% | 132.8238 | 1.715% | 1726 | 7724.2903 | 7611.1762 | 1.486% | 0.259%
2017-05-04 | 14 | 7744 | 113.1141 | 1.461% | 19.7097 | 0.2545% | 132.8238 | 1.715% | 1727 | 7724.2903 | 7611.1762 | 1.486% | 0.259%
2017-05-04 | 20 | 7744 | 113.1141 | 1.461% | 19.7097 | 0.2545% | 132.8238 | 1.715% | 1728 | 7724.2903 | 7611.1762 | 1.486% | 0.259%
2017-03-06 | 5 | 7745 | 113.1178 | 1.461% | 19.7119 | 0.2545% | 132.8296 | 1.715% | 1729 | 7725.2881 | 7612.1704 | 1.486% | 0.259%
2017-03-04 | 22 | 7746 | 113.1214 | 1.46% | 19.714 | 0.2545% | 132.8354 | 1.715% | 1730 | 7726.286 | 7613.1646 | 1.486% | 0.2589%
2017-04-12 | 19 | 7746 | 113.1214 | 1.46% | 19.714 | 0.2545% | 132.8354 | 1.715% | 1731 | 7726.286 | 7613.1646 | 1.486% | 0.2589%
2017-05-02 | 14 | 7747 | 113.1251 | 1.46% | 19.7161 | 0.2545% | 132.8412 | 1.715% | 1732 | 7727.2839 | 7614.1588 | 1.486% | 0.2589%
2017-05-24 | 20 | 7753 | 113.1471 | 1.459% | 19.729 | 0.2545% | 132.876 | 1.714% | 1733 | 7733.271 | 7620.124 | 1.485% | 0.2589%
2017-05-28 | 11 | 7754 | 113.1507 | 1.459% | 19.7311 | 0.2545% | 132.8818 | 1.714% | 1734 | 7734.2689 | 7621.1182 | 1.485% | 0.2589%
2017-05-24 | 21 | 7756 | 113.1581 | 1.459% | 19.7354 | 0.2545% | 132.8934 | 1.713% | 1735 | 7736.2646 | 7623.1066 | 1.484% | 0.2589%
2017-05-15 | 12 | 7758 | 113.1654 | 1.459% | 19.7397 | 0.2544% | 132.9051 | 1.713% | 1736 | 7738.2603 | 7625.0949 | 1.484% | 0.2589%
2017-04-04 | 17 | 7764 | 113.1874 | 1.458% | 19.7525 | 0.2544% | 132.9399 | 1.712% | 1737 | 7744.2475 | 7631.0601 | 1.483% | 0.2588%
2017-03-16 | 19 | 7775 | 113.2277 | 1.456% | 19.776 | 0.2544% | 133.0037 | 1.711% | 1738 | 7755.224 | 7641.9963 | 1.482% | 0.2588%
2017-04-04 | 21 | 7776 | 113.2313 | 1.456% | 19.7782 | 0.2543% | 133.0095 | 1.711% | 1739 | 7756.2218 | 7642.9905 | 1.482% | 0.2588%
2017-05-26 | 14 | 7776 | 113.2313 | 1.456% | 19.7782 | 0.2543% | 133.0095 | 1.711% | 1740 | 7756.2218 | 7642.9905 | 1.482% | 0.2588%
2017-04-20 | 14 | 7780 | 113.246 | 1.456% | 19.7867 | 0.2543% | 133.0327 | 1.71% | 1741 | 7760.2133 | 7646.9673 | 1.481% | 0.2588%
2017-04-11 | 18 | 7783 | 113.257 | 1.455% | 19.7932 | 0.2543% | 133.0501 | 1.709% | 1742 | 7763.2068 | 7649.9499 | 1.48% | 0.2587%
2017-05-27 | 12 | 7785 | 113.2643 | 1.455% | 19.7974 | 0.2543% | 133.0617 | 1.709% | 1743 | 7765.2026 | 7651.9383 | 1.48% | 0.2587%
2017-05-10 | 14 | 7786 | 113.268 | 1.455% | 19.7996 | 0.2543% | 133.0675 | 1.709% | 1744 | 7766.2004 | 7652.9325 | 1.48% | 0.2587%
2017-03-03 | 20 | 7791 | 113.2863 | 1.454% | 19.8103 | 0.2543% | 133.0966 | 1.708% | 1745 | 7771.1897 | 7657.9034 | 1.479% | 0.2587%
2017-04-17 | 14 | 7800 | 113.3193 | 1.453% | 19.8295 | 0.2542% | 133.1488 | 1.707% | 1746 | 7780.1705 | 7666.8512 | 1.478% | 0.2586%
2017-05-31 | 23 | 7807 | 113.3449 | 1.452% | 19.8445 | 0.2542% | 133.1894 | 1.706% | 1747 | 7787.1555 | 7673.8106 | 1.477% | 0.2586%
2017-03-04 | 4 | 7813 | 113.3669 | 1.451% | 19.8574 | 0.2542% | 133.2242 | 1.705% | 1748 | 7793.1426 | 7679.7758 | 1.476% | 0.2586%
2017-05-02 | 21 | 7818 | 113.3852 | 1.45% | 19.8681 | 0.2541% | 133.2532 | 1.704% | 1749 | 7798.1319 | 7684.7468 | 1.475% | 0.2585%
2017-05-26 | 21 | 7821 | 113.3962 | 1.45% | 19.8745 | 0.2541% | 133.2707 | 1.704% | 1750 | 7801.1255 | 7687.7293 | 1.475% | 0.2585%
2017-04-04 | 19 | 7825 | 113.4108 | 1.449% | 19.883 | 0.2541% | 133.2939 | 1.703% | 1751 | 7805.117 | 7691.7061 | 1.474% | 0.2585%
2017-03-03 | 22 | 7826 | 113.4145 | 1.449% | 19.8852 | 0.2541% | 133.2997 | 1.703% | 1752 | 7806.1148 | 7692.7003 | 1.474% | 0.2585%
2017-05-04 | 19 | 7826 | 113.4145 | 1.449% | 19.8852 | 0.2541% | 133.2997 | 1.703% | 1753 | 7806.1148 | 7692.7003 | 1.474% | 0.2585%
2017-05-27 | 23 | 7827 | 113.4182 | 1.449% | 19.8873 | 0.2541% | 133.3055 | 1.703% | 1754 | 7807.1127 | 7693.6945 | 1.474% | 0.2585%
2017-05-22 | 11 | 7831 | 113.4328 | 1.449% | 19.8959 | 0.2541% | 133.3287 | 1.703% | 1755 | 7811.1041 | 7697.6713 | 1.474% | 0.2585%
2017-03-20 | 5 | 7834 | 113.4438 | 1.448% | 19.9023 | 0.2541% | 133.3461 | 1.702% | 1756 | 7814.0977 | 7700.6539 | 1.473% | 0.2584%
2017-04-22 | 20 | 7837 | 113.4548 | 1.448% | 19.9087 | 0.254% | 133.3635 | 1.702% | 1757 | 7817.0913 | 7703.6365 | 1.473% | 0.2584%
2017-04-27 | 13 | 7841 | 113.4695 | 1.447% | 19.9173 | 0.254% | 133.3867 | 1.701% | 1758 | 7821.0827 | 7707.6133 | 1.472% | 0.2584%
2017-03-03 | 10 | 7854 | 113.5171 | 1.445% | 19.9451 | 0.2539% | 133.4622 | 1.699% | 1759 | 7834.0549 | 7720.5378 | 1.47% | 0.2583%
2017-04-04 | 18 | 7856 | 113.5244 | 1.445% | 19.9494 | 0.2539% | 133.4738 | 1.699% | 1760 | 7836.0506 | 7722.5262 | 1.47% | 0.2583%
2017-04-26 | 16 | 7863 | 113.55 | 1.444% | 19.9643 | 0.2539% | 133.5144 | 1.698% | 1761 | 7843.0357 | 7729.4856 | 1.469% | 0.2583%
2017-05-11 | 12 | 7865 | 113.5574 | 1.444% | 19.9686 | 0.2539% | 133.526 | 1.698% | 1762 | 7845.0314 | 7731.474 | 1.469% | 0.2583%
2017-05-31 | 10 | 7871 | 113.5794 | 1.443% | 19.9815 | 0.2539% | 133.5608 | 1.697% | 1763 | 7851.0185 | 7737.4392 | 1.468% | 0.2582%
2017-03-03 | 21 | 7877 | 113.6013 | 1.442% | 19.9943 | 0.2538% | 133.5956 | 1.696% | 1764 | 7857.0057 | 7743.4044 | 1.467% | 0.2582%
2017-03-11 | 10 | 7878 | 113.605 | 1.442% | 19.9964 | 0.2538% | 133.6014 | 1.696% | 1765 | 7858.0036 | 7744.3986 | 1.467% | 0.2582%
2017-05-03 | 15 | 7883 | 113.6233 | 1.441% | 20.0071 | 0.2538% | 133.6305 | 1.695% | 1766 | 7862.9929 | 7749.3695 | 1.466% | 0.2582%
2017-03-12 | 16 | 7885 | 113.6306 | 1.441% | 20.0114 | 0.2538% | 133.6421 | 1.695% | 1767 | 7864.9886 | 7751.3579 | 1.466% | 0.2582%
2017-05-04 | 18 | 7898 | 113.6783 | 1.439% | 20.0392 | 0.2537% | 133.7175 | 1.693% | 1768 | 7877.9608 | 7764.2825 | 1.464% | 0.2581%
2017-04-27 | 22 | 7899 | 113.6819 | 1.439% | 20.0414 | 0.2537% | 133.7233 | 1.693% | 1769 | 7878.9586 | 7765.2767 | 1.464% | 0.2581%
2017-03-05 | 5 | 7907 | 113.7112 | 1.438% | 20.0585 | 0.2537% | 133.7697 | 1.692% | 1770 | 7886.9415 | 7773.2303 | 1.463% | 0.258%
2017-05-01 | 11 | 7913 | 113.7332 | 1.437% | 20.0713 | 0.2537% | 133.8046 | 1.691% | 1771 | 7892.9287 | 7779.1954 | 1.462% | 0.258%
2017-05-04 | 15 | 7916 | 113.7442 | 1.437% | 20.0778 | 0.2536% | 133.822 | 1.691% | 1772 | 7895.9222 | 7782.178 | 1.462% | 0.258%
2017-05-04 | 21 | 7918 | 113.7515 | 1.437% | 20.082 | 0.2536% | 133.8336 | 1.69% | 1773 | 7897.918 | 7784.1664 | 1.461% | 0.258%
2017-04-29 | 23 | 7922 | 113.7662 | 1.436% | 20.0906 | 0.2536% | 133.8568 | 1.69% | 1774 | 7901.9094 | 7788.1432 | 1.461% | 0.258%
2017-05-02 | 20 | 7925 | 113.7772 | 1.436% | 20.097 | 0.2536% | 133.8742 | 1.689% | 1775 | 7904.903 | 7791.1258 | 1.46% | 0.2579%
2017-05-24 | 14 | 7934 | 113.8102 | 1.434% | 20.1163 | 0.2535% | 133.9264 | 1.688% | 1776 | 7913.8837 | 7800.0736 | 1.459% | 0.2579%
2017-05-30 | 11 | 7935 | 113.8138 | 1.434% | 20.1184 | 0.2535% | 133.9322 | 1.688% | 1777 | 7914.8816 | 7801.0678 | 1.459% | 0.2579%
2017-03-16 | 15 | 7937 | 113.8211 | 1.434% | 20.1227 | 0.2535% | 133.9438 | 1.688% | 1778 | 7916.8773 | 7803.0562 | 1.459% | 0.2579%
2017-05-21 | 20 | 7947 | 113.8578 | 1.433% | 20.1441 | 0.2535% | 134.0019 | 1.686% | 1779 | 7926.8559 | 7812.9981 | 1.457% | 0.2578%
2017-04-30 | 12 | 7948 | 113.8614 | 1.433% | 20.1462 | 0.2535% | 134.0077 | 1.686% | 1780 | 7927.8538 | 7813.9923 | 1.457% | 0.2578%
2017-05-03 | 21 | 7955 | 113.8871 | 1.432% | 20.1612 | 0.2534% | 134.0483 | 1.685% | 1781 | 7934.8388 | 7820.9517 | 1.456% | 0.2578%
2017-03-14 | 14 | 7959 | 113.9017 | 1.431% | 20.1698 | 0.2534% | 134.0715 | 1.685% | 1782 | 7938.8302 | 7824.9285 | 1.456% | 0.2578%
2017-05-19 | 23 | 7961 | 113.9091 | 1.431% | 20.1741 | 0.2534% | 134.0831 | 1.684% | 1783 | 7940.8259 | 7826.9169 | 1.455% | 0.2578%
2017-05-24 | 19 | 7961 | 113.9091 | 1.431% | 20.1741 | 0.2534% | 134.0831 | 1.684% | 1784 | 7940.8259 | 7826.9169 | 1.455% | 0.2578%
2017-03-14 | 19 | 7966 | 113.9274 | 1.43% | 20.1847 | 0.2534% | 134.1121 | 1.684% | 1785 | 7945.8153 | 7831.8879 | 1.455% | 0.2577%
2017-05-16 | 23 | 7967 | 113.931 | 1.43% | 20.1869 | 0.2534% | 134.1179 | 1.683% | 1786 | 7946.8131 | 7832.8821 | 1.455% | 0.2577%
2017-05-21 | 21 | 7970 | 113.942 | 1.43% | 20.1933 | 0.2534% | 134.1353 | 1.683% | 1787 | 7949.8067 | 7835.8647 | 1.454% | 0.2577%
2017-03-04 | 11 | 7973 | 113.953 | 1.429% | 20.1997 | 0.2534% | 134.1528 | 1.683% | 1788 | 7952.8003 | 7838.8472 | 1.454% | 0.2577%
2017-03-09 | 7 | 7976 | 113.964 | 1.429% | 20.2061 | 0.2533% | 134.1702 | 1.682% | 1789 | 7955.7939 | 7841.8298 | 1.453% | 0.2577%
2017-04-17 | 15 | 7976 | 113.964 | 1.429% | 20.2061 | 0.2533% | 134.1702 | 1.682% | 1790 | 7955.7939 | 7841.8298 | 1.453% | 0.2577%
2017-05-29 | 23 | 7978 | 113.9713 | 1.429% | 20.2104 | 0.2533% | 134.1818 | 1.682% | 1791 | 7957.7896 | 7843.8182 | 1.453% | 0.2577%
2017-04-21 | 12 | 7980 | 113.9787 | 1.428% | 20.2147 | 0.2533% | 134.1934 | 1.682% | 1792 | 7959.7853 | 7845.8066 | 1.453% | 0.2576%
2017-05-02 | 15 | 7987 | 114.0043 | 1.427% | 20.2297 | 0.2533% | 134.234 | 1.681% | 1793 | 7966.7703 | 7852.766 | 1.452% | 0.2576%
2017-04-22 | 13 | 7994 | 114.03 | 1.426% | 20.2447 | 0.2532% | 134.2746 | 1.68% | 1794 | 7973.7553 | 7859.7254 | 1.451% | 0.2576%
2017-05-21 | 16 | 7997 | 114.041 | 1.426% | 20.2511 | 0.2532% | 134.292 | 1.679% | 1795 | 7976.7489 | 7862.708 | 1.45% | 0.2576%
2017-04-20 | 22 | 8000 | 114.0519 | 1.426% | 20.2575 | 0.2532% | 134.3094 | 1.679% | 1796 | 7979.7425 | 7865.6906 | 1.45% | 0.2575%
2017-05-20 | 23 | 8019 | 114.1216 | 1.423% | 20.2982 | 0.2531% | 134.4197 | 1.676% | 1797 | 7998.7018 | 7884.5803 | 1.447% | 0.2574%
2017-04-17 | 21 | 8022 | 114.1325 | 1.423% | 20.3046 | 0.2531% | 134.4371 | 1.676% | 1798 | 8001.6954 | 7887.5629 | 1.447% | 0.2574%
2017-04-21 | 22 | 8030 | 114.1618 | 1.422% | 20.3217 | 0.2531% | 134.4835 | 1.675% | 1799 | 8009.6783 | 7895.5165 | 1.446% | 0.2574%
2017-05-04 | 16 | 8032 | 114.1692 | 1.421% | 20.326 | 0.2531% | 134.4952 | 1.674% | 1800 | 8011.674 | 7897.5048 | 1.446% | 0.2574%
2017-05-24 | 16 | 8039 | 114.1948 | 1.421% | 20.341 | 0.253% | 134.5358 | 1.674% | 1801 | 8018.659 | 7904.4642 | 1.445% | 0.2573%
2017-05-04 | 17 | 8042 | 114.2058 | 1.42% | 20.3474 | 0.253% | 134.5532 | 1.673% | 1802 | 8021.6526 | 7907.4468 | 1.444% | 0.2573%
2017-05-24 | 15 | 8043 | 114.2095 | 1.42% | 20.3495 | 0.253% | 134.559 | 1.673% | 1803 | 8022.6505 | 7908.441 | 1.444% | 0.2573%
2017-03-11 | 9 | 8049 | 114.2315 | 1.419% | 20.3624 | 0.253% | 134.5938 | 1.672% | 1804 | 8028.6376 | 7914.4062 | 1.443% | 0.2573%
2017-05-03 | 20 | 8058 | 114.2644 | 1.418% | 20.3816 | 0.2529% | 134.646 | 1.671% | 1805 | 8037.6184 | 7923.354 | 1.442% | 0.2572%
2017-04-28 | 11 | 8059 | 114.2681 | 1.418% | 20.3838 | 0.2529% | 134.6518 | 1.671% | 1806 | 8038.6162 | 7924.3482 | 1.442% | 0.2572%
2017-03-06 | 10 | 8060 | 114.2718 | 1.418% | 20.3859 | 0.2529% | 134.6576 | 1.671% | 1807 | 8039.6141 | 7925.3424 | 1.442% | 0.2572%
2017-04-20 | 15 | 8065 | 114.2901 | 1.417% | 20.3966 | 0.2529% | 134.6867 | 1.67% | 1808 | 8044.6034 | 7930.3133 | 1.441% | 0.2572%
2017-05-15 | 13 | 8065 | 114.2901 | 1.417% | 20.3966 | 0.2529% | 134.6867 | 1.67% | 1809 | 8044.6034 | 7930.3133 | 1.441% | 0.2572%
2017-04-27 | 20 | 8074 | 114.323 | 1.416% | 20.4158 | 0.2529% | 134.7389 | 1.669% | 1810 | 8053.5842 | 7939.2611 | 1.44% | 0.2572%
2017-03-04 | 5 | 8083 | 114.356 | 1.415% | 20.4351 | 0.2528% | 134.7911 | 1.668% | 1811 | 8062.5649 | 7948.2089 | 1.439% | 0.2571%
2017-05-24 | 17 | 8088 | 114.3743 | 1.414% | 20.4458 | 0.2528% | 134.8201 | 1.667% | 1812 | 8067.5542 | 7953.1799 | 1.438% | 0.2571%
2017-05-24 | 18 | 8088 | 114.3743 | 1.414% | 20.4458 | 0.2528% | 134.8201 | 1.667% | 1813 | 8067.5542 | 7953.1799 | 1.438% | 0.2571%
2017-03-17 | 13 | 8098 | 114.411 | 1.413% | 20.4672 | 0.2527% | 134.8782 | 1.666% | 1814 | 8077.5328 | 7963.1218 | 1.437% | 0.257%
2017-04-26 | 20 | 8104 | 114.4329 | 1.412% | 20.48 | 0.2527% | 134.913 | 1.665% | 1815 | 8083.52 | 7969.087 | 1.436% | 0.257%
2017-05-18 | 11 | 8116 | 114.4769 | 1.411% | 20.5057 | 0.2527% | 134.9826 | 1.663% | 1816 | 8095.4943 | 7981.0174 | 1.434% | 0.2569%
2017-05-17 | 23 | 8118 | 114.4842 | 1.41% | 20.51 | 0.2526% | 134.9942 | 1.663% | 1817 | 8097.49 | 7983.0058 | 1.434% | 0.2569%
2017-05-26 | 15 | 8119 | 114.4879 | 1.41% | 20.5121 | 0.2526% | 135 | 1.663% | 1818 | 8098.4879 | 7984 | 1.434% | 0.2569%
2017-04-17 | 20 | 8120 | 114.4916 | 1.41% | 20.5143 | 0.2526% | 135.0058 | 1.663% | 1819 | 8099.4857 | 7984.9942 | 1.434% | 0.2569%
2017-05-10 | 15 | 8123 | 114.5026 | 1.41% | 20.5207 | 0.2526% | 135.0233 | 1.662% | 1820 | 8102.4793 | 7987.9767 | 1.433% | 0.2569%
2017-05-29 | 11 | 8123 | 114.5026 | 1.41% | 20.5207 | 0.2526% | 135.0233 | 1.662% | 1821 | 8102.4793 | 7987.9767 | 1.433% | 0.2569%
2017-03-05 | 6 | 8135 | 114.5465 | 1.408% | 20.5464 | 0.2526% | 135.0929 | 1.661% | 1822 | 8114.4536 | 7999.9071 | 1.432% | 0.2568%
2017-04-27 | 14 | 8138 | 114.5575 | 1.408% | 20.5528 | 0.2526% | 135.1103 | 1.66% | 1823 | 8117.4472 | 8002.8897 | 1.431% | 0.2568%
2017-04-26 | 17 | 8139 | 114.5612 | 1.408% | 20.5549 | 0.2525% | 135.1161 | 1.66% | 1824 | 8118.4451 | 8003.8839 | 1.431% | 0.2568%
2017-05-21 | 19 | 8141 | 114.5685 | 1.407% | 20.5592 | 0.2525% | 135.1277 | 1.66% | 1825 | 8120.4408 | 8005.8723 | 1.431% | 0.2568%
2017-03-11 | 8 | 8148 | 114.5941 | 1.406% | 20.5742 | 0.2525% | 135.1683 | 1.659% | 1826 | 8127.4258 | 8012.8317 | 1.43% | 0.2568%
2017-04-30 | 22 | 8153 | 114.6125 | 1.406% | 20.5849 | 0.2525% | 135.1974 | 1.658% | 1827 | 8132.4151 | 8017.8026 | 1.429% | 0.2567%
2017-05-30 | 23 | 8154 | 114.6161 | 1.406% | 20.587 | 0.2525% | 135.2032 | 1.658% | 1828 | 8133.413 | 8018.7968 | 1.429% | 0.2567%
2017-04-26 | 21 | 8157 | 114.6271 | 1.405% | 20.5935 | 0.2525% | 135.2206 | 1.658% | 1829 | 8136.4065 | 8021.7794 | 1.429% | 0.2567%
2017-05-20 | 11 | 8163 | 114.6491 | 1.404% | 20.6063 | 0.2524% | 135.2554 | 1.657% | 1830 | 8142.3937 | 8027.7446 | 1.428% | 0.2567%
2017-04-20 | 16 | 8171 | 114.6784 | 1.403% | 20.6234 | 0.2524% | 135.3018 | 1.656% | 1831 | 8150.3766 | 8035.6982 | 1.427% | 0.2566%
2017-05-18 | 23 | 8173 | 114.6857 | 1.403% | 20.6277 | 0.2524% | 135.3134 | 1.656% | 1832 | 8152.3723 | 8037.6866 | 1.427% | 0.2566%
2017-04-27 | 19 | 8176 | 114.6967 | 1.403% | 20.6341 | 0.2524% | 135.3308 | 1.655% | 1833 | 8155.3659 | 8040.6692 | 1.426% | 0.2566%
2017-03-09 | 8 | 8180 | 114.7114 | 1.402% | 20.6427 | 0.2524% | 135.354 | 1.655% | 1834 | 8159.3573 | 8044.646 | 1.426% | 0.2566%
2017-05-02 | 16 | 8182 | 114.7187 | 1.402% | 20.647 | 0.2523% | 135.3656 | 1.654% | 1835 | 8161.353 | 8046.6344 | 1.426% | 0.2566%
2017-05-26 | 20 | 8184 | 114.726 | 1.402% | 20.6512 | 0.2523% | 135.3773 | 1.654% | 1836 | 8163.3488 | 8048.6227 | 1.425% | 0.2566%
2017-05-16 | 12 | 8186 | 114.7333 | 1.402% | 20.6555 | 0.2523% | 135.3889 | 1.654% | 1837 | 8165.3445 | 8050.6111 | 1.425% | 0.2566%
2017-04-29 | 11 | 8188 | 114.7407 | 1.401% | 20.6598 | 0.2523% | 135.4005 | 1.654% | 1838 | 8167.3402 | 8052.5995 | 1.425% | 0.2566%
2017-03-05 | 10 | 8194 | 114.7627 | 1.401% | 20.6726 | 0.2523% | 135.4353 | 1.653% | 1839 | 8173.3274 | 8058.5647 | 1.424% | 0.2565%
2017-03-20 | 6 | 8194 | 114.7627 | 1.401% | 20.6726 | 0.2523% | 135.4353 | 1.653% | 1840 | 8173.3274 | 8058.5647 | 1.424% | 0.2565%
2017-05-22 | 22 | 8194 | 114.7627 | 1.401% | 20.6726 | 0.2523% | 135.4353 | 1.653% | 1841 | 8173.3274 | 8058.5647 | 1.424% | 0.2565%
2017-05-21 | 17 | 8196 | 114.77 | 1.4% | 20.6769 | 0.2523% | 135.4469 | 1.653% | 1842 | 8175.3231 | 8060.5531 | 1.424% | 0.2565%
2017-05-03 | 16 | 8200 | 114.7846 | 1.4% | 20.6855 | 0.2523% | 135.4701 | 1.652% | 1843 | 8179.3145 | 8064.5299 | 1.423% | 0.2565%
2017-05-22 | 12 | 8201 | 114.7883 | 1.4% | 20.6876 | 0.2523% | 135.4759 | 1.652% | 1844 | 8180.3124 | 8065.5241 | 1.423% | 0.2565%
2017-05-17 | 11 | 8202 | 114.792 | 1.4% | 20.6897 | 0.2523% | 135.4817 | 1.652% | 1845 | 8181.3103 | 8066.5183 | 1.423% | 0.2565%
2017-04-28 | 23 | 8224 | 114.8726 | 1.397% | 20.7368 | 0.2522% | 135.6094 | 1.649% | 1846 | 8203.2632 | 8088.3906 | 1.42% | 0.2564%
2017-05-01 | 12 | 8230 | 114.8945 | 1.396% | 20.7497 | 0.2521% | 135.6442 | 1.648% | 1847 | 8209.2503 | 8094.3558 | 1.419% | 0.2563%
2017-04-27 | 21 | 8231 | 114.8982 | 1.396% | 20.7518 | 0.2521% | 135.65 | 1.648% | 1848 | 8210.2482 | 8095.35 | 1.419% | 0.2563%
2017-04-17 | 16 | 8233 | 114.9055 | 1.396% | 20.7561 | 0.2521% | 135.6616 | 1.648% | 1849 | 8212.2439 | 8097.3384 | 1.419% | 0.2563%
2017-05-11 | 13 | 8234 | 114.9092 | 1.396% | 20.7582 | 0.2521% | 135.6674 | 1.648% | 1850 | 8213.2418 | 8098.3326 | 1.419% | 0.2563% | 8240.1444
2017-05-31 | 11 | 8244 | 114.9739 | 1.395% | 20.7787 | 0.252% | 135.7526 | 1.647% | 1851 | 8223.2213 | 8108.2474 | 1.418% | 0.2563%
2017-05-10 | 22 | 8256 | 115.1144 | 1.394% | 20.801 | 0.252% | 135.9155 | 1.646% | 1852 | 8235.199 | 8120.0845 | 1.418% | 0.2562%
2017-04-26 | 19 | 8257 | 115.1261 | 1.394% | 20.8029 | 0.2519% | 135.9291 | 1.646% | 1853 | 8236.1971 | 8121.0709 | 1.418% | 0.2562%
2017-05-27 | 13 | 8257 | 115.1261 | 1.394% | 20.8029 | 0.2519% | 135.9291 | 1.646% | 1854 | 8236.1971 | 8121.0709 | 1.418% | 0.2562%
2017-04-26 | 18 | 8273 | 115.3135 | 1.394% | 20.8328 | 0.2518% | 136.1462 | 1.646% | 1855 | 8252.1672 | 8136.8538 | 1.417% | 0.256%
2017-04-17 | 19 | 8274 | 115.3252 | 1.394% | 20.8346 | 0.2518% | 136.1598 | 1.646% | 1856 | 8253.1654 | 8137.8402 | 1.417% | 0.256%
2017-03-14 | 6 | 8280 | 115.3955 | 1.394% | 20.8458 | 0.2518% | 136.2413 | 1.645% | 1857 | 8259.1542 | 8143.7587 | 1.417% | 0.256%
2017-05-19 | 11 | 8288 | 115.4891 | 1.393% | 20.8607 | 0.2517% | 136.3499 | 1.645% | 1858 | 8267.1393 | 8151.6501 | 1.417% | 0.2559%
2017-03-12 | 15 | 8292 | 115.536 | 1.393% | 20.8682 | 0.2517% | 136.4042 | 1.645% | 1859 | 8271.1318 | 8155.5958 | 1.417% | 0.2559%
2017-05-21 | 18 | 8293 | 115.5477 | 1.393% | 20.8701 | 0.2517% | 136.4177 | 1.645% | 1860 | 8272.1299 | 8156.5823 | 1.417% | 0.2559%
2017-04-27 | 15 | 8296 | 115.5828 | 1.393% | 20.8757 | 0.2516% | 136.4585 | 1.645% | 1861 | 8275.1243 | 8159.5415 | 1.417% | 0.2558%
2017-05-02 | 19 | 8304 | 115.6765 | 1.393% | 20.8906 | 0.2516% | 136.5671 | 1.645% | 1862 | 8283.1094 | 8167.4329 | 1.416% | 0.2558%
2017-03-23 | 11 | 8311 | 115.7584 | 1.393% | 20.9036 | 0.2515% | 136.6621 | 1.644% | 1863 | 8290.0964 | 8174.3379 | 1.416% | 0.2557%
2017-03-13 | 23 | 8312 | 115.7701 | 1.393% | 20.9055 | 0.2515% | 136.6757 | 1.644% | 1864 | 8291.0945 | 8175.3243 | 1.416% | 0.2557%
2017-03-16 | 14 | 8324 | 115.9106 | 1.392% | 20.9279 | 0.2514% | 136.8385 | 1.644% | 1865 | 8303.0721 | 8187.1615 | 1.416% | 0.2556%
2017-04-22 | 19 | 8326 | 115.9341 | 1.392% | 20.9316 | 0.2514% | 136.8657 | 1.644% | 1866 | 8305.0684 | 8189.1343 | 1.416% | 0.2556%
2017-05-28 | 12 | 8326 | 115.9341 | 1.392% | 20.9316 | 0.2514% | 136.8657 | 1.644% | 1867 | 8305.0684 | 8189.1343 | 1.416% | 0.2556%
2017-05-11 | 22 | 8331 | 115.9926 | 1.392% | 20.941 | 0.2514% | 136.9336 | 1.644% | 1868 | 8310.059 | 8194.0664 | 1.416% | 0.2556%
2017-04-30 | 13 | 8333 | 116.016 | 1.392% | 20.9447 | 0.2513% | 136.9607 | 1.644% | 1869 | 8312.0553 | 8196.0393 | 1.416% | 0.2555%
2017-03-20 | 11 | 8335 | 116.0394 | 1.392% | 20.9484 | 0.2513% | 136.9879 | 1.644% | 1870 | 8314.0516 | 8198.0121 | 1.415% | 0.2555%
2017-03-13 | 1 | 8338 | 116.0746 | 1.392% | 20.954 | 0.2513% | 137.0286 | 1.643% | 1871 | 8317.046 | 8200.9714 | 1.415% | 0.2555%
2017-04-22 | 14 | 8343 | 116.1331 | 1.392% | 20.9633 | 0.2513% | 137.0965 | 1.643% | 1872 | 8322.0367 | 8205.9035 | 1.415% | 0.2555%
2017-03-15 | 1 | 8358 | 116.3088 | 1.392% | 20.9913 | 0.2512% | 137.3001 | 1.643% | 1873 | 8337.0087 | 8220.6999 | 1.415% | 0.2553%
2017-04-17 | 18 | 8359 | 116.3205 | 1.392% | 20.9932 | 0.2511% | 137.3136 | 1.643% | 1874 | 8338.0068 | 8221.6864 | 1.415% | 0.2553%
2017-03-14 | 13 | 8365 | 116.3907 | 1.391% | 21.0044 | 0.2511% | 137.3951 | 1.642% | 1875 | 8343.9956 | 8227.6049 | 1.415% | 0.2553%
2017-04-17 | 17 | 8371 | 116.461 | 1.391% | 21.0156 | 0.2511% | 137.4765 | 1.642% | 1876 | 8349.9844 | 8233.5235 | 1.414% | 0.2552%
2017-03-12 | 9 | 8372 | 116.4727 | 1.391% | 21.0174 | 0.251% | 137.4901 | 1.642% | 1877 | 8350.9826 | 8234.5099 | 1.414% | 0.2552%
2017-05-02 | 17 | 8375 | 116.5078 | 1.391% | 21.023 | 0.251% | 137.5308 | 1.642% | 1878 | 8353.977 | 8237.4692 | 1.414% | 0.2552%
2017-04-20 | 20 | 8382 | 116.5898 | 1.391% | 21.0361 | 0.251% | 137.6259 | 1.642% | 1879 | 8360.9639 | 8244.3741 | 1.414% | 0.2552%
2017-05-28 | 22 | 8383 | 116.6015 | 1.391% | 21.038 | 0.251% | 137.6394 | 1.642% | 1880 | 8361.962 | 8245.3606 | 1.414% | 0.2551%
2017-03-12 | 20 | 8394 | 116.7303 | 1.391% | 21.0585 | 0.2509% | 137.7887 | 1.642% | 1881 | 8372.9415 | 8256.2113 | 1.414% | 0.2551%
2017-04-20 | 21 | 8398 | 116.7771 | 1.391% | 21.0659 | 0.2508% | 137.843 | 1.641% | 1882 | 8376.9341 | 8260.157 | 1.414% | 0.255%
2017-03-14 | 24 | 8401 | 116.8122 | 1.39% | 21.0715 | 0.2508% | 137.8838 | 1.641% | 1883 | 8379.9285 | 8263.1162 | 1.414% | 0.255%
2017-05-26 | 16 | 8402 | 116.8239 | 1.39% | 21.0734 | 0.2508% | 137.8973 | 1.641% | 1884 | 8380.9266 | 8264.1027 | 1.414% | 0.255%
2017-05-03 | 17 | 8403 | 116.8357 | 1.39% | 21.0753 | 0.2508% | 137.9109 | 1.641% | 1885 | 8381.9247 | 8265.0891 | 1.414% | 0.255%
2017-04-27 | 18 | 8409 | 116.9059 | 1.39% | 21.0865 | 0.2508% | 137.9924 | 1.641% | 1886 | 8387.9135 | 8271.0076 | 1.413% | 0.2549%
2017-04-21 | 13 | 8410 | 116.9176 | 1.39% | 21.0883 | 0.2508% | 138.0059 | 1.641% | 1887 | 8388.9117 | 8271.9941 | 1.413% | 0.2549%
2017-04-27 | 16 | 8418 | 117.0113 | 1.39% | 21.1032 | 0.2507% | 138.1145 | 1.641% | 1888 | 8396.8968 | 8279.8855 | 1.413% | 0.2549%
2017-05-01 | 22 | 8422 | 117.0581 | 1.39% | 21.1107 | 0.2507% | 138.1688 | 1.641% | 1889 | 8400.8893 | 8283.8312 | 1.413% | 0.2548%
2017-03-13 | 2 | 8426 | 117.105 | 1.39% | 21.1182 | 0.2506% | 138.2231 | 1.64% | 1890 | 8404.8818 | 8287.7769 | 1.413% | 0.2548%
2017-05-10 | 16 | 8426 | 117.105 | 1.39% | 21.1182 | 0.2506% | 138.2231 | 1.64% | 1891 | 8404.8818 | 8287.7769 | 1.413% | 0.2548%
2017-05-30 | 12 | 8430 | 117.1518 | 1.39% | 21.1256 | 0.2506% | 138.2774 | 1.64% | 1892 | 8408.8744 | 8291.7226 | 1.413% | 0.2548%
2017-05-02 | 18 | 8442 | 117.2923 | 1.389% | 21.148 | 0.2505% | 138.4403 | 1.64% | 1893 | 8420.852 | 8303.5597 | 1.413% | 0.2547%
2017-04-20 | 19 | 8443 | 117.304 | 1.389% | 21.1499 | 0.2505% | 138.4539 | 1.64% | 1894 | 8421.8501 | 8304.5461 | 1.413% | 0.2547%
2017-05-15 | 22 | 8448 | 117.3626 | 1.389% | 21.1592 | 0.2505% | 138.5218 | 1.64% | 1895 | 8426.8408 | 8309.4782 | 1.412% | 0.2546%
2017-04-20 | 17 | 8456 | 117.4562 | 1.389% | 21.1741 | 0.2504% | 138.6304 | 1.639% | 1896 | 8434.8259 | 8317.3696 | 1.412% | 0.2546%
2017-03-06 | 6 | 8462 | 117.5265 | 1.389% | 21.1853 | 0.2504% | 138.7118 | 1.639% | 1897 | 8440.8147 | 8323.2882 | 1.412% | 0.2545%
2017-04-20 | 18 | 8483 | 117.7724 | 1.388% | 21.2245 | 0.2502% | 138.9969 | 1.639% | 1898 | 8461.7755 | 8344.0031 | 1.411% | 0.2544%
2017-04-21 | 21 | 8486 | 117.8075 | 1.388% | 21.2301 | 0.2502% | 139.0376 | 1.638% | 1899 | 8464.7699 | 8346.9624 | 1.411% | 0.2543%
2017-03-23 | 7 | 8489 | 117.8426 | 1.388% | 21.2357 | 0.2502% | 139.0783 | 1.638% | 1900 | 8467.7643 | 8349.9217 | 1.411% | 0.2543%
2017-03-12 | 24 | 8493 | 117.8895 | 1.388% | 21.2431 | 0.2501% | 139.1326 | 1.638% | 1901 | 8471.7569 | 8353.8674 | 1.411% | 0.2543%
2017-05-15 | 14 | 8493 | 117.8895 | 1.388% | 21.2431 | 0.2501% | 139.1326 | 1.638% | 1902 | 8471.7569 | 8353.8674 | 1.411% | 0.2543%
2017-03-05 | 7 | 8496 | 117.9246 | 1.388% | 21.2487 | 0.2501% | 139.1733 | 1.638% | 1903 | 8474.7513 | 8356.8267 | 1.411% | 0.2543%
2017-03-03 | 9 | 8499 | 117.9597 | 1.388% | 21.2543 | 0.2501% | 139.2141 | 1.638% | 1904 | 8477.7457 | 8359.7859 | 1.411% | 0.2542%
2017-04-28 | 12 | 8505 | 118.03 | 1.388% | 21.2655 | 0.25% | 139.2955 | 1.638% | 1905 | 8483.7345 | 8365.7045 | 1.411% | 0.2542%
2017-05-03 | 19 | 8508 | 118.0651 | 1.388% | 21.2711 | 0.25% | 139.3362 | 1.638% | 1906 | 8486.7289 | 8368.6638 | 1.411% | 0.2542%
2017-03-15 | 2 | 8512 | 118.1119 | 1.388% | 21.2786 | 0.25% | 139.3905 | 1.638% | 1907 | 8490.7214 | 8372.6095 | 1.411% | 0.2541%
2017-03-04 | 10 | 8513 | 118.1236 | 1.388% | 21.2805 | 0.25% | 139.4041 | 1.638% | 1908 | 8491.7195 | 8373.5959 | 1.411% | 0.2541%
2017-03-16 | 20 | 8514 | 118.1354 | 1.388% | 21.2823 | 0.25% | 139.4177 | 1.638% | 1909 | 8492.7177 | 8374.5823 | 1.411% | 0.2541%
2017-04-27 | 17 | 8524 | 118.2524 | 1.387% | 21.301 | 0.2499% | 139.5534 | 1.637% | 1910 | 8502.699 | 8384.4466 | 1.41% | 0.2541%
2017-03-04 | 6 | 8528 | 118.2993 | 1.387% | 21.3084 | 0.2499% | 139.6077 | 1.637% | 1911 | 8506.6916 | 8388.3923 | 1.41% | 0.254%
2017-03-24 | 10 | 8548 | 118.5335 | 1.387% | 21.3457 | 0.2497% | 139.8792 | 1.636% | 1912 | 8526.6543 | 8408.1208 | 1.41% | 0.2539%
2017-04-22 | 15 | 8548 | 118.5335 | 1.387% | 21.3457 | 0.2497% | 139.8792 | 1.636% | 1913 | 8526.6543 | 8408.1208 | 1.41% | 0.2539%
2017-05-22 | 13 | 8553 | 118.592 | 1.387% | 21.3551 | 0.2497% | 139.9471 | 1.636% | 1914 | 8531.6449 | 8413.0529 | 1.41% | 0.2538%
2017-04-21 | 20 | 8570 | 118.7911 | 1.386% | 21.3868 | 0.2496% | 140.1778 | 1.636% | 1915 | 8548.6132 | 8429.8222 | 1.409% | 0.2537%
2017-05-10 | 21 | 8570 | 118.7911 | 1.386% | 21.3868 | 0.2496% | 140.1778 | 1.636% | 1916 | 8548.6132 | 8429.8222 | 1.409% | 0.2537%
2017-05-27 | 22 | 8578 | 118.8847 | 1.386% | 21.4017 | 0.2495% | 140.2864 | 1.635% | 1917 | 8556.5983 | 8437.7136 | 1.409% | 0.2536%
2017-05-26 | 19 | 8579 | 118.8964 | 1.386% | 21.4036 | 0.2495% | 140.3 | 1.635% | 1918 | 8557.5964 | 8438.7 | 1.409% | 0.2536%
2017-05-16 | 13 | 8592 | 119.0486 | 1.386% | 21.4278 | 0.2494% | 140.4765 | 1.635% | 1919 | 8570.5722 | 8451.5235 | 1.409% | 0.2535%
2017-03-13 | 3 | 8594 | 119.0721 | 1.386% | 21.4316 | 0.2494% | 140.5036 | 1.635% | 1920 | 8572.5684 | 8453.4964 | 1.409% | 0.2535%
2017-03-17 | 12 | 8599 | 119.1306 | 1.385% | 21.4409 | 0.2493% | 140.5715 | 1.635% | 1921 | 8577.5591 | 8458.4285 | 1.408% | 0.2535%
2017-04-30 | 21 | 8600 | 119.1423 | 1.385% | 21.4427 | 0.2493% | 140.5851 | 1.635% | 1922 | 8578.5573 | 8459.4149 | 1.408% | 0.2535%
2017-05-11 | 14 | 8603 | 119.1774 | 1.385% | 21.4483 | 0.2493% | 140.6258 | 1.635% | 1923 | 8581.5517 | 8462.3742 | 1.408% | 0.2535%
2017-05-31 | 22 | 8609 | 119.2477 | 1.385% | 21.4595 | 0.2493% | 140.7072 | 1.634% | 1924 | 8587.5405 | 8468.2928 | 1.408% | 0.2534%
2017-04-29 | 22 | 8612 | 119.2828 | 1.385% | 21.4651 | 0.2492% | 140.748 | 1.634% | 1925 | 8590.5349 | 8471.252 | 1.408% | 0.2534%
2017-05-03 | 18 | 8612 | 119.2828 | 1.385% | 21.4651 | 0.2492% | 140.748 | 1.634% | 1926 | 8590.5349 | 8471.252 | 1.408% | 0.2534%
2017-03-24 | 7 | 8617 | 119.3414 | 1.385% | 21.4745 | 0.2492% | 140.8158 | 1.634% | 1927 | 8595.5255 | 8476.1842 | 1.408% | 0.2534%
2017-03-17 | 1 | 8619 | 119.3648 | 1.385% | 21.4782 | 0.2492% | 140.843 | 1.634% | 1928 | 8597.5218 | 8478.157 | 1.408% | 0.2533%
2017-03-13 | 16 | 8621 | 119.3882 | 1.385% | 21.4819 | 0.2492% | 140.8701 | 1.634% | 1929 | 8599.5181 | 8480.1299 | 1.408% | 0.2533%
2017-03-14 | 20 | 8625 | 119.435 | 1.385% | 21.4894 | 0.2492% | 140.9244 | 1.634% | 1930 | 8603.5106 | 8484.0756 | 1.408% | 0.2533%
2017-05-26 | 17 | 8637 | 119.5756 | 1.384% | 21.5118 | 0.2491% | 141.0873 | 1.634% | 1931 | 8615.4882 | 8495.9127 | 1.407% | 0.2532%
2017-05-01 | 13 | 8647 | 119.6926 | 1.384% | 21.5304 | 0.249% | 141.2231 | 1.633% | 1932 | 8625.4696 | 8505.7769 | 1.407% | 0.2531%
2017-05-18 | 12 | 8653 | 119.7629 | 1.384% | 21.5416 | 0.2489% | 141.3045 | 1.633% | 1933 | 8631.4584 | 8511.6955 | 1.407% | 0.2531%
2017-03-13 | 15 | 8655 | 119.7863 | 1.384% | 21.5453 | 0.2489% | 141.3317 | 1.633% | 1934 | 8633.4547 | 8513.6683 | 1.407% | 0.2531%
2017-03-03 | 7 | 8656 | 119.798 | 1.384% | 21.5472 | 0.2489% | 141.3452 | 1.633% | 1935 | 8634.4528 | 8514.6548 | 1.407% | 0.2531%
2017-03-14 | 23 | 8664 | 119.8917 | 1.384% | 21.5621 | 0.2489% | 141.4538 | 1.633% | 1936 | 8642.4379 | 8522.5462 | 1.407% | 0.253%
2017-05-22 | 21 | 8664 | 119.8917 | 1.384% | 21.5621 | 0.2489% | 141.4538 | 1.633% | 1937 | 8642.4379 | 8522.5462 | 1.407% | 0.253%
2017-05-31 | 12 | 8665 | 119.9034 | 1.384% | 21.564 | 0.2489% | 141.4674 | 1.633% | 1938 | 8643.436 | 8523.5326 | 1.407% | 0.253%
2017-04-30 | 20 | 8669 | 119.9502 | 1.384% | 21.5715 | 0.2488% | 141.5217 | 1.633% | 1939 | 8647.4285 | 8527.4783 | 1.407% | 0.253%
2017-03-05 | 8 | 8677 | 120.0439 | 1.383% | 21.5864 | 0.2488% | 141.6303 | 1.632% | 1940 | 8655.4136 | 8535.3697 | 1.406% | 0.2529%
2017-04-22 | 16 | 8677 | 120.0439 | 1.383% | 21.5864 | 0.2488% | 141.6303 | 1.632% | 1941 | 8655.4136 | 8535.3697 | 1.406% | 0.2529%
2017-04-22 | 18 | 8679 | 120.0673 | 1.383% | 21.5901 | 0.2488% | 141.6574 | 1.632% | 1942 | 8657.4099 | 8537.3426 | 1.406% | 0.2529%
2017-05-10 | 20 | 8684 | 120.1259 | 1.383% | 21.5994 | 0.2487% | 141.7253 | 1.632% | 1943 | 8662.4006 | 8542.2747 | 1.406% | 0.2529%
2017-03-05 | 9 | 8690 | 120.1961 | 1.383% | 21.6106 | 0.2487% | 141.8068 | 1.632% | 1944 | 8668.3894 | 8548.1932 | 1.406% | 0.2528%
2017-04-30 | 14 | 8698 | 120.2898 | 1.383% | 21.6256 | 0.2486% | 141.9154 | 1.632% | 1945 | 8676.3744 | 8556.0846 | 1.406% | 0.2528%
2017-04-29 | 12 | 8699 | 120.3015 | 1.383% | 21.6274 | 0.2486% | 141.9289 | 1.632% | 1946 | 8677.3726 | 8557.0711 | 1.406% | 0.2527%
2017-05-26 | 18 | 8709 | 120.4186 | 1.383% | 21.6461 | 0.2485% | 142.0647 | 1.631% | 1947 | 8687.3539 | 8566.9353 | 1.406% | 0.2527%
2017-04-22 | 17 | 8710 | 120.4303 | 1.383% | 21.6479 | 0.2485% | 142.0783 | 1.631% | 1948 | 8688.3521 | 8567.9217 | 1.406% | 0.2527%
2017-03-23 | 10 | 8714 | 120.4771 | 1.383% | 21.6554 | 0.2485% | 142.1325 | 1.631% | 1949 | 8692.3446 | 8571.8675 | 1.405% | 0.2526%
2017-03-15 | 17 | 8720 | 120.5474 | 1.382% | 21.6666 | 0.2485% | 142.214 | 1.631% | 1950 | 8698.3334 | 8577.786 | 1.405% | 0.2526%
2017-03-12 | 23 | 8725 | 120.6059 | 1.382% | 21.6759 | 0.2484% | 142.2819 | 1.631% | 1951 | 8703.3241 | 8582.7181 | 1.405% | 0.2526%
2017-03-17 | 2 | 8733 | 120.6996 | 1.382% | 21.6908 | 0.2484% | 142.3905 | 1.63% | 1952 | 8711.3092 | 8590.6095 | 1.405% | 0.2525%
2017-03-16 | 24 | 8747 | 120.8635 | 1.382% | 21.717 | 0.2483% | 142.5805 | 1.63% | 1953 | 8725.283 | 8604.4195 | 1.405% | 0.2524%
2017-03-15 | 18 | 8749 | 120.887 | 1.382% | 21.7207 | 0.2483% | 142.6077 | 1.63% | 1954 | 8727.2793 | 8606.3923 | 1.405% | 0.2524%
2017-03-06 | 9 | 8751 | 120.9104 | 1.382% | 21.7244 | 0.2483% | 142.6348 | 1.63% | 1955 | 8729.2756 | 8608.3652 | 1.405% | 0.2524%
2017-03-13 | 17 | 8753 | 120.9338 | 1.382% | 21.7282 | 0.2482% | 142.6619 | 1.63% | 1956 | 8731.2718 | 8610.3381 | 1.405% | 0.2523%
2017-03-13 | 14 | 8770 | 121.1328 | 1.381% | 21.7599 | 0.2481% | 142.8927 | 1.629% | 1957 | 8748.2401 | 8627.1073 | 1.404% | 0.2522%
2017-05-19 | 22 | 8774 | 121.1797 | 1.381% | 21.7673 | 0.2481% | 142.947 | 1.629% | 1958 | 8752.2327 | 8631.053 | 1.404% | 0.2522%
2017-03-13 | 4 | 8776 | 121.2031 | 1.381% | 21.7711 | 0.2481% | 142.9742 | 1.629% | 1959 | 8754.2289 | 8633.0258 | 1.404% | 0.2522%
2017-05-29 | 12 | 8777 | 121.2148 | 1.381% | 21.7729 | 0.2481% | 142.9877 | 1.629% | 1960 | 8755.2271 | 8634.0123 | 1.404% | 0.2522%
2017-05-10 | 17 | 8788 | 121.3436 | 1.381% | 21.7934 | 0.248% | 143.1371 | 1.629% | 1961 | 8766.2066 | 8644.8629 | 1.404% | 0.2521%
2017-05-28 | 21 | 8793 | 121.4021 | 1.381% | 21.8028 | 0.248% | 143.2049 | 1.629% | 1962 | 8771.1972 | 8649.7951 | 1.404% | 0.2521%
2017-03-12 | 14 | 8800 | 121.4841 | 1.381% | 21.8158 | 0.2479% | 143.2999 | 1.628% | 1963 | 8778.1842 | 8656.7001 | 1.403% | 0.252%
2017-05-30 | 13 | 8800 | 121.4841 | 1.381% | 21.8158 | 0.2479% | 143.2999 | 1.628% | 1964 | 8778.1842 | 8656.7001 | 1.403% | 0.252%
2017-03-15 | 3 | 8801 | 121.4958 | 1.38% | 21.8177 | 0.2479% | 143.3135 | 1.628% | 1965 | 8779.1823 | 8657.6865 | 1.403% | 0.252%
2017-05-19 | 12 | 8818 | 121.6949 | 1.38% | 21.8494 | 0.2478% | 143.5443 | 1.628% | 1966 | 8796.1506 | 8674.4557 | 1.403% | 0.2519%
2017-05-22 | 20 | 8821 | 121.73 | 1.38% | 21.855 | 0.2478% | 143.585 | 1.628% | 1967 | 8799.145 | 8677.415 | 1.403% | 0.2519%
2017-04-28 | 22 | 8832 | 121.8588 | 1.38% | 21.8755 | 0.2477% | 143.7343 | 1.627% | 1968 | 8810.1245 | 8688.2657 | 1.403% | 0.2518%
2017-05-28 | 13 | 8834 | 121.8822 | 1.38% | 21.8793 | 0.2477% | 143.7615 | 1.627% | 1969 | 8812.1207 | 8690.2385 | 1.403% | 0.2518%
2017-05-20 | 12 | 8835 | 121.8939 | 1.38% | 21.8811 | 0.2477% | 143.775 | 1.627% | 1970 | 8813.1189 | 8691.225 | 1.402% | 0.2518%
2017-04-21 | 14 | 8846 | 122.0227 | 1.379% | 21.9016 | 0.2476% | 143.9244 | 1.627% | 1971 | 8824.0984 | 8702.0756 | 1.402% | 0.2517%
2017-03-13 | 22 | 8851 | 122.0813 | 1.379% | 21.911 | 0.2476% | 143.9922 | 1.627% | 1972 | 8829.089 | 8707.0078 | 1.402% | 0.2516%
2017-05-27 | 14 | 8851 | 122.0813 | 1.379% | 21.911 | 0.2476% | 143.9922 | 1.627% | 1973 | 8829.089 | 8707.0078 | 1.402% | 0.2516%
2017-04-28 | 13 | 8856 | 122.1398 | 1.379% | 21.9203 | 0.2475% | 144.0601 | 1.627% | 1974 | 8834.0797 | 8711.9399 | 1.402% | 0.2516%
2017-05-11 | 21 | 8859 | 122.1749 | 1.379% | 21.9259 | 0.2475% | 144.1008 | 1.627% | 1975 | 8837.0741 | 8714.8992 | 1.402% | 0.2516%
2017-03-04 | 7 | 8871 | 122.3154 | 1.379% | 21.9483 | 0.2474% | 144.2637 | 1.626% | 1976 | 8849.0517 | 8726.7363 | 1.402% | 0.2515%
2017-03-16 | 13 | 8883 | 122.456 | 1.379% | 21.9707 | 0.2473% | 144.4266 | 1.626% | 1977 | 8861.0293 | 8738.5734 | 1.401% | 0.2514%
2017-05-01 | 21 | 8891 | 122.5496 | 1.378% | 21.9856 | 0.2473% | 144.5352 | 1.626% | 1978 | 8869.0144 | 8746.4648 | 1.401% | 0.2514%
2017-05-27 | 21 | 8891 | 122.5496 | 1.378% | 21.9856 | 0.2473% | 144.5352 | 1.626% | 1979 | 8869.0144 | 8746.4648 | 1.401% | 0.2514%
2017-05-01 | 20 | 8899 | 122.6433 | 1.378% | 22.0005 | 0.2472% | 144.6438 | 1.625% | 1980 | 8876.9995 | 8754.3562 | 1.401% | 0.2513%
2017-05-15 | 21 | 8910 | 122.7721 | 1.378% | 22.021 | 0.2471% | 144.7931 | 1.625% | 1981 | 8887.979 | 8765.2069 | 1.401% | 0.2512%
2017-03-04 | 9 | 8916 | 122.8424 | 1.378% | 22.0322 | 0.2471% | 144.8746 | 1.625% | 1982 | 8893.9678 | 8771.1254 | 1.401% | 0.2512%
2017-05-11 | 15 | 8918 | 122.8658 | 1.378% | 22.0359 | 0.2471% | 144.9017 | 1.625% | 1983 | 8895.9641 | 8773.0983 | 1.4% | 0.2512%
2017-05-31 | 13 | 8918 | 122.8658 | 1.378% | 22.0359 | 0.2471% | 144.9017 | 1.625% | 1984 | 8895.9641 | 8773.0983 | 1.4% | 0.2512%
2017-05-17 | 12 | 8919 | 122.8775 | 1.378% | 22.0378 | 0.2471% | 144.9153 | 1.625% | 1985 | 8896.9622 | 8774.0847 | 1.4% | 0.2512%
2017-03-12 | 22 | 8920 | 122.8892 | 1.378% | 22.0397 | 0.2471% | 144.9289 | 1.625% | 1986 | 8897.9603 | 8775.0711 | 1.4% | 0.2512%
2017-03-03 | 8 | 8922 | 122.9126 | 1.378% | 22.0434 | 0.2471% | 144.956 | 1.625% | 1987 | 8899.9566 | 8777.044 | 1.4% | 0.2511%
2017-03-12 | 21 | 8926 | 122.9594 | 1.378% | 22.0509 | 0.247% | 145.0103 | 1.625% | 1988 | 8903.9491 | 8780.9897 | 1.4% | 0.2511%
2017-05-31 | 21 | 8926 | 122.9594 | 1.378% | 22.0509 | 0.247% | 145.0103 | 1.625% | 1989 | 8903.9491 | 8780.9897 | 1.4% | 0.2511%
2017-03-17 | 3 | 8931 | 123.018 | 1.377% | 22.0602 | 0.247% | 145.0782 | 1.624% | 1990 | 8908.9398 | 8785.9218 | 1.4% | 0.2511%
2017-05-01 | 14 | 8936 | 123.0765 | 1.377% | 22.0695 | 0.247% | 145.1461 | 1.624% | 1991 | 8913.9305 | 8790.8539 | 1.4% | 0.2511%
2017-03-14 | 22 | 8937 | 123.0882 | 1.377% | 22.0714 | 0.247% | 145.1596 | 1.624% | 1992 | 8914.9286 | 8791.8404 | 1.4% | 0.251%
2017-05-20 | 22 | 8943 | 123.1585 | 1.377% | 22.0826 | 0.2469% | 145.2411 | 1.624% | 1993 | 8920.9174 | 8797.7589 | 1.4% | 0.251%
2017-04-30 | 15 | 8945 | 123.1819 | 1.377% | 22.0863 | 0.2469% | 145.2682 | 1.624% | 1994 | 8922.9137 | 8799.7318 | 1.4% | 0.251%
2017-04-21 | 15 | 8949 | 123.2287 | 1.377% | 22.0938 | 0.2469% | 145.3225 | 1.624% | 1995 | 8926.9062 | 8803.6775 | 1.4% | 0.251%
2017-05-22 | 14 | 8954 | 123.2873 | 1.377% | 22.1031 | 0.2469% | 145.3904 | 1.624% | 1996 | 8931.8969 | 8808.6096 | 1.4% | 0.2509%
2017-05-10 | 19 | 8956 | 123.3107 | 1.377% | 22.1068 | 0.2468% | 145.4175 | 1.624% | 1997 | 8933.8932 | 8810.5825 | 1.4% | 0.2509%
2017-05-15 | 15 | 8956 | 123.3107 | 1.377% | 22.1068 | 0.2468% | 145.4175 | 1.624% | 1998 | 8933.8932 | 8810.5825 | 1.4% | 0.2509%
2017-03-13 | 18 | 8959 | 123.3458 | 1.377% | 22.1124 | 0.2468% | 145.4583 | 1.624% | 1999 | 8936.8876 | 8813.5417 | 1.4% | 0.2509%
2017-03-14 | 12 | 8961 | 123.3693 | 1.377% | 22.1162 | 0.2468% | 145.4854 | 1.624% | 2000 | 8938.8838 | 8815.5146 | 1.399% | 0.2509%
2017-05-11 | 20 | 8967 | 123.4395 | 1.377% | 22.1274 | 0.2468% | 145.5669 | 1.623% | 2001 | 8944.8726 | 8821.4331 | 1.399% | 0.2508%
2017-03-16 | 23 | 8969 | 123.4629 | 1.377% | 22.1311 | 0.2468% | 145.594 | 1.623% | 2002 | 8946.8689 | 8823.406 | 1.399% | 0.2508%
2017-05-10 | 18 | 8982 | 123.6151 | 1.376% | 22.1553 | 0.2467% | 145.7705 | 1.623% | 2003 | 8959.8447 | 8836.2295 | 1.399% | 0.2507%
2017-03-12 | 10 | 8992 | 123.7322 | 1.376% | 22.174 | 0.2466% | 145.9062 | 1.623% | 2004 | 8969.826 | 8846.0938 | 1.399% | 0.2507%
2017-05-16 | 22 | 9001 | 123.8376 | 1.376% | 22.1908 | 0.2465% | 146.0284 | 1.622% | 2005 | 8978.8092 | 8854.9716 | 1.399% | 0.2506%
2017-04-21 | 19 | 9004 | 123.8727 | 1.376% | 22.1964 | 0.2465% | 146.0691 | 1.622% | 2006 | 8981.8036 | 8857.9309 | 1.398% | 0.2506%
2017-03-13 | 13 | 9005 | 123.8844 | 1.376% | 22.1982 | 0.2465% | 146.0827 | 1.622% | 2007 | 8982.8018 | 8858.9173 | 1.398% | 0.2506%
2017-03-14 | 21 | 9008 | 123.9196 | 1.376% | 22.2038 | 0.2465% | 146.1234 | 1.622% | 2008 | 8985.7962 | 8861.8766 | 1.398% | 0.2506%
2017-05-30 | 22 | 9010 | 123.943 | 1.376% | 22.2076 | 0.2465% | 146.1506 | 1.622% | 2009 | 8987.7924 | 8863.8494 | 1.398% | 0.2505%
2017-03-24 | 9 | 9041 | 124.306 | 1.375% | 22.2654 | 0.2463% | 146.5714 | 1.621% | 2010 | 9018.7346 | 8894.4286 | 1.398% | 0.2503%
2017-04-30 | 19 | 9049 | 124.3996 | 1.375% | 22.2803 | 0.2462% | 146.68 | 1.621% | 2011 | 9026.7197 | 8902.32 | 1.397% | 0.2503%
2017-05-31 | 20 | 9053 | 124.4465 | 1.375% | 22.2878 | 0.2462% | 146.7343 | 1.621% | 2012 | 9030.7122 | 8906.2657 | 1.397% | 0.2502%
2017-04-29 | 21 | 9086 | 124.8329 | 1.374% | 22.3493 | 0.246% | 147.1822 | 1.62% | 2013 | 9063.6507 | 8938.8178 | 1.397% | 0.25%
2017-05-28 | 20 | 9098 | 124.9734 | 1.374% | 22.3717 | 0.2459% | 147.3451 | 1.62% | 2014 | 9075.6283 | 8950.6549 | 1.396% | 0.2499%
2017-03-13 | 5 | 9107 | 125.0788 | 1.373% | 22.3885 | 0.2458% | 147.4673 | 1.619% | 2015 | 9084.6115 | 8959.5327 | 1.396% | 0.2499%
2017-03-20 | 10 | 9108 | 125.0905 | 1.373% | 22.3904 | 0.2458% | 147.4808 | 1.619% | 2016 | 9085.6096 | 8960.5192 | 1.396% | 0.2499%
2017-03-04 | 8 | 9113 | 125.149 | 1.373% | 22.3997 | 0.2458% | 147.5487 | 1.619% | 2017 | 9090.6003 | 8965.4513 | 1.396% | 0.2498%
2017-05-18 | 22 | 9115 | 125.1724 | 1.373% | 22.4034 | 0.2458% | 147.5759 | 1.619% | 2018 | 9092.5966 | 8967.4241 | 1.396% | 0.2498%
2017-04-21 | 18 | 9120 | 125.231 | 1.373% | 22.4128 | 0.2458% | 147.6437 | 1.619% | 2019 | 9097.5872 | 8972.3563 | 1.396% | 0.2498%
2017-05-29 | 22 | 9130 | 125.3481 | 1.373% | 22.4314 | 0.2457% | 147.7795 | 1.619% | 2020 | 9107.5686 | 8982.2205 | 1.396% | 0.2497%
2017-04-21 | 16 | 9132 | 125.3715 | 1.373% | 22.4351 | 0.2457% | 147.8066 | 1.619% | 2021 | 9109.5649 | 8984.1934 | 1.395% | 0.2497%
2017-05-18 | 13 | 9132 | 125.3715 | 1.373% | 22.4351 | 0.2457% | 147.8066 | 1.619% | 2022 | 9109.5649 | 8984.1934 | 1.395% | 0.2497%
2017-05-22 | 19 | 9135 | 125.4066 | 1.373% | 22.4407 | 0.2457% | 147.8474 | 1.618% | 2023 | 9112.5593 | 8987.1526 | 1.395% | 0.2497%
2017-05-15 | 20 | 9143 | 125.5003 | 1.373% | 22.4557 | 0.2456% | 147.956 | 1.618% | 2024 | 9120.5443 | 8995.044 | 1.395% | 0.2496%
2017-03-15 | 4 | 9146 | 125.5354 | 1.373% | 22.4613 | 0.2456% | 147.9967 | 1.618% | 2025 | 9123.5387 | 8998.0033 | 1.395% | 0.2496%
2017-05-01 | 15 | 9154 | 125.6291 | 1.372% | 22.4762 | 0.2455% | 148.1053 | 1.618% | 2026 | 9131.5238 | 9005.8947 | 1.395% | 0.2496%
2017-04-30 | 16 | 9158 | 125.6759 | 1.372% | 22.4836 | 0.2455% | 148.1596 | 1.618% | 2027 | 9135.5164 | 9009.8404 | 1.395% | 0.2495%
2017-03-17 | 4 | 9163 | 125.7345 | 1.372% | 22.493 | 0.2455% | 148.2274 | 1.618% | 2028 | 9140.507 | 9014.7726 | 1.395% | 0.2495%
2017-04-29 | 13 | 9168 | 125.793 | 1.372% | 22.5023 | 0.2454% | 148.2953 | 1.618% | 2029 | 9145.4977 | 9019.7047 | 1.395% | 0.2495%
2017-05-19 | 21 | 9173 | 125.8516 | 1.372% | 22.5116 | 0.2454% | 148.3632 | 1.617% | 2030 | 9150.4884 | 9024.6368 | 1.395% | 0.2494%
2017-03-13 | 19 | 9178 | 125.9101 | 1.372% | 22.521 | 0.2454% | 148.4311 | 1.617% | 2031 | 9155.479 | 9029.5689 | 1.394% | 0.2494%
2017-05-17 | 22 | 9189 | 126.0389 | 1.372% | 22.5415 | 0.2453% | 148.5804 | 1.617% | 2032 | 9166.4585 | 9040.4196 | 1.394% | 0.2493%
2017-05-01 | 19 | 9202 | 126.1911 | 1.371% | 22.5657 | 0.2452% | 148.7568 | 1.617% | 2033 | 9179.4343 | 9053.2432 | 1.394% | 0.2493%
2017-03-15 | 19 | 9208 | 126.2614 | 1.371% | 22.5769 | 0.2452% | 148.8383 | 1.616% | 2034 | 9185.4231 | 9059.1617 | 1.394% | 0.2492%
2017-04-28 | 21 | 9210 | 126.2848 | 1.371% | 22.5807 | 0.2452% | 148.8654 | 1.616% | 2035 | 9187.4193 | 9061.1346 | 1.394% | 0.2492%
2017-03-12 | 11 | 9217 | 126.3667 | 1.371% | 22.5937 | 0.2451% | 148.9605 | 1.616% | 2036 | 9194.4063 | 9068.0395 | 1.394% | 0.2492%
2017-05-11 | 16 | 9217 | 126.3667 | 1.371% | 22.5937 | 0.2451% | 148.9605 | 1.616% | 2037 | 9194.4063 | 9068.0395 | 1.394% | 0.2492%
2017-03-14 | 7 | 9221 | 126.4136 | 1.371% | 22.6012 | 0.2451% | 149.0148 | 1.616% | 2038 | 9198.3988 | 9071.9852 | 1.393% | 0.2491%
2017-03-15 | 16 | 9227 | 126.4838 | 1.371% | 22.6124 | 0.2451% | 149.0962 | 1.616% | 2039 | 9204.3876 | 9077.9038 | 1.393% | 0.2491%
2017-05-28 | 14 | 9230 | 126.519 | 1.371% | 22.618 | 0.245% | 149.1369 | 1.616% | 2040 | 9207.382 | 9080.8631 | 1.393% | 0.2491%
2017-05-22 | 15 | 9238 | 126.6126 | 1.371% | 22.6329 | 0.245% | 149.2455 | 1.616% | 2041 | 9215.3671 | 9088.7545 | 1.393% | 0.249%
2017-03-06 | 7 | 9244 | 126.6829 | 1.37% | 22.6441 | 0.245% | 149.327 | 1.615% | 2042 | 9221.3559 | 9094.673 | 1.393% | 0.249%
2017-03-12 | 13 | 9248 | 126.7297 | 1.37% | 22.6515 | 0.2449% | 149.3813 | 1.615% | 2043 | 9225.3485 | 9098.6187 | 1.393% | 0.249%
2017-03-16 | 22 | 9248 | 126.7297 | 1.37% | 22.6515 | 0.2449% | 149.3813 | 1.615% | 2044 | 9225.3485 | 9098.6187 | 1.393% | 0.249%
2017-05-27 | 20 | 9248 | 126.7297 | 1.37% | 22.6515 | 0.2449% | 149.3813 | 1.615% | 2045 | 9225.3485 | 9098.6187 | 1.393% | 0.249%
2017-04-21 | 17 | 9253 | 126.7883 | 1.37% | 22.6609 | 0.2449% | 149.4491 | 1.615% | 2046 | 9230.3391 | 9103.5509 | 1.393% | 0.2489%
2017-03-15 | 15 | 9262 | 126.8937 | 1.37% | 22.6777 | 0.2448% | 149.5713 | 1.615% | 2047 | 9239.3223 | 9112.4287 | 1.393% | 0.2489%
2017-05-16 | 14 | 9263 | 126.9054 | 1.37% | 22.6795 | 0.2448% | 149.5849 | 1.615% | 2048 | 9240.3205 | 9113.4151 | 1.393% | 0.2489%
2017-03-12 | 12 | 9271 | 126.999 | 1.37% | 22.6944 | 0.2448% | 149.6935 | 1.615% | 2049 | 9248.3056 | 9121.3065 | 1.392% | 0.2488%
2017-03-17 | 11 | 9276 | 127.0576 | 1.37% | 22.7038 | 0.2448% | 149.7613 | 1.615% | 2050 | 9253.2962 | 9126.2387 | 1.392% | 0.2488%
2017-05-29 | 13 | 9279 | 127.0927 | 1.37% | 22.7094 | 0.2447% | 149.8021 | 1.614% | 2051 | 9256.2906 | 9129.1979 | 1.392% | 0.2488%
2017-05-15 | 16 | 9280 | 127.1044 | 1.37% | 22.7112 | 0.2447% | 149.8156 | 1.614% | 2052 | 9257.2888 | 9130.1844 | 1.392% | 0.2487%
2017-03-13 | 21 | 9281 | 127.1161 | 1.37% | 22.7131 | 0.2447% | 149.8292 | 1.614% | 2053 | 9258.2869 | 9131.1708 | 1.392% | 0.2487%
2017-05-27 | 15 | 9281 | 127.1161 | 1.37% | 22.7131 | 0.2447% | 149.8292 | 1.614% | 2054 | 9258.2869 | 9131.1708 | 1.392% | 0.2487%
2017-04-28 | 14 | 9286 | 127.1747 | 1.37% | 22.7224 | 0.2447% | 149.8971 | 1.614% | 2055 | 9263.2776 | 9136.1029 | 1.392% | 0.2487%
2017-04-30 | 18 | 9307 | 127.4206 | 1.369% | 22.7616 | 0.2446% | 150.1821 | 1.614% | 2056 | 9284.2384 | 9156.8179 | 1.392% | 0.2486%
2017-03-06 | 8 | 9311 | 127.4674 | 1.369% | 22.7691 | 0.2445% | 150.2364 | 1.614% | 2057 | 9288.2309 | 9160.7636 | 1.391% | 0.2485%
2017-05-01 | 16 | 9317 | 127.5376 | 1.369% | 22.7803 | 0.2445% | 150.3179 | 1.613% | 2058 | 9294.2197 | 9166.6821 | 1.391% | 0.2485%
2017-05-11 | 19 | 9317 | 127.5376 | 1.369% | 22.7803 | 0.2445% | 150.3179 | 1.613% | 2059 | 9294.2197 | 9166.6821 | 1.391% | 0.2485%
2017-04-30 | 17 | 9318 | 127.5494 | 1.369% | 22.7821 | 0.2445% | 150.3315 | 1.613% | 2060 | 9295.2179 | 9167.6685 | 1.391% | 0.2485%
2017-05-17 | 13 | 9320 | 127.5728 | 1.369% | 22.7858 | 0.2445% | 150.3586 | 1.613% | 2061 | 9297.2142 | 9169.6414 | 1.391% | 0.2485%
2017-03-23 | 8 | 9321 | 127.5845 | 1.369% | 22.7877 | 0.2445% | 150.3722 | 1.613% | 2062 | 9298.2123 | 9170.6278 | 1.391% | 0.2485%
2017-04-29 | 20 | 9331 | 127.7016 | 1.369% | 22.8064 | 0.2444% | 150.5079 | 1.613% | 2063 | 9308.1936 | 9180.4921 | 1.391% | 0.2484%
2017-04-28 | 20 | 9332 | 127.7133 | 1.369% | 22.8082 | 0.2444% | 150.5215 | 1.613% | 2064 | 9309.1918 | 9181.4785 | 1.391% | 0.2484%
2017-03-16 | 21 | 9333 | 127.725 | 1.369% | 22.8101 | 0.2444% | 150.5351 | 1.613% | 2065 | 9310.1899 | 9182.4649 | 1.391% | 0.2484%
2017-03-14 | 11 | 9337 | 127.7718 | 1.368% | 22.8176 | 0.2444% | 150.5894 | 1.613% | 2066 | 9314.1824 | 9186.4106 | 1.391% | 0.2484%
2017-05-01 | 18 | 9356 | 127.9943 | 1.368% | 22.853 | 0.2443% | 150.8473 | 1.612% | 2067 | 9333.147 | 9205.1527 | 1.39% | 0.2483%
2017-03-23 | 9 | 9361 | 128.0528 | 1.368% | 22.8623 | 0.2442% | 150.9152 | 1.612% | 2068 | 9338.1377 | 9210.0848 | 1.39% | 0.2482%
2017-03-24 | 8 | 9367 | 128.1231 | 1.368% | 22.8735 | 0.2442% | 150.9966 | 1.612% | 2069 | 9344.1265 | 9216.0034 | 1.39% | 0.2482%
2017-05-30 | 14 | 9392 | 128.4158 | 1.367% | 22.9202 | 0.244% | 151.336 | 1.611% | 2070 | 9369.0798 | 9240.664 | 1.39% | 0.248%
2017-05-30 | 21 | 9392 | 128.4158 | 1.367% | 22.9202 | 0.244% | 151.336 | 1.611% | 2071 | 9369.0798 | 9240.664 | 1.39% | 0.248%
2017-05-19 | 13 | 9394 | 128.4392 | 1.367% | 22.9239 | 0.244% | 151.3631 | 1.611% | 2072 | 9371.0761 | 9242.6369 | 1.39% | 0.248%
2017-03-13 | 20 | 9397 | 128.4744 | 1.367% | 22.9295 | 0.244% | 151.4038 | 1.611% | 2073 | 9374.0705 | 9245.5962 | 1.39% | 0.248%
2017-03-13 | 12 | 9404 | 128.5563 | 1.367% | 22.9425 | 0.244% | 151.4989 | 1.611% | 2074 | 9381.0575 | 9252.5011 | 1.389% | 0.248%
2017-03-16 | 2 | 9405 | 128.568 | 1.367% | 22.9444 | 0.244% | 151.5124 | 1.611% | 2075 | 9382.0556 | 9253.4876 | 1.389% | 0.248%
2017-05-31 | 14 | 9407 | 128.5914 | 1.367% | 22.9481 | 0.2439% | 151.5396 | 1.611% | 2076 | 9384.0519 | 9255.4604 | 1.389% | 0.2479%
2017-04-28 | 15 | 9414 | 128.6734 | 1.367% | 22.9612 | 0.2439% | 151.6346 | 1.611% | 2077 | 9391.0388 | 9262.3654 | 1.389% | 0.2479%
2017-05-22 | 18 | 9415 | 128.6851 | 1.367% | 22.9631 | 0.2439% | 151.6482 | 1.611% | 2078 | 9392.0369 | 9263.3518 | 1.389% | 0.2479%
2017-05-20 | 13 | 9418 | 128.7202 | 1.367% | 22.9687 | 0.2439% | 151.6889 | 1.611% | 2079 | 9395.0313 | 9266.3111 | 1.389% | 0.2479%
2017-05-31 | 19 | 9428 | 128.8373 | 1.367% | 22.9873 | 0.2438% | 151.8246 | 1.61% | 2080 | 9405.0127 | 9276.1754 | 1.389% | 0.2478%
2017-05-01 | 17 | 9431 | 128.8725 | 1.366% | 22.9929 | 0.2438% | 151.8654 | 1.61% | 2081 | 9408.0071 | 9279.1346 | 1.389% | 0.2478%
2017-04-29 | 14 | 9439 | 128.9661 | 1.366% | 23.0078 | 0.2438% | 151.974 | 1.61% | 2082 | 9415.9922 | 9287.026 | 1.389% | 0.2477%
2017-05-11 | 17 | 9448 | 129.0715 | 1.366% | 23.0246 | 0.2437% | 152.0961 | 1.61% | 2083 | 9424.9754 | 9295.9039 | 1.388% | 0.2477%
2017-03-14 | 10 | 9458 | 129.1886 | 1.366% | 23.0433 | 0.2436% | 152.2319 | 1.61% | 2084 | 9434.9567 | 9305.7681 | 1.388% | 0.2476%
2017-05-20 | 21 | 9464 | 129.2589 | 1.366% | 23.0545 | 0.2436% | 152.3133 | 1.609% | 2085 | 9440.9455 | 9311.6867 | 1.388% | 0.2476%
2017-05-11 | 18 | 9468 | 129.3057 | 1.366% | 23.0619 | 0.2436% | 152.3676 | 1.609% | 2086 | 9444.9381 | 9315.6324 | 1.388% | 0.2476%
2017-05-15 | 17 | 9489 | 129.5516 | 1.365% | 23.1011 | 0.2435% | 152.6527 | 1.609% | 2087 | 9465.8989 | 9336.3473 | 1.388% | 0.2474%
2017-05-22 | 16 | 9505 | 129.7389 | 1.365% | 23.1309 | 0.2434% | 152.8699 | 1.608% | 2088 | 9481.8691 | 9352.1301 | 1.387% | 0.2473%
2017-05-18 | 21 | 9508 | 129.7741 | 1.365% | 23.1365 | 0.2433% | 152.9106 | 1.608% | 2089 | 9484.8635 | 9355.0894 | 1.387% | 0.2473%
2017-05-29 | 21 | 9513 | 129.8326 | 1.365% | 23.1459 | 0.2433% | 152.9785 | 1.608% | 2090 | 9489.8541 | 9360.0215 | 1.387% | 0.2473%
2017-03-13 | 6 | 9515 | 129.856 | 1.365% | 23.1496 | 0.2433% | 153.0056 | 1.608% | 2091 | 9491.8504 | 9361.9944 | 1.387% | 0.2473%
2017-03-16 | 1 | 9529 | 130.0199 | 1.364% | 23.1757 | 0.2432% | 153.1957 | 1.608% | 2092 | 9505.8243 | 9375.8043 | 1.387% | 0.2472%
2017-05-28 | 19 | 9531 | 130.0434 | 1.364% | 23.1794 | 0.2432% | 153.2228 | 1.608% | 2093 | 9507.8206 | 9377.7772 | 1.387% | 0.2472%
2017-05-28 | 15 | 9532 | 130.0551 | 1.364% | 23.1813 | 0.2432% | 153.2364 | 1.608% | 2094 | 9508.8187 | 9378.7636 | 1.387% | 0.2472%
2017-03-16 | 3 | 9539 | 130.137 | 1.364% | 23.1944 | 0.2432% | 153.3314 | 1.607% | 2095 | 9515.8056 | 9385.6686 | 1.387% | 0.2471%
2017-05-15 | 19 | 9539 | 130.137 | 1.364% | 23.1944 | 0.2432% | 153.3314 | 1.607% | 2096 | 9515.8056 | 9385.6686 | 1.387% | 0.2471%
2017-03-15 | 14 | 9547 | 130.2307 | 1.364% | 23.2093 | 0.2431% | 153.44 | 1.607% | 2097 | 9523.7907 | 9393.56 | 1.386% | 0.2471%
2017-03-17 | 5 | 9551 | 130.2775 | 1.364% | 23.2168 | 0.2431% | 153.4943 | 1.607% | 2098 | 9527.7832 | 9397.5057 | 1.386% | 0.2471%
2017-05-16 | 21 | 9557 | 130.3478 | 1.364% | 23.2279 | 0.243% | 153.5757 | 1.607% | 2099 | 9533.7721 | 9403.4243 | 1.386% | 0.247%
2017-05-18 | 14 | 9563 | 130.418 | 1.364% | 23.2391 | 0.243% | 153.6572 | 1.607% | 2100 | 9539.7609 | 9409.3428 | 1.386% | 0.247%
2017-03-14 | 9 | 9568 | 130.4766 | 1.364% | 23.2485 | 0.243% | 153.7251 | 1.607% | 2101 | 9544.7515 | 9414.2749 | 1.386% | 0.2469%
2017-05-19 | 20 | 9572 | 130.5234 | 1.364% | 23.2559 | 0.243% | 153.7794 | 1.607% | 2102 | 9548.7441 | 9418.2206 | 1.386% | 0.2469%
2017-04-29 | 19 | 9578 | 130.5937 | 1.363% | 23.2671 | 0.2429% | 153.8608 | 1.606% | 2103 | 9554.7329 | 9424.1392 | 1.386% | 0.2469%
2017-05-22 | 17 | 9584 | 130.6639 | 1.363% | 23.2783 | 0.2429% | 153.9423 | 1.606% | 2104 | 9560.7217 | 9430.0577 | 1.386% | 0.2469%
2017-03-16 | 12 | 9599 | 130.8396 | 1.363% | 23.3063 | 0.2428% | 154.1459 | 1.606% | 2105 | 9575.6937 | 9444.8541 | 1.385% | 0.2468%
2017-05-27 | 16 | 9605 | 130.9098 | 1.363% | 23.3175 | 0.2428% | 154.2273 | 1.606% | 2106 | 9581.6825 | 9450.7727 | 1.385% | 0.2467%
2017-03-16 | 4 | 9611 | 130.9801 | 1.363% | 23.3287 | 0.2427% | 154.3088 | 1.606% | 2107 | 9587.6713 | 9456.6912 | 1.385% | 0.2467%
2017-04-28 | 19 | 9612 | 130.9918 | 1.363% | 23.3305 | 0.2427% | 154.3223 | 1.606% | 2108 | 9588.6695 | 9457.6777 | 1.385% | 0.2467%
2017-05-15 | 18 | 9615 | 131.0269 | 1.363% | 23.3361 | 0.2427% | 154.3631 | 1.605% | 2109 | 9591.6639 | 9460.6369 | 1.385% | 0.2467%
2017-03-15 | 5 | 9625 | 131.144 | 1.363% | 23.3548 | 0.2426% | 154.4988 | 1.605% | 2110 | 9601.6452 | 9470.5012 | 1.385% | 0.2466%
2017-04-28 | 16 | 9634 | 131.2494 | 1.362% | 23.3716 | 0.2426% | 154.621 | 1.605% | 2111 | 9610.6284 | 9479.379 | 1.385% | 0.2466%
2017-05-31 | 15 | 9646 | 131.3899 | 1.362% | 23.394 | 0.2425% | 154.7839 | 1.605% | 2112 | 9622.606 | 9491.2161 | 1.384% | 0.2465%
2017-05-30 | 20 | 9652 | 131.4601 | 1.362% | 23.4052 | 0.2425% | 154.8653 | 1.604% | 2113 | 9628.5948 | 9497.1347 | 1.384% | 0.2464%
2017-05-16 | 15 | 9653 | 131.4719 | 1.362% | 23.407 | 0.2425% | 154.8789 | 1.604% | 2114 | 9629.593 | 9498.1211 | 1.384% | 0.2464%
2017-05-29 | 14 | 9658 | 131.5304 | 1.362% | 23.4164 | 0.2425% | 154.9468 | 1.604% | 2115 | 9634.5836 | 9503.0532 | 1.384% | 0.2464%
2017-05-31 | 18 | 9668 | 131.6475 | 1.362% | 23.435 | 0.2424% | 155.0825 | 1.604% | 2116 | 9644.565 | 9512.9175 | 1.384% | 0.2463%
2017-03-15 | 20 | 9673 | 131.706 | 1.362% | 23.4443 | 0.2424% | 155.1504 | 1.604% | 2117 | 9649.5557 | 9517.8496 | 1.384% | 0.2463%
2017-05-27 | 19 | 9677 | 131.7529 | 1.362% | 23.4518 | 0.2423% | 155.2047 | 1.604% | 2118 | 9653.5482 | 9521.7953 | 1.384% | 0.2463%
2017-05-28 | 16 | 9709 | 132.1276 | 1.361% | 23.5115 | 0.2422% | 155.639 | 1.603% | 2119 | 9685.4885 | 9553.361 | 1.383% | 0.2461%
2017-05-30 | 15 | 9714 | 132.1861 | 1.361% | 23.5208 | 0.2421% | 155.7069 | 1.603% | 2120 | 9690.4792 | 9558.2931 | 1.383% | 0.2461%
2017-05-31 | 17 | 9714 | 132.1861 | 1.361% | 23.5208 | 0.2421% | 155.7069 | 1.603% | 2121 | 9690.4792 | 9558.2931 | 1.383% | 0.2461%
2017-04-29 | 18 | 9720 | 132.2564 | 1.361% | 23.532 | 0.2421% | 155.7884 | 1.603% | 2122 | 9696.468 | 9564.2116 | 1.383% | 0.246%
2017-05-17 | 21 | 9725 | 132.3149 | 1.361% | 23.5413 | 0.2421% | 155.8562 | 1.603% | 2123 | 9701.4587 | 9569.1438 | 1.383% | 0.246%
2017-03-15 | 24 | 9726 | 132.3266 | 1.361% | 23.5432 | 0.2421% | 155.8698 | 1.603% | 2124 | 9702.4568 | 9570.1302 | 1.383% | 0.246%
2017-05-29 | 20 | 9732 | 132.3969 | 1.36% | 23.5544 | 0.242% | 155.9513 | 1.602% | 2125 | 9708.4456 | 9576.0487 | 1.383% | 0.246%
2017-03-14 | 8 | 9737 | 132.4554 | 1.36% | 23.5637 | 0.242% | 156.0191 | 1.602% | 2126 | 9713.4363 | 9580.9809 | 1.382% | 0.2459%
2017-05-31 | 16 | 9743 | 132.5257 | 1.36% | 23.5749 | 0.242% | 156.1006 | 1.602% | 2127 | 9719.4251 | 9586.8994 | 1.382% | 0.2459%
2017-04-28 | 17 | 9754 | 132.6545 | 1.36% | 23.5954 | 0.2419% | 156.2499 | 1.602% | 2128 | 9730.4046 | 9597.7501 | 1.382% | 0.2458%
2017-04-28 | 18 | 9759 | 132.713 | 1.36% | 23.6048 | 0.2419% | 156.3178 | 1.602% | 2129 | 9735.3952 | 9602.6822 | 1.382% | 0.2458%
2017-05-28 | 18 | 9768 | 132.8184 | 1.36% | 23.6216 | 0.2418% | 156.4399 | 1.602% | 2130 | 9744.3784 | 9611.5601 | 1.382% | 0.2458%
2017-04-29 | 15 | 9774 | 132.8886 | 1.36% | 23.6327 | 0.2418% | 156.5214 | 1.601% | 2131 | 9750.3673 | 9617.4786 | 1.382% | 0.2457%
2017-05-18 | 20 | 9781 | 132.9706 | 1.359% | 23.6458 | 0.2418% | 156.6164 | 1.601% | 2132 | 9757.3542 | 9624.3836 | 1.382% | 0.2457%
2017-05-27 | 17 | 9798 | 133.1697 | 1.359% | 23.6775 | 0.2417% | 156.8472 | 1.601% | 2133 | 9774.3225 | 9641.1528 | 1.381% | 0.2456%
2017-03-20 | 7 | 9832 | 133.5678 | 1.359% | 23.7409 | 0.2415% | 157.3087 | 1.6% | 2134 | 9808.2591 | 9674.6913 | 1.381% | 0.2454%
2017-04-29 | 17 | 9833 | 133.5795 | 1.358% | 23.7428 | 0.2415% | 157.3223 | 1.6% | 2135 | 9809.2572 | 9675.6777 | 1.381% | 0.2454%
2017-05-17 | 14 | 9841 | 133.6731 | 1.358% | 23.7577 | 0.2414% | 157.4309 | 1.6% | 2136 | 9817.2423 | 9683.5691 | 1.38% | 0.2453%
2017-04-29 | 16 | 9851 | 133.7902 | 1.358% | 23.7764 | 0.2414% | 157.5666 | 1.599% | 2137 | 9827.2236 | 9693.4334 | 1.38% | 0.2453%
2017-05-28 | 17 | 9852 | 133.8019 | 1.358% | 23.7782 | 0.2414% | 157.5802 | 1.599% | 2138 | 9828.2218 | 9694.4198 | 1.38% | 0.2453%
2017-05-16 | 16 | 9861 | 133.9073 | 1.358% | 23.795 | 0.2413% | 157.7024 | 1.599% | 2139 | 9837.205 | 9703.2976 | 1.38% | 0.2452%
2017-05-19 | 14 | 9862 | 133.919 | 1.358% | 23.7969 | 0.2413% | 157.7159 | 1.599% | 2140 | 9838.2031 | 9704.2841 | 1.38% | 0.2452%
2017-03-20 | 9 | 9863 | 133.9307 | 1.358% | 23.7988 | 0.2413% | 157.7295 | 1.599% | 2141 | 9839.2012 | 9705.2705 | 1.38% | 0.2452%
2017-05-27 | 18 | 9864 | 133.9424 | 1.358% | 23.8006 | 0.2413% | 157.7431 | 1.599% | 2142 | 9840.1994 | 9706.2569 | 1.38% | 0.2452%
2017-05-20 | 20 | 9875 | 134.0712 | 1.358% | 23.8212 | 0.2412% | 157.8924 | 1.599% | 2143 | 9851.1788 | 9717.1076 | 1.38% | 0.2451%
2017-03-15 | 13 | 9895 | 134.3054 | 1.357% | 23.8585 | 0.2411% | 158.1639 | 1.598% | 2144 | 9871.1415 | 9736.8361 | 1.379% | 0.245%
2017-05-16 | 20 | 9910 | 134.4811 | 1.357% | 23.8864 | 0.241% | 158.3675 | 1.598% | 2145 | 9886.1136 | 9751.6325 | 1.379% | 0.2449%
2017-05-30 | 16 | 9930 | 134.7152 | 1.357% | 23.9237 | 0.2409% | 158.639 | 1.598% | 2146 | 9906.0763 | 9771.361 | 1.379% | 0.2448%
2017-05-30 | 19 | 9940 | 134.8323 | 1.356% | 23.9424 | 0.2409% | 158.7747 | 1.597% | 2147 | 9916.0576 | 9781.2253 | 1.378% | 0.2448%
2017-05-20 | 14 | 9963 | 135.1016 | 1.356% | 23.9853 | 0.2407% | 159.0869 | 1.597% | 2148 | 9939.0147 | 9803.9131 | 1.378% | 0.2447%
2017-05-29 | 15 | 9967 | 135.1485 | 1.356% | 23.9928 | 0.2407% | 159.1412 | 1.597% | 2149 | 9943.0072 | 9807.8588 | 1.378% | 0.2446%
2017-03-15 | 6 | 9985 | 135.3592 | 1.356% | 24.0263 | 0.2406% | 159.3856 | 1.596% | 2150 | 9960.9737 | 9825.6144 | 1.378% | 0.2445%
2017-03-15 | 23 | 9985 | 135.3592 | 1.356% | 24.0263 | 0.2406% | 159.3856 | 1.596% | 2151 | 9960.9737 | 9825.6144 | 1.378% | 0.2445%
2017-03-13 | 7 | 9989 | 135.4061 | 1.356% | 24.0338 | 0.2406% | 159.4399 | 1.596% | 2152 | 9964.9662 | 9829.5601 | 1.378% | 0.2445%
2017-05-18 | 15 | 10003 | 135.57 | 1.355% | 24.0599 | 0.2405% | 159.6299 | 1.596% | 2153 | 9978.9401 | 9843.3701 | 1.377% | 0.2444%
2017-03-16 | 5 | 10036 | 135.9564 | 1.355% | 24.1215 | 0.2403% | 160.0779 | 1.595% | 2154 | 10011.8785 | 9875.9221 | 1.377% | 0.2442%
2017-05-30 | 18 | 10082 | 136.495 | 1.354% | 24.2073 | 0.2401% | 160.7023 | 1.594% | 2155 | 10057.7927 | 9921.2977 | 1.376% | 0.244%
2017-05-30 | 17 | 10091 | 136.6004 | 1.354% | 24.2241 | 0.2401% | 160.8245 | 1.594% | 2156 | 10066.7759 | 9930.1755 | 1.376% | 0.2439%
2017-05-19 | 15 | 10113 | 136.858 | 1.353% | 24.2651 | 0.2399% | 161.1231 | 1.593% | 2157 | 10088.7349 | 9951.8769 | 1.375% | 0.2438%
2017-05-29 | 19 | 10130 | 137.057 | 1.353% | 24.2968 | 0.2399% | 161.3539 | 1.593% | 2158 | 10105.7032 | 9968.6461 | 1.375% | 0.2437%
2017-05-19 | 19 | 10146 | 137.2444 | 1.353% | 24.3267 | 0.2398% | 161.571 | 1.592% | 2159 | 10121.6733 | 9984.429 | 1.375% | 0.2436%
2017-05-16 | 17 | 10153 | 137.3263 | 1.353% | 24.3397 | 0.2397% | 161.6661 | 1.592% | 2160 | 10128.6603 | 9991.3339 | 1.374% | 0.2436%
2017-05-16 | 19 | 10158 | 137.3849 | 1.352% | 24.3491 | 0.2397% | 161.7339 | 1.592% | 2161 | 10133.6509 | 9996.2661 | 1.374% | 0.2436%
2017-05-17 | 20 | 10161 | 137.42 | 1.352% | 24.3547 | 0.2397% | 161.7747 | 1.592% | 2162 | 10136.6453 | 9999.2253 | 1.374% | 0.2436%
2017-05-16 | 18 | 10174 | 137.5722 | 1.352% | 24.3789 | 0.2396% | 161.9511 | 1.592% | 2163 | 10149.6211 | 10012.0489 | 1.374% | 0.2435%
2017-03-17 | 10 | 10186 | 137.7127 | 1.352% | 24.4013 | 0.2396% | 162.114 | 1.592% | 2164 | 10161.5987 | 10023.886 | 1.374% | 0.2434%
2017-03-13 | 11 | 10210 | 137.9937 | 1.352% | 24.4461 | 0.2394% | 162.4398 | 1.591% | 2165 | 10185.5539 | 10047.5602 | 1.373% | 0.2433%
2017-03-15 | 21 | 10210 | 137.9937 | 1.352% | 24.4461 | 0.2394% | 162.4398 | 1.591% | 2166 | 10185.5539 | 10047.5602 | 1.373% | 0.2433%
2017-05-29 | 16 | 10220 | 138.1108 | 1.351% | 24.4647 | 0.2394% | 162.5755 | 1.591% | 2167 | 10195.5353 | 10057.4245 | 1.373% | 0.2433%
2017-05-29 | 17 | 10221 | 138.1225 | 1.351% | 24.4666 | 0.2394% | 162.5891 | 1.591% | 2168 | 10196.5334 | 10058.4109 | 1.373% | 0.2432%
2017-05-29 | 18 | 10225 | 138.1694 | 1.351% | 24.474 | 0.2394% | 162.6434 | 1.591% | 2169 | 10200.526 | 10062.3566 | 1.373% | 0.2432%
2017-05-17 | 15 | 10230 | 138.2279 | 1.351% | 24.4834 | 0.2393% | 162.7113 | 1.591% | 2170 | 10205.5166 | 10067.2887 | 1.373% | 0.2432%
2017-05-20 | 15 | 10248 | 138.4387 | 1.351% | 24.517 | 0.2392% | 162.9556 | 1.59% | 2171 | 10223.483 | 10085.0444 | 1.373% | 0.2431%
2017-05-18 | 19 | 10261 | 138.5909 | 1.351% | 24.5412 | 0.2392% | 163.1321 | 1.59% | 2172 | 10236.4588 | 10097.8679 | 1.372% | 0.243%
2017-05-20 | 19 | 10317 | 139.2466 | 1.35% | 24.6457 | 0.2389% | 163.8923 | 1.589% | 2173 | 10292.3543 | 10153.1077 | 1.371% | 0.2427%
2017-03-17 | 6 | 10319 | 139.27 | 1.35% | 24.6494 | 0.2389% | 163.9194 | 1.589% | 2174 | 10294.3506 | 10155.0806 | 1.371% | 0.2427%
2017-05-18 | 16 | 10336 | 139.4691 | 1.349% | 24.6811 | 0.2388% | 164.1502 | 1.588% | 2175 | 10311.3189 | 10171.8498 | 1.371% | 0.2426%
2017-03-20 | 8 | 10394 | 140.1482 | 1.348% | 24.7893 | 0.2385% | 164.9375 | 1.587% | 2176 | 10369.2107 | 10229.0625 | 1.37% | 0.2423%
2017-05-20 | 16 | 10432 | 140.5931 | 1.348% | 24.8602 | 0.2383% | 165.4533 | 1.586% | 2177 | 10407.1398 | 10266.5467 | 1.369% | 0.2421%
2017-03-16 | 6 | 10440 | 140.6868 | 1.348% | 24.8751 | 0.2383% | 165.5619 | 1.586% | 2178 | 10415.1249 | 10274.4381 | 1.369% | 0.2421%
2017-03-15 | 22 | 10453 | 140.839 | 1.347% | 24.8994 | 0.2382% | 165.7384 | 1.586% | 2179 | 10428.1006 | 10287.2616 | 1.369% | 0.242%
2017-05-18 | 17 | 10453 | 140.839 | 1.347% | 24.8994 | 0.2382% | 165.7384 | 1.586% | 2180 | 10428.1006 | 10287.2616 | 1.369% | 0.242%
2017-05-18 | 18 | 10459 | 140.9093 | 1.347% | 24.9106 | 0.2382% | 165.8198 | 1.585% | 2181 | 10434.0894 | 10293.1802 | 1.369% | 0.242%
2017-03-13 | 10 | 10461 | 140.9327 | 1.347% | 24.9143 | 0.2382% | 165.847 | 1.585% | 2182 | 10436.0857 | 10295.153 | 1.369% | 0.242%
2017-05-19 | 18 | 10463 | 140.9561 | 1.347% | 24.918 | 0.2382% | 165.8741 | 1.585% | 2183 | 10438.082 | 10297.1259 | 1.369% | 0.242%
2017-05-20 | 17 | 10474 | 141.0849 | 1.347% | 24.9385 | 0.2381% | 166.0234 | 1.585% | 2184 | 10449.0615 | 10307.9766 | 1.369% | 0.2419%
2017-03-16 | 11 | 10501 | 141.401 | 1.347% | 24.9889 | 0.238% | 166.3899 | 1.585% | 2185 | 10476.0111 | 10334.6101 | 1.368% | 0.2418%
2017-05-17 | 16 | 10503 | 141.4245 | 1.347% | 24.9926 | 0.238% | 166.4171 | 1.584% | 2186 | 10478.0074 | 10336.5829 | 1.368% | 0.2418%
2017-03-15 | 12 | 10509 | 141.4947 | 1.346% | 25.0038 | 0.2379% | 166.4985 | 1.584% | 2187 | 10483.9962 | 10342.5015 | 1.368% | 0.2418%
2017-05-20 | 18 | 10509 | 141.4947 | 1.346% | 25.0038 | 0.2379% | 166.4985 | 1.584% | 2188 | 10483.9962 | 10342.5015 | 1.368% | 0.2418%
2017-05-19 | 16 | 10537 | 141.8226 | 1.346% | 25.0561 | 0.2378% | 166.8786 | 1.584% | 2189 | 10511.9439 | 10370.1214 | 1.368% | 0.2416%
2017-05-17 | 19 | 10565 | 142.1504 | 1.345% | 25.1083 | 0.2377% | 167.2587 | 1.583% | 2190 | 10539.8917 | 10397.7413 | 1.367% | 0.2415%
2017-05-19 | 17 | 10567 | 142.1738 | 1.345% | 25.112 | 0.2376% | 167.2859 | 1.583% | 2191 | 10541.888 | 10399.7141 | 1.367% | 0.2415%
2017-05-17 | 17 | 10660 | 143.2628 | 1.344% | 25.2855 | 0.2372% | 168.5483 | 1.581% | 2192 | 10634.7145 | 10491.4517 | 1.366% | 0.241%
2017-05-17 | 18 | 10685 | 143.5555 | 1.344% | 25.3321 | 0.2371% | 168.8876 | 1.581% | 2193 | 10659.6679 | 10516.1124 | 1.365% | 0.2409%
2017-03-13 | 8 | 10721 | 143.977 | 1.343% | 25.3993 | 0.2369% | 169.3763 | 1.58% | 2194 | 10695.6007 | 10551.6237 | 1.365% | 0.2407%
2017-03-13 | 9 | 10754 | 144.3634 | 1.342% | 25.4609 | 0.2368% | 169.8243 | 1.579% | 2195 | 10728.5391 | 10584.1757 | 1.364% | 0.2406% | 10770.4071
2017-03-16 | 10 | 10965 | 147.3666 | 1.344% | 25.9626 | 0.2368% | 173.3291 | 1.581% | 2196 | 10939.0374 | 10791.6709 | 1.366% | 0.2406%
2017-03-15 | 7 | 10990 | 147.7275 | 1.344% | 26.023 | 0.2368% | 173.7506 | 1.581% | 2197 | 10963.977 | 10816.2494 | 1.366% | 0.2406%
2017-03-17 | 7 | 10990 | 147.7275 | 1.344% | 26.023 | 0.2368% | 173.7506 | 1.581% | 2198 | 10963.977 | 10816.2494 | 1.366% | 0.2406%
2017-03-15 | 11 | 11460 | 154.5135 | 1.348% | 27.1602 | 0.237% | 181.6737 | 1.585% | 2199 | 11432.8398 | 11278.3263 | 1.37% | 0.2408%
2017-03-17 | 9 | 11463 | 154.5568 | 1.348% | 27.1674 | 0.237% | 181.7242 | 1.585% | 2200 | 11435.8326 | 11281.2758 | 1.37% | 0.2408%
2017-03-16 | 7 | 11509 | 155.221 | 1.349% | 27.2787 | 0.237% | 182.4997 | 1.586% | 2201 | 11481.7213 | 11326.5003 | 1.37% | 0.2408%
2017-03-15 | 10 | 11587 | 156.3472 | 1.349% | 27.4674 | 0.2371% | 183.8146 | 1.586% | 2202 | 11559.5326 | 11403.1854 | 1.371% | 0.2409%
2017-03-15 | 9 | 11754 | 158.7584 | 1.351% | 27.8715 | 0.2371% | 186.6298 | 1.588% | 2203 | 11726.1285 | 11567.3702 | 1.372% | 0.2409%
2017-03-16 | 9 | 11787 | 159.2348 | 1.351% | 27.9513 | 0.2371% | 187.1861 | 1.588% | 2204 | 11759.0487 | 11599.8139 | 1.373% | 0.241%
2017-03-17 | 8 | 11829 | 159.8412 | 1.351% | 28.0529 | 0.2372% | 187.8942 | 1.588% | 2205 | 11800.9471 | 11641.1058 | 1.373% | 0.241%
2017-03-15 | 8 | 11937 | 161.4006 | 1.352% | 28.3142 | 0.2372% | 189.7148 | 1.589% | 2206 | 11908.6858 | 11747.2852 | 1.374% | 0.241% | 11952.7416
2017-03-16 | 8 | 12024 | 162.6567 | 1.353% | 28.5247 | 0.2372% | 191.1814 | 1.59% | 2207 | 11995.4753 | 11832.8186 | 1.375% | 0.2411%
|  | 15085108 | 240226.7997 | 1.592% | 39260.9061 | 0.2603% | 279487.7058 | 1.853% |  | 15045847.0939 | 14805620.2942 | 1.623% | 0.2652%
Note on C3: Quaintance, William Harford: Measured at generator energy meter
Note on C4: Quaintance, William Harford: Keep sorted by MW load, smallest to largest
Note on O4: Quaintance, William Harford: For blue diamonds in LEFT graph, copy each number from column R to this column where it matches column C.

## Losses from PSSE
|  | GSU + Transmission Losses |  |  |  | Transmission Losses Only |  |  |  | GSU Losses Only |  |  |  | CPLE & CPLW Load (MW)
PSSE Case Name | CPLE & CPLW PSSE Load(MW) | Line & Copper Losses (MW) | Core Losses (MW) | Line, Copper, & Core Losses (MW) | Line, Copper, & Core Losses (%) | Line & Copper Losses (MW) | Core Losses (MW) | Line, Copper, & Core Losses (MW) | Line, Copper, & Core Losses (%) | Copper Losses (MW) | Core Losses (MW) | Copper & Core Losses (MW) | Copper & Core Losses (%) | POD (PSSE) LOAD | GEN HIGH SIDE LOAD | GEN LOW SIDE LOAD
Hour_001_2017_03_26_02.sav | 4413.7403 | 71.6142 | 17.7516 | 89.3658 | 2.025% | 65.0334 | 10.8045 | 75.8379 | 1.718% | 6.5808 | 6.9471 | 13.5279 | 0.3065% | 4413.7403 | 4489.5782 | 4503.1061
Hour_001_2017_05_13_07.sav | 5447.5184 | 102.4426 | 17.7516 | 120.1942 | 2.206% | 94.3369 | 10.8045 | 105.1413 | 1.93% | 8.1057 | 6.9471 | 15.0529 | 0.2763% | 5447.5184 | 5552.6597 | 5567.7126
Hour_001_2017_05_17_09.sav | 8104.8019 | 117.9536 | 17.7516 | 135.7052 | 1.674% | 104.1286 | 10.8045 | 114.933 | 1.418% | 13.825 | 6.9471 | 20.7721 | 0.2563% | 8104.8019 | 8219.735 | 8240.5071
Hour_001_2017_03_13_07.sav | 10599.828 | 152.288 | 17.7516 | 170.0397 | 1.604% | 133.7447 | 10.8045 | 144.5492 | 1.364% | 18.5433 | 6.9471 | 25.4905 | 0.2405% | 10599.828 | 10744.3772 | 10769.8677
Hour_001_2017_03_15_06.sav | 11762.5009 | 172.2241 | 17.7516 | 189.9757 | 1.615% | 150.8195 | 10.8045 | 161.624 | 1.374% | 21.4045 | 6.9471 | 28.3517 | 0.241% | 11762.5009 | 11924.1249 | 11952.4766
From power flow model
From core losses sheet
Calculated values |  |  |  | Note: PSSE Loads are equivalent to POD loads
Note on Q3: Quaintance, William Harford: Represents POD load plus transmission losses
Note on R3: Quaintance, William Harford: Represents POD load plus transmission and GSU losses, equivalent to BA load from control center

## Core Losses
| From: | LS FeLossDoc2018 03-26-18.xlsx
MW
6.9471 | GSU Core Losses
10.8045 | T-T Core Losses
17.7516 | Total