## Final Loss Calculation
Summer Only |  |  | 276115.8536 |  | 44146.3064 | [5 empty] | 18627291.84 | 1.482% | 0.237%
[12 empty] | Transmission | GSU
|  | Control | T-only | T-only | GSU-only | GSU-only | GSU+T | GSU+T |  | GSU |  | Losses | Losses |  |  | GSU | T-only | T-only | GSU-only | GSU-only
|  | Area | Losses | Losses | Losses | Losses | Losses | Losses |  | High Side | POD | vs | vs | Model |  | Low Side | Losses | Losses | Losses | Losses
Date | Time | Load | (MW) | (%) | (MW) | (%) | (MW) | (%) | Hour # | Load (MW) | Load (MW) | POD Load | POD Load | Points | Hour # | Load(MW) | (MW) | Slope | (MW) | Slope
2017-06-09 | 4 | 4768 | 115.802 | 2.429% | 15.1341 | 0.3174% | 130.9361 | 2.746% | 1 | 4752.8659 | 4637.0639 | 2.497% | 0.3264% |  | 3 | 4841.9097 | 115.0414 | -0.010292 | 15.189 | 0.00074303
2017-06-09 | 3 | 4806 | 115.4109 | 2.401% | 15.1623 | 0.3155% | 130.5732 | 2.717% | 2 | 4790.8377 | 4675.4268 | 2.468% | 0.3243% |  | 180 | 5985.9077 | 103.2673 | 0.004257 | 16.039 | 0.00097316
2017-06-09 | 5 | 4826 | 115.2051 | 2.387% | 15.1772 | 0.3145% | 130.3823 | 2.702% | 3 | 4810.8228 | 4695.6177 | 2.453% | 0.3232% | 4841.4015 | 1200 | 8791.0133 | 115.2086 | 0.019417 | 18.7688 | 0.0029386
2017-06-08 | 4 | 4867 | 114.7831 | 2.358% | 15.2076 | 0.3125% | 129.9907 | 2.671% | 4 | 4851.7924 | 4737.0093 | 2.423% | 0.321% |  | 2045 | 11595.2189 | 169.6575 | -0.0032164 | 27.0093 | 0.0024399
2017-06-08 | 5 | 4902 | 114.4229 | 2.334% | 15.2336 | 0.3108% | 129.6565 | 2.645% | 5 | 4886.7664 | 4772.3435 | 2.398% | 0.3192% |  | 2204 | 12698.4753 | 166.109 |  | 29.7011
2017-06-08 | 3 | 4960 | 113.826 | 2.295% | 15.2767 | 0.308% | 129.1027 | 2.603% | 6 | 4944.7233 | 4830.8973 | 2.356% | 0.3162%
2017-06-10 | 5 | 4992 | 113.4966 | 2.274% | 15.3005 | 0.3065% | 128.7971 | 2.58% | 7 | 4976.6995 | 4863.2029 | 2.334% | 0.3146%
2017-06-09 | 2 | 5008 | 113.332 | 2.263% | 15.3124 | 0.3058% | 128.6443 | 2.569% | 8 | 4992.6876 | 4879.3557 | 2.323% | 0.3138%
2017-06-10 | 4 | 5043 | 112.9717 | 2.24% | 15.3384 | 0.3042% | 128.3101 | 2.544% | 9 | 5027.6616 | 4914.6899 | 2.299% | 0.3121%
2017-06-10 | 6 | 5050 | 112.8997 | 2.236% | 15.3436 | 0.3038% | 128.2433 | 2.539% | 10 | 5034.6564 | 4921.7567 | 2.294% | 0.3118%
2017-06-03 | 5 | 5070 | 112.6939 | 2.223% | 15.3584 | 0.3029% | 128.0523 | 2.526% | 11 | 5054.6416 | 4941.9477 | 2.28% | 0.3108%
2017-06-10 | 7 | 5076 | 112.6321 | 2.219% | 15.3629 | 0.3027% | 127.995 | 2.522% | 12 | 5060.6371 | 4948.005 | 2.276% | 0.3105%
2017-07-31 | 4 | 5099 | 112.3954 | 2.204% | 15.38 | 0.3016% | 127.7754 | 2.506% | 13 | 5083.62 | 4971.2246 | 2.261% | 0.3094%
2017-06-03 | 6 | 5108 | 112.3028 | 2.199% | 15.3867 | 0.3012% | 127.6894 | 2.5% | 14 | 5092.6133 | 4980.3106 | 2.255% | 0.309%
2017-06-04 | 7 | 5108 | 112.3028 | 2.199% | 15.3867 | 0.3012% | 127.6894 | 2.5% | 15 | 5092.6133 | 4980.3106 | 2.255% | 0.309%
2017-06-09 | 6 | 5116 | 112.2204 | 2.194% | 15.3926 | 0.3009% | 127.6131 | 2.494% | 16 | 5100.6074 | 4988.3869 | 2.25% | 0.3086%
2017-06-11 | 7 | 5122 | 112.1587 | 2.19% | 15.3971 | 0.3006% | 127.5558 | 2.49% | 17 | 5106.6029 | 4994.4442 | 2.246% | 0.3083%
2017-06-04 | 6 | 5139 | 111.9837 | 2.179% | 15.4097 | 0.2999% | 127.3934 | 2.479% | 18 | 5123.5903 | 5011.6066 | 2.234% | 0.3075%
2017-06-11 | 6 | 5141 | 111.9631 | 2.178% | 15.4112 | 0.2998% | 127.3743 | 2.478% | 19 | 5125.5888 | 5013.6257 | 2.233% | 0.3074%
2017-07-31 | 5 | 5141 | 111.9631 | 2.178% | 15.4112 | 0.2998% | 127.3743 | 2.478% | 20 | 5125.5888 | 5013.6257 | 2.233% | 0.3074%
2017-06-03 | 4 | 5149 | 111.8808 | 2.173% | 15.4171 | 0.2994% | 127.2979 | 2.472% | 21 | 5133.5829 | 5021.7021 | 2.228% | 0.307%
2017-06-08 | 2 | 5153 | 111.8396 | 2.17% | 15.4201 | 0.2992% | 127.2597 | 2.47% | 22 | 5137.5799 | 5025.7403 | 2.225% | 0.3068%
2017-06-04 | 5 | 5159 | 111.7779 | 2.167% | 15.4246 | 0.299% | 127.2024 | 2.466% | 23 | 5143.5754 | 5031.7976 | 2.221% | 0.3065%
2017-06-28 | 4 | 5164 | 111.7264 | 2.164% | 15.4283 | 0.2988% | 127.1547 | 2.462% | 24 | 5148.5717 | 5036.8453 | 2.218% | 0.3063%
2017-06-11 | 5 | 5177 | 111.5926 | 2.156% | 15.438 | 0.2982% | 127.0306 | 2.454% | 25 | 5161.562 | 5049.9694 | 2.21% | 0.3057%
2017-06-28 | 5 | 5179 | 111.572 | 2.154% | 15.4394 | 0.2981% | 127.0115 | 2.452% | 26 | 5163.5606 | 5051.9885 | 2.208% | 0.3056%
2017-06-03 | 7 | 5190 | 111.4588 | 2.148% | 15.4476 | 0.2976% | 126.9064 | 2.445% | 27 | 5174.5524 | 5063.0936 | 2.201% | 0.3051%
2017-06-10 | 3 | 5220 | 111.1501 | 2.129% | 15.4699 | 0.2964% | 126.62 | 2.426% | 28 | 5204.5301 | 5093.38 | 2.182% | 0.3037%
2017-06-08 | 6 | 5223 | 111.1192 | 2.127% | 15.4721 | 0.2962% | 126.5913 | 2.424% | 29 | 5207.5279 | 5096.4087 | 2.18% | 0.3036%
2017-08-28 | 4 | 5226 | 111.0883 | 2.126% | 15.4744 | 0.2961% | 126.5627 | 2.422% | 30 | 5210.5256 | 5099.4373 | 2.178% | 0.3035%
2017-06-29 | 4 | 5240 | 110.9442 | 2.117% | 15.4848 | 0.2955% | 126.429 | 2.413% | 31 | 5224.5152 | 5113.571 | 2.17% | 0.3028%
2017-07-31 | 3 | 5240 | 110.9442 | 2.117% | 15.4848 | 0.2955% | 126.429 | 2.413% | 32 | 5224.5152 | 5113.571 | 2.17% | 0.3028%
2017-06-29 | 5 | 5245 | 110.8928 | 2.114% | 15.4885 | 0.2953% | 126.3812 | 2.41% | 33 | 5229.5115 | 5118.6188 | 2.166% | 0.3026%
2017-08-30 | 4 | 5246 | 110.8825 | 2.114% | 15.4892 | 0.2953% | 126.3717 | 2.409% | 34 | 5230.5108 | 5119.6283 | 2.166% | 0.3025%
2017-07-30 | 7 | 5268 | 110.656 | 2.101% | 15.5056 | 0.2943% | 126.1616 | 2.395% | 35 | 5252.4944 | 5141.8384 | 2.152% | 0.3016%
2017-06-09 | 1 | 5272 | 110.6149 | 2.098% | 15.5085 | 0.2942% | 126.1234 | 2.392% | 36 | 5256.4915 | 5145.8766 | 2.15% | 0.3014%
2017-07-30 | 6 | 5275 | 110.584 | 2.096% | 15.5108 | 0.294% | 126.0948 | 2.39% | 37 | 5259.4892 | 5148.9052 | 2.148% | 0.3012%
2017-06-04 | 4 | 5288 | 110.4502 | 2.089% | 15.5204 | 0.2935% | 125.9706 | 2.382% | 38 | 5272.4796 | 5162.0294 | 2.14% | 0.3007%
2017-08-30 | 5 | 5308 | 110.2444 | 2.077% | 15.5353 | 0.2927% | 125.7797 | 2.37% | 39 | 5292.4647 | 5182.2203 | 2.127% | 0.2998%
2017-08-28 | 5 | 5309 | 110.2341 | 2.076% | 15.536 | 0.2926% | 125.7701 | 2.369% | 40 | 5293.464 | 5183.2299 | 2.127% | 0.2997%
2017-07-30 | 5 | 5310 | 110.2238 | 2.076% | 15.5368 | 0.2926% | 125.7606 | 2.368% | 41 | 5294.4632 | 5184.2394 | 2.126% | 0.2997%
2017-06-28 | 3 | 5319 | 110.1311 | 2.071% | 15.5435 | 0.2922% | 125.6746 | 2.363% | 42 | 5303.4565 | 5193.3254 | 2.121% | 0.2993%
2017-08-30 | 3 | 5324 | 110.0797 | 2.068% | 15.5472 | 0.292% | 125.6269 | 2.36% | 43 | 5308.4528 | 5198.3731 | 2.118% | 0.2991%
2017-06-11 | 4 | 5328 | 110.0385 | 2.065% | 15.5502 | 0.2919% | 125.5887 | 2.357% | 44 | 5312.4498 | 5202.4113 | 2.115% | 0.2989%
2017-08-28 | 3 | 5328 | 110.0385 | 2.065% | 15.5502 | 0.2919% | 125.5887 | 2.357% | 45 | 5312.4498 | 5202.4113 | 2.115% | 0.2989%
2017-08-01 | 5 | 5347 | 109.843 | 2.054% | 15.5643 | 0.2911% | 125.4072 | 2.345% | 46 | 5331.4357 | 5221.5928 | 2.104% | 0.2981%
2017-06-03 | 3 | 5351 | 109.8018 | 2.052% | 15.5672 | 0.2909% | 125.369 | 2.343% | 47 | 5335.4328 | 5225.631 | 2.101% | 0.2979%
2017-08-01 | 4 | 5362 | 109.6886 | 2.046% | 15.5754 | 0.2905% | 125.264 | 2.336% | 48 | 5346.4246 | 5236.736 | 2.095% | 0.2974%
2017-06-29 | 3 | 5386 | 109.4416 | 2.032% | 15.5932 | 0.2895% | 125.0348 | 2.321% | 49 | 5370.4068 | 5260.9652 | 2.08% | 0.2964%
2017-06-27 | 5 | 5402 | 109.2769 | 2.023% | 15.6051 | 0.2889% | 124.882 | 2.312% | 50 | 5386.3949 | 5277.118 | 2.071% | 0.2957%
2017-07-30 | 4 | 5413 | 109.1637 | 2.017% | 15.6133 | 0.2884% | 124.777 | 2.305% | 51 | 5397.3867 | 5288.223 | 2.064% | 0.2952%
2017-06-27 | 4 | 5420 | 109.0917 | 2.013% | 15.6185 | 0.2882% | 124.7102 | 2.301% | 52 | 5404.3815 | 5295.2898 | 2.06% | 0.295%
2017-07-31 | 6 | 5435 | 108.9373 | 2.004% | 15.6297 | 0.2876% | 124.5669 | 2.292% | 53 | 5419.3703 | 5310.4331 | 2.051% | 0.2943%
2017-06-08 | 1 | 5457 | 108.7109 | 1.992% | 15.646 | 0.2867% | 124.3569 | 2.279% | 54 | 5441.354 | 5332.6431 | 2.039% | 0.2934%
2017-06-28 | 6 | 5459 | 108.6903 | 1.991% | 15.6475 | 0.2866% | 124.3378 | 2.278% | 55 | 5443.3525 | 5334.6622 | 2.037% | 0.2933%
2017-06-04 | 3 | 5463 | 108.6491 | 1.989% | 15.6505 | 0.2865% | 124.2996 | 2.275% | 56 | 5447.3495 | 5338.7004 | 2.035% | 0.2932%
2017-07-31 | 2 | 5472 | 108.5565 | 1.984% | 15.6571 | 0.2861% | 124.2136 | 2.27% | 57 | 5456.3429 | 5347.7864 | 2.03% | 0.2928%
2017-08-27 | 5 | 5475 | 108.5256 | 1.982% | 15.6594 | 0.286% | 124.185 | 2.268% | 58 | 5459.3406 | 5350.815 | 2.028% | 0.2927%
2017-06-29 | 6 | 5478 | 108.4947 | 1.981% | 15.6616 | 0.2859% | 124.1563 | 2.266% | 59 | 5462.3384 | 5353.8437 | 2.026% | 0.2925%
2017-08-27 | 6 | 5492 | 108.3506 | 1.973% | 15.672 | 0.2854% | 124.0226 | 2.258% | 60 | 5476.328 | 5367.9774 | 2.018% | 0.292%
2017-06-26 | 4 | 5496 | 108.3095 | 1.971% | 15.675 | 0.2852% | 123.9844 | 2.256% | 61 | 5480.325 | 5372.0156 | 2.016% | 0.2918%
2017-06-01 | 4 | 5504 | 108.2271 | 1.966% | 15.6809 | 0.2849% | 123.9081 | 2.251% | 62 | 5488.3191 | 5380.0919 | 2.012% | 0.2915%
2017-08-28 | 2 | 5512 | 108.1448 | 1.962% | 15.6869 | 0.2846% | 123.8317 | 2.247% | 63 | 5496.3131 | 5388.1683 | 2.007% | 0.2911%
2017-06-26 | 5 | 5514 | 108.1242 | 1.961% | 15.6884 | 0.2845% | 123.8126 | 2.245% | 64 | 5498.3116 | 5390.1874 | 2.006% | 0.2911%
2017-06-02 | 4 | 5515 | 108.1139 | 1.96% | 15.6891 | 0.2845% | 123.803 | 2.245% | 65 | 5499.3109 | 5391.197 | 2.005% | 0.291%
2017-08-27 | 7 | 5516 | 108.1036 | 1.96% | 15.6898 | 0.2844% | 123.7935 | 2.244% | 66 | 5500.3102 | 5392.2065 | 2.005% | 0.291%
2017-08-01 | 3 | 5517 | 108.0933 | 1.959% | 15.6906 | 0.2844% | 123.7839 | 2.244% | 67 | 5501.3094 | 5393.2161 | 2.004% | 0.2909%
2017-08-30 | 2 | 5524 | 108.0213 | 1.955% | 15.6958 | 0.2841% | 123.7171 | 2.24% | 68 | 5508.3042 | 5400.2829 | 2% | 0.2906%
2017-06-10 | 8 | 5526 | 108.0007 | 1.954% | 15.6973 | 0.2841% | 123.698 | 2.238% | 69 | 5510.3027 | 5402.302 | 1.999% | 0.2906%
2017-06-01 | 5 | 5535 | 107.9081 | 1.95% | 15.704 | 0.2837% | 123.612 | 2.233% | 70 | 5519.296 | 5411.388 | 1.994% | 0.2902%
2017-07-30 | 8 | 5537 | 107.8875 | 1.948% | 15.7054 | 0.2836% | 123.5929 | 2.232% | 71 | 5521.2946 | 5413.4071 | 1.993% | 0.2901%
2017-06-10 | 2 | 5541 | 107.8463 | 1.946% | 15.7084 | 0.2835% | 123.5547 | 2.23% | 72 | 5525.2916 | 5417.4453 | 1.991% | 0.29%
2017-06-02 | 5 | 5550 | 107.7537 | 1.942% | 15.7151 | 0.2832% | 123.4688 | 2.225% | 73 | 5534.2849 | 5426.5312 | 1.986% | 0.2896%
2017-06-27 | 3 | 5555 | 107.7022 | 1.939% | 15.7188 | 0.283% | 123.4211 | 2.222% | 74 | 5539.2812 | 5431.5789 | 1.983% | 0.2894%
2017-06-12 | 5 | 5563 | 107.6199 | 1.935% | 15.7248 | 0.2827% | 123.3447 | 2.217% | 75 | 5547.2752 | 5439.6553 | 1.978% | 0.2891%
2017-06-07 | 4 | 5568 | 107.5684 | 1.932% | 15.7285 | 0.2825% | 123.2969 | 2.214% | 76 | 5552.2715 | 5444.7031 | 1.976% | 0.2889%
2017-06-12 | 4 | 5568 | 107.5684 | 1.932% | 15.7285 | 0.2825% | 123.2969 | 2.214% | 77 | 5552.2715 | 5444.7031 | 1.976% | 0.2889%
2017-06-11 | 3 | 5587 | 107.3729 | 1.922% | 15.7426 | 0.2818% | 123.1155 | 2.204% | 78 | 5571.2574 | 5463.8845 | 1.965% | 0.2881%
2017-08-10 | 4 | 5593 | 107.3111 | 1.919% | 15.7471 | 0.2815% | 123.0582 | 2.2% | 79 | 5577.2529 | 5469.9418 | 1.962% | 0.2879%
2017-08-27 | 4 | 5594 | 107.3008 | 1.918% | 15.7478 | 0.2815% | 123.0486 | 2.2% | 80 | 5578.2522 | 5470.9514 | 1.961% | 0.2878%
2017-06-11 | 8 | 5599 | 107.2494 | 1.916% | 15.7515 | 0.2813% | 123.0009 | 2.197% | 81 | 5583.2485 | 5475.9991 | 1.959% | 0.2876%
2017-06-04 | 8 | 5600 | 107.2391 | 1.915% | 15.7523 | 0.2813% | 122.9914 | 2.196% | 82 | 5584.2477 | 5477.0086 | 1.958% | 0.2876%
2017-08-10 | 5 | 5600 | 107.2391 | 1.915% | 15.7523 | 0.2813% | 122.9914 | 2.196% | 83 | 5584.2477 | 5477.0086 | 1.958% | 0.2876%
2017-06-07 | 5 | 5602 | 107.2185 | 1.914% | 15.7537 | 0.2812% | 122.9723 | 2.195% | 84 | 5586.2463 | 5479.0277 | 1.957% | 0.2875%
2017-08-02 | 5 | 5607 | 107.1671 | 1.911% | 15.7575 | 0.281% | 122.9245 | 2.192% | 85 | 5591.2425 | 5484.0755 | 1.954% | 0.2873%
2017-06-28 | 2 | 5609 | 107.1465 | 1.91% | 15.7589 | 0.281% | 122.9054 | 2.191% | 86 | 5593.2411 | 5486.0946 | 1.953% | 0.2873%
2017-07-30 | 3 | 5609 | 107.1465 | 1.91% | 15.7589 | 0.281% | 122.9054 | 2.191% | 87 | 5593.2411 | 5486.0946 | 1.953% | 0.2873%
2017-08-01 | 6 | 5610 | 107.1362 | 1.91% | 15.7597 | 0.2809% | 122.8959 | 2.191% | 88 | 5594.2403 | 5487.1041 | 1.953% | 0.2872%
2017-06-09 | 7 | 5611 | 107.1259 | 1.909% | 15.7604 | 0.2809% | 122.8863 | 2.19% | 89 | 5595.2396 | 5488.1137 | 1.952% | 0.2872%
2017-06-03 | 8 | 5615 | 107.0847 | 1.907% | 15.7634 | 0.2807% | 122.8481 | 2.188% | 90 | 5599.2366 | 5492.1519 | 1.95% | 0.287%
2017-06-06 | 4 | 5620 | 107.0333 | 1.905% | 15.7671 | 0.2806% | 122.8004 | 2.185% | 91 | 5604.2329 | 5497.1996 | 1.947% | 0.2868%
2017-08-06 | 5 | 5639 | 106.8377 | 1.895% | 15.7812 | 0.2799% | 122.6189 | 2.174% | 92 | 5623.2188 | 5516.3811 | 1.937% | 0.2861%
2017-08-29 | 4 | 5640 | 106.8274 | 1.894% | 15.782 | 0.2798% | 122.6094 | 2.174% | 93 | 5624.218 | 5517.3906 | 1.936% | 0.286%
2017-06-06 | 5 | 5644 | 106.7862 | 1.892% | 15.7849 | 0.2797% | 122.5712 | 2.172% | 94 | 5628.2151 | 5521.4288 | 1.934% | 0.2859%
2017-08-06 | 6 | 5651 | 106.7142 | 1.888% | 15.7901 | 0.2794% | 122.5044 | 2.168% | 95 | 5635.2099 | 5528.4956 | 1.93% | 0.2856%
2017-06-27 | 6 | 5653 | 106.6936 | 1.887% | 15.7916 | 0.2793% | 122.4853 | 2.167% | 96 | 5637.2084 | 5530.5147 | 1.929% | 0.2855%
2017-08-02 | 4 | 5654 | 106.6833 | 1.887% | 15.7924 | 0.2793% | 122.4757 | 2.166% | 97 | 5638.2076 | 5531.5243 | 1.929% | 0.2855%
2017-08-30 | 6 | 5663 | 106.5907 | 1.882% | 15.7991 | 0.279% | 122.3898 | 2.161% | 98 | 5647.2009 | 5540.6102 | 1.924% | 0.2852%
2017-06-03 | 2 | 5668 | 106.5392 | 1.88% | 15.8028 | 0.2788% | 122.342 | 2.158% | 99 | 5652.1972 | 5545.658 | 1.921% | 0.285%
2017-06-01 | 3 | 5672 | 106.4981 | 1.878% | 15.8058 | 0.2787% | 122.3038 | 2.156% | 100 | 5656.1942 | 5549.6962 | 1.919% | 0.2848%
2017-06-29 | 2 | 5682 | 106.3952 | 1.872% | 15.8132 | 0.2783% | 122.2083 | 2.151% | 101 | 5666.1868 | 5559.7917 | 1.914% | 0.2844%
2017-08-29 | 5 | 5685 | 106.3643 | 1.871% | 15.8154 | 0.2782% | 122.1797 | 2.149% | 102 | 5669.1846 | 5562.8203 | 1.912% | 0.2843%
2017-08-06 | 7 | 5691 | 106.3025 | 1.868% | 15.8199 | 0.278% | 122.1224 | 2.146% | 103 | 5675.1801 | 5568.8776 | 1.909% | 0.2841%
2017-06-02 | 3 | 5701 | 106.1996 | 1.863% | 15.8273 | 0.2776% | 122.0269 | 2.14% | 104 | 5685.1727 | 5578.9731 | 1.904% | 0.2837%
2017-07-09 | 7 | 5708 | 106.1276 | 1.859% | 15.8325 | 0.2774% | 121.9601 | 2.137% | 105 | 5692.1675 | 5586.0399 | 1.9% | 0.2834%
2017-06-26 | 3 | 5709 | 106.1173 | 1.859% | 15.8332 | 0.2773% | 121.9505 | 2.136% | 106 | 5693.1668 | 5587.0495 | 1.899% | 0.2834%
2017-08-27 | 8 | 5718 | 106.0246 | 1.854% | 15.8399 | 0.277% | 121.8646 | 2.131% | 107 | 5702.1601 | 5596.1354 | 1.895% | 0.2831%
2017-06-08 | 7 | 5723 | 105.9732 | 1.852% | 15.8436 | 0.2768% | 121.8168 | 2.129% | 108 | 5707.1564 | 5601.1832 | 1.892% | 0.2829%
2017-08-29 | 3 | 5725 | 105.9526 | 1.851% | 15.8451 | 0.2768% | 121.7977 | 2.127% | 109 | 5709.1549 | 5603.2023 | 1.891% | 0.2828%
2017-08-10 | 3 | 5735 | 105.8497 | 1.846% | 15.8526 | 0.2764% | 121.7022 | 2.122% | 110 | 5719.1474 | 5613.2978 | 1.886% | 0.2824%
2017-08-06 | 4 | 5739 | 105.8085 | 1.844% | 15.8555 | 0.2763% | 121.664 | 2.12% | 111 | 5723.1445 | 5617.336 | 1.884% | 0.2823%
2017-06-13 | 5 | 5742 | 105.7776 | 1.842% | 15.8578 | 0.2762% | 121.6354 | 2.118% | 112 | 5726.1422 | 5620.3646 | 1.882% | 0.2821%
2017-06-07 | 3 | 5743 | 105.7673 | 1.842% | 15.8585 | 0.2761% | 121.6258 | 2.118% | 113 | 5727.1415 | 5621.3742 | 1.882% | 0.2821%
2017-08-28 | 6 | 5771 | 105.4792 | 1.828% | 15.8793 | 0.2752% | 121.3585 | 2.103% | 114 | 5755.1207 | 5649.6415 | 1.867% | 0.2811%
2017-06-14 | 5 | 5773 | 105.4586 | 1.827% | 15.8808 | 0.2751% | 121.3394 | 2.102% | 115 | 5757.1192 | 5651.6606 | 1.866% | 0.281%
2017-06-06 | 3 | 5778 | 105.4071 | 1.824% | 15.8845 | 0.2749% | 121.2916 | 2.099% | 116 | 5762.1155 | 5656.7084 | 1.863% | 0.2808%
2017-06-28 | 7 | 5784 | 105.3454 | 1.821% | 15.889 | 0.2747% | 121.2343 | 2.096% | 117 | 5768.111 | 5662.7657 | 1.86% | 0.2806%
2017-08-02 | 3 | 5784 | 105.3454 | 1.821% | 15.889 | 0.2747% | 121.2343 | 2.096% | 118 | 5768.111 | 5662.7657 | 1.86% | 0.2806%
2017-06-12 | 3 | 5785 | 105.3351 | 1.821% | 15.8897 | 0.2747% | 121.2248 | 2.096% | 119 | 5769.1103 | 5663.7752 | 1.86% | 0.2805%
2017-06-26 | 6 | 5785 | 105.3351 | 1.821% | 15.8897 | 0.2747% | 121.2248 | 2.096% | 120 | 5769.1103 | 5663.7752 | 1.86% | 0.2805%
2017-06-08 | 24 | 5786 | 105.3248 | 1.82% | 15.8905 | 0.2746% | 121.2152 | 2.095% | 121 | 5770.1095 | 5664.7848 | 1.859% | 0.2805%
2017-06-21 | 5 | 5789 | 105.2939 | 1.819% | 15.8927 | 0.2745% | 121.1866 | 2.093% | 122 | 5773.1073 | 5667.8134 | 1.858% | 0.2804%
2017-06-14 | 4 | 5792 | 105.263 | 1.817% | 15.8949 | 0.2744% | 121.1579 | 2.092% | 123 | 5776.1051 | 5670.8421 | 1.856% | 0.2803%
2017-06-13 | 4 | 5795 | 105.2322 | 1.816% | 15.8971 | 0.2743% | 121.1293 | 2.09% | 124 | 5779.1029 | 5673.8707 | 1.855% | 0.2802%
2017-06-21 | 4 | 5795 | 105.2322 | 1.816% | 15.8971 | 0.2743% | 121.1293 | 2.09% | 125 | 5779.1029 | 5673.8707 | 1.855% | 0.2802%
2017-08-09 | 4 | 5802 | 105.1601 | 1.812% | 15.9023 | 0.2741% | 121.0625 | 2.087% | 126 | 5786.0977 | 5680.9375 | 1.851% | 0.2799%
2017-06-05 | 4 | 5803 | 105.1498 | 1.812% | 15.9031 | 0.274% | 121.0529 | 2.086% | 127 | 5787.0969 | 5681.9471 | 1.851% | 0.2799%
2017-07-31 | 7 | 5803 | 105.1498 | 1.812% | 15.9031 | 0.274% | 121.0529 | 2.086% | 128 | 5787.0969 | 5681.9471 | 1.851% | 0.2799%
2017-07-09 | 6 | 5804 | 105.1395 | 1.812% | 15.9038 | 0.274% | 121.0434 | 2.086% | 129 | 5788.0962 | 5682.9566 | 1.85% | 0.2799%
2017-08-01 | 2 | 5804 | 105.1395 | 1.812% | 15.9038 | 0.274% | 121.0434 | 2.086% | 130 | 5788.0962 | 5682.9566 | 1.85% | 0.2799%
2017-08-27 | 3 | 5810 | 105.0778 | 1.809% | 15.9083 | 0.2738% | 120.9861 | 2.082% | 131 | 5794.0917 | 5689.0139 | 1.847% | 0.2796%
2017-06-04 | 2 | 5817 | 105.0057 | 1.805% | 15.9135 | 0.2736% | 120.9192 | 2.079% | 132 | 5801.0865 | 5696.0808 | 1.843% | 0.2794%
2017-06-25 | 5 | 5818 | 104.9954 | 1.805% | 15.9142 | 0.2735% | 120.9097 | 2.078% | 133 | 5802.0858 | 5697.0903 | 1.843% | 0.2793%
2017-07-09 | 5 | 5823 | 104.944 | 1.802% | 15.918 | 0.2734% | 120.8619 | 2.076% | 134 | 5807.082 | 5702.1381 | 1.84% | 0.2792%
2017-06-12 | 6 | 5832 | 104.8514 | 1.798% | 15.9246 | 0.2731% | 120.776 | 2.071% | 135 | 5816.0754 | 5711.224 | 1.836% | 0.2788%
2017-06-25 | 6 | 5833 | 104.8411 | 1.797% | 15.9254 | 0.273% | 120.7664 | 2.07% | 136 | 5817.0746 | 5712.2336 | 1.835% | 0.2788%
2017-08-30 | 1 | 5833 | 104.8411 | 1.797% | 15.9254 | 0.273% | 120.7664 | 2.07% | 137 | 5817.0746 | 5712.2336 | 1.835% | 0.2788%
2017-06-29 | 7 | 5834 | 104.8308 | 1.797% | 15.9261 | 0.273% | 120.7569 | 2.07% | 138 | 5818.0739 | 5713.2431 | 1.835% | 0.2788%
2017-08-09 | 5 | 5835 | 104.8205 | 1.796% | 15.9269 | 0.273% | 120.7473 | 2.069% | 139 | 5819.0731 | 5714.2527 | 1.834% | 0.2787%
2017-06-21 | 3 | 5837 | 104.7999 | 1.795% | 15.9284 | 0.2729% | 120.7282 | 2.068% | 140 | 5821.0716 | 5716.2718 | 1.833% | 0.2786%
2017-06-25 | 7 | 5837 | 104.7999 | 1.795% | 15.9284 | 0.2729% | 120.7282 | 2.068% | 141 | 5821.0716 | 5716.2718 | 1.833% | 0.2786%
2017-08-28 | 1 | 5842 | 104.7484 | 1.793% | 15.9321 | 0.2727% | 120.6805 | 2.066% | 142 | 5826.0679 | 5721.3195 | 1.831% | 0.2785%
2017-07-02 | 7 | 5852 | 104.6455 | 1.788% | 15.9395 | 0.2724% | 120.585 | 2.061% | 143 | 5836.0605 | 5731.415 | 1.826% | 0.2781%
2017-06-05 | 5 | 5853 | 104.6352 | 1.788% | 15.9402 | 0.2723% | 120.5755 | 2.06% | 144 | 5837.0598 | 5732.4245 | 1.825% | 0.2781%
2017-08-26 | 5 | 5855 | 104.6146 | 1.787% | 15.9417 | 0.2723% | 120.5564 | 2.059% | 145 | 5839.0583 | 5734.4436 | 1.824% | 0.278%
2017-06-30 | 5 | 5859 | 104.5735 | 1.785% | 15.9447 | 0.2721% | 120.5182 | 2.057% | 146 | 5843.0553 | 5738.4818 | 1.822% | 0.2779%
2017-06-02 | 6 | 5861 | 104.5529 | 1.784% | 15.9462 | 0.2721% | 120.4991 | 2.056% | 147 | 5845.0538 | 5740.5009 | 1.821% | 0.2778%
2017-08-10 | 6 | 5870 | 104.4603 | 1.78% | 15.9529 | 0.2718% | 120.4131 | 2.051% | 148 | 5854.0471 | 5749.5869 | 1.817% | 0.2775%
2017-06-27 | 2 | 5872 | 104.4397 | 1.779% | 15.9544 | 0.2717% | 120.394 | 2.05% | 149 | 5856.0456 | 5751.606 | 1.816% | 0.2774%
2017-06-01 | 6 | 5873 | 104.4294 | 1.778% | 15.9551 | 0.2717% | 120.3845 | 2.05% | 150 | 5857.0449 | 5752.6155 | 1.815% | 0.2774%
2017-08-31 | 4 | 5877 | 104.3882 | 1.776% | 15.9581 | 0.2715% | 120.3463 | 2.048% | 151 | 5861.0419 | 5756.6537 | 1.813% | 0.2772%
2017-07-30 | 2 | 5878 | 104.3779 | 1.776% | 15.9588 | 0.2715% | 120.3367 | 2.047% | 152 | 5862.0412 | 5757.6633 | 1.813% | 0.2772%
2017-08-02 | 6 | 5882 | 104.3368 | 1.774% | 15.9618 | 0.2714% | 120.2985 | 2.045% | 153 | 5866.0382 | 5761.7015 | 1.811% | 0.277%
2017-07-31 | 1 | 5889 | 104.2647 | 1.77% | 15.967 | 0.2711% | 120.2317 | 2.042% | 154 | 5873.033 | 5768.7683 | 1.807% | 0.2768%
2017-06-25 | 4 | 5893 | 104.2235 | 1.769% | 15.97 | 0.271% | 120.1935 | 2.04% | 155 | 5877.03 | 5772.8065 | 1.805% | 0.2766%
2017-07-02 | 6 | 5906 | 104.0897 | 1.762% | 15.9796 | 0.2706% | 120.0694 | 2.033% | 156 | 5890.0204 | 5785.9306 | 1.799% | 0.2762%
2017-08-09 | 3 | 5909 | 104.0589 | 1.761% | 15.9819 | 0.2705% | 120.0407 | 2.031% | 157 | 5893.0181 | 5788.9593 | 1.798% | 0.2761%
2017-08-26 | 6 | 5910 | 104.0486 | 1.761% | 15.9826 | 0.2704% | 120.0312 | 2.031% | 158 | 5894.0174 | 5789.9688 | 1.797% | 0.276%
2017-07-04 | 5 | 5911 | 104.0383 | 1.76% | 15.9833 | 0.2704% | 120.0216 | 2.03% | 159 | 5895.0167 | 5790.9784 | 1.797% | 0.276%
2017-06-05 | 3 | 5912 | 104.028 | 1.76% | 15.9841 | 0.2704% | 120.0121 | 2.03% | 160 | 5896.0159 | 5791.9879 | 1.796% | 0.276%
2017-08-06 | 8 | 5914 | 104.0074 | 1.759% | 15.9856 | 0.2703% | 119.993 | 2.029% | 161 | 5898.0144 | 5794.007 | 1.795% | 0.2759%
2017-06-07 | 6 | 5915 | 103.9971 | 1.758% | 15.9863 | 0.2703% | 119.9834 | 2.028% | 162 | 5899.0137 | 5795.0166 | 1.795% | 0.2759%
2017-06-30 | 4 | 5916 | 103.9868 | 1.758% | 15.9871 | 0.2702% | 119.9739 | 2.028% | 163 | 5900.0129 | 5796.0261 | 1.794% | 0.2758%
2017-08-29 | 2 | 5916 | 103.9868 | 1.758% | 15.9871 | 0.2702% | 119.9739 | 2.028% | 164 | 5900.0129 | 5796.0261 | 1.794% | 0.2758%
2017-06-01 | 2 | 5919 | 103.9559 | 1.756% | 15.9893 | 0.2701% | 119.9452 | 2.026% | 165 | 5903.0107 | 5799.0548 | 1.793% | 0.2757%
2017-08-31 | 5 | 5929 | 103.853 | 1.752% | 15.9967 | 0.2698% | 119.8497 | 2.021% | 166 | 5913.0033 | 5809.1503 | 1.788% | 0.2754%
2017-06-11 | 2 | 5934 | 103.8016 | 1.749% | 16.0004 | 0.2696% | 119.802 | 2.019% | 167 | 5917.9996 | 5814.198 | 1.785% | 0.2752%
2017-06-10 | 1 | 5946 | 103.6781 | 1.744% | 16.0093 | 0.2692% | 119.6874 | 2.013% | 168 | 5929.9907 | 5826.3126 | 1.779% | 0.2748%
2017-06-02 | 2 | 5955 | 103.5854 | 1.739% | 16.016 | 0.269% | 119.6015 | 2.008% | 169 | 5938.984 | 5835.3985 | 1.775% | 0.2745%
2017-07-04 | 7 | 5965 | 103.4825 | 1.735% | 16.0235 | 0.2686% | 119.506 | 2.003% | 170 | 5948.9765 | 5845.494 | 1.77% | 0.2741%
2017-07-19 | 5 | 5965 | 103.4825 | 1.735% | 16.0235 | 0.2686% | 119.506 | 2.003% | 171 | 5948.9765 | 5845.494 | 1.77% | 0.2741%
2017-08-03 | 5 | 5966 | 103.4722 | 1.734% | 16.0242 | 0.2686% | 119.4964 | 2.003% | 172 | 5949.9758 | 5846.5036 | 1.77% | 0.2741%
2017-08-26 | 4 | 5966 | 103.4722 | 1.734% | 16.0242 | 0.2686% | 119.4964 | 2.003% | 173 | 5949.9758 | 5846.5036 | 1.77% | 0.2741%
2017-06-13 | 3 | 5968 | 103.4516 | 1.733% | 16.0257 | 0.2685% | 119.4773 | 2.002% | 174 | 5951.9743 | 5848.5227 | 1.769% | 0.274%
2017-07-02 | 5 | 5970 | 103.4311 | 1.733% | 16.0272 | 0.2685% | 119.4582 | 2.001% | 175 | 5953.9728 | 5850.5418 | 1.768% | 0.2739%
2017-07-04 | 6 | 5970 | 103.4311 | 1.733% | 16.0272 | 0.2685% | 119.4582 | 2.001% | 176 | 5953.9728 | 5850.5418 | 1.768% | 0.2739%
2017-06-17 | 5 | 5973 | 103.4002 | 1.731% | 16.0294 | 0.2684% | 119.4296 | 1.999% | 177 | 5956.9706 | 5853.5704 | 1.766% | 0.2738%
2017-08-31 | 3 | 5974 | 103.3899 | 1.731% | 16.0301 | 0.2683% | 119.42 | 1.999% | 178 | 5957.9699 | 5854.58 | 1.766% | 0.2738%
2017-08-03 | 4 | 5979 | 103.3384 | 1.728% | 16.0339 | 0.2682% | 119.3723 | 1.997% | 179 | 5962.9661 | 5859.6277 | 1.764% | 0.2736%
2017-08-01 | 7 | 5985 | 103.2767 | 1.726% | 16.0383 | 0.268% | 119.315 | 1.994% | 180 | 5968.9617 | 5865.685 | 1.761% | 0.2734%
2017-06-07 | 24 | 5986 | 103.2677 | 1.725% | 16.0391 | 0.2679% | 119.3068 | 1.993% | 181 | 5969.9609 | 5866.6932 | 1.76% | 0.2734%
2017-06-18 | 6 | 5986 | 103.2677 | 1.725% | 16.0391 | 0.2679% | 119.3068 | 1.993% | 182 | 5969.9609 | 5866.6932 | 1.76% | 0.2734% | 5985.9532
2017-07-09 | 4 | 5986 | 103.2677 | 1.725% | 16.0391 | 0.2679% | 119.3068 | 1.993% | 183 | 5969.9609 | 5866.6932 | 1.76% | 0.2734%
2017-06-06 | 6 | 5987 | 103.272 | 1.725% | 16.0401 | 0.2679% | 119.312 | 1.993% | 184 | 5970.9599 | 5867.688 | 1.76% | 0.2734%
2017-06-18 | 7 | 5993 | 103.2975 | 1.724% | 16.0459 | 0.2677% | 119.3434 | 1.991% | 185 | 5976.9541 | 5873.6566 | 1.759% | 0.2732%
2017-08-06 | 3 | 5994 | 103.3018 | 1.723% | 16.0469 | 0.2677% | 119.3487 | 1.991% | 186 | 5977.9531 | 5874.6513 | 1.758% | 0.2732%
2017-08-10 | 2 | 5994 | 103.3018 | 1.723% | 16.0469 | 0.2677% | 119.3487 | 1.991% | 187 | 5977.9531 | 5874.6513 | 1.758% | 0.2732%
2017-07-19 | 4 | 5996 | 103.3103 | 1.723% | 16.0488 | 0.2677% | 119.3591 | 1.991% | 188 | 5979.9512 | 5876.6409 | 1.758% | 0.2731%
2017-06-13 | 6 | 5998 | 103.3188 | 1.723% | 16.0508 | 0.2676% | 119.3696 | 1.99% | 189 | 5981.9492 | 5878.6304 | 1.758% | 0.273%
2017-06-18 | 5 | 5998 | 103.3188 | 1.723% | 16.0508 | 0.2676% | 119.3696 | 1.99% | 190 | 5981.9492 | 5878.6304 | 1.758% | 0.273%
2017-06-14 | 3 | 6001 | 103.3316 | 1.722% | 16.0537 | 0.2675% | 119.3853 | 1.989% | 191 | 5984.9463 | 5881.6147 | 1.757% | 0.2729%
2017-06-26 | 2 | 6001 | 103.3316 | 1.722% | 16.0537 | 0.2675% | 119.3853 | 1.989% | 192 | 5984.9463 | 5881.6147 | 1.757% | 0.2729%
2017-07-04 | 4 | 6002 | 103.3358 | 1.722% | 16.0547 | 0.2675% | 119.3905 | 1.989% | 193 | 5985.9453 | 5882.6095 | 1.757% | 0.2729%
2017-06-06 | 2 | 6003 | 103.3401 | 1.721% | 16.0556 | 0.2675% | 119.3957 | 1.989% | 194 | 5986.9444 | 5883.6043 | 1.756% | 0.2729%
2017-06-09 | 8 | 6004 | 103.3444 | 1.721% | 16.0566 | 0.2674% | 119.401 | 1.989% | 195 | 5987.9434 | 5884.599 | 1.756% | 0.2729%
2017-06-17 | 4 | 6014 | 103.3869 | 1.719% | 16.0663 | 0.2671% | 119.4533 | 1.986% | 196 | 5997.9337 | 5894.5467 | 1.754% | 0.2726%
2017-06-21 | 2 | 6014 | 103.3869 | 1.719% | 16.0663 | 0.2671% | 119.4533 | 1.986% | 197 | 5997.9337 | 5894.5467 | 1.754% | 0.2726%
2017-06-07 | 2 | 6017 | 103.3997 | 1.718% | 16.0693 | 0.2671% | 119.4689 | 1.986% | 198 | 6000.9307 | 5897.5311 | 1.753% | 0.2725%
2017-06-27 | 7 | 6017 | 103.3997 | 1.718% | 16.0693 | 0.2671% | 119.4689 | 1.986% | 199 | 6000.9307 | 5897.5311 | 1.753% | 0.2725%
2017-08-26 | 7 | 6019 | 103.4082 | 1.718% | 16.0712 | 0.267% | 119.4794 | 1.985% | 200 | 6002.9288 | 5899.5206 | 1.753% | 0.2724%
2017-07-17 | 4 | 6031 | 103.4593 | 1.715% | 16.0829 | 0.2667% | 119.5422 | 1.982% | 201 | 6014.9171 | 5911.4578 | 1.75% | 0.2721%
2017-07-01 | 5 | 6036 | 103.4806 | 1.714% | 16.0877 | 0.2665% | 119.5683 | 1.981% | 202 | 6019.9123 | 5916.4317 | 1.749% | 0.2719%
2017-06-14 | 6 | 6045 | 103.5189 | 1.712% | 16.0965 | 0.2663% | 119.6154 | 1.979% | 203 | 6028.9035 | 5925.3846 | 1.747% | 0.2717%
2017-06-17 | 6 | 6049 | 103.5359 | 1.712% | 16.1004 | 0.2662% | 119.6363 | 1.978% | 204 | 6032.8996 | 5929.3637 | 1.746% | 0.2715%
2017-06-18 | 4 | 6055 | 103.5615 | 1.71% | 16.1062 | 0.266% | 119.6677 | 1.976% | 205 | 6038.8938 | 5935.3323 | 1.745% | 0.2714%
2017-06-25 | 3 | 6055 | 103.5615 | 1.71% | 16.1062 | 0.266% | 119.6677 | 1.976% | 206 | 6038.8938 | 5935.3323 | 1.745% | 0.2714%
2017-07-01 | 6 | 6055 | 103.5615 | 1.71% | 16.1062 | 0.266% | 119.6677 | 1.976% | 207 | 6038.8938 | 5935.3323 | 1.745% | 0.2714%
2017-08-29 | 6 | 6061 | 103.587 | 1.709% | 16.1121 | 0.2658% | 119.6991 | 1.975% | 208 | 6044.8879 | 5941.3009 | 1.744% | 0.2712%
2017-06-28 | 1 | 6064 | 103.5998 | 1.708% | 16.115 | 0.2657% | 119.7148 | 1.974% | 209 | 6047.885 | 5944.2852 | 1.743% | 0.2711%
2017-08-02 | 2 | 6067 | 103.6125 | 1.708% | 16.1179 | 0.2657% | 119.7305 | 1.973% | 210 | 6050.8821 | 5947.2695 | 1.742% | 0.271%
2017-07-17 | 5 | 6079 | 103.6636 | 1.705% | 16.1296 | 0.2653% | 119.7932 | 1.971% | 211 | 6062.8704 | 5959.2068 | 1.74% | 0.2707%
2017-06-30 | 6 | 6080 | 103.6679 | 1.705% | 16.1306 | 0.2653% | 119.7984 | 1.97% | 212 | 6063.8694 | 5960.2016 | 1.739% | 0.2706%
2017-06-08 | 8 | 6082 | 103.6764 | 1.705% | 16.1325 | 0.2653% | 119.8089 | 1.97% | 213 | 6065.8675 | 5962.1911 | 1.739% | 0.2706%
2017-08-25 | 4 | 6086 | 103.6934 | 1.704% | 16.1364 | 0.2651% | 119.8298 | 1.969% | 214 | 6069.8636 | 5966.1702 | 1.738% | 0.2705%
2017-06-21 | 6 | 6090 | 103.7104 | 1.703% | 16.1403 | 0.265% | 119.8507 | 1.968% | 215 | 6073.8597 | 5970.1493 | 1.737% | 0.2703%
2017-06-22 | 4 | 6090 | 103.7104 | 1.703% | 16.1403 | 0.265% | 119.8507 | 1.968% | 216 | 6073.8597 | 5970.1493 | 1.737% | 0.2703%
2017-06-16 | 5 | 6091 | 103.7147 | 1.703% | 16.1413 | 0.265% | 119.856 | 1.968% | 217 | 6074.8587 | 5971.144 | 1.737% | 0.2703%
2017-06-22 | 5 | 6092 | 103.719 | 1.703% | 16.1422 | 0.265% | 119.8612 | 1.968% | 218 | 6075.8578 | 5972.1388 | 1.737% | 0.2703%
2017-07-01 | 4 | 6092 | 103.719 | 1.703% | 16.1422 | 0.265% | 119.8612 | 1.968% | 219 | 6075.8578 | 5972.1388 | 1.737% | 0.2703%
2017-08-27 | 2 | 6092 | 103.719 | 1.703% | 16.1422 | 0.265% | 119.8612 | 1.968% | 220 | 6075.8578 | 5972.1388 | 1.737% | 0.2703%
2017-06-30 | 3 | 6103 | 103.7658 | 1.7% | 16.1529 | 0.2647% | 119.9187 | 1.965% | 221 | 6086.8471 | 5983.0813 | 1.734% | 0.27%
2017-08-09 | 2 | 6104 | 103.77 | 1.7% | 16.1539 | 0.2646% | 119.924 | 1.965% | 222 | 6087.8461 | 5984.076 | 1.734% | 0.2699%
2017-06-12 | 2 | 6105 | 103.7743 | 1.7% | 16.1549 | 0.2646% | 119.9292 | 1.964% | 223 | 6088.8451 | 5985.0708 | 1.734% | 0.2699%
2017-06-16 | 4 | 6111 | 103.7998 | 1.699% | 16.1607 | 0.2645% | 119.9606 | 1.963% | 224 | 6094.8393 | 5991.0394 | 1.733% | 0.2697%
2017-06-17 | 7 | 6112 | 103.8041 | 1.698% | 16.1617 | 0.2644% | 119.9658 | 1.963% | 225 | 6095.8383 | 5992.0342 | 1.732% | 0.2697%
2017-07-10 | 4 | 6116 | 103.8211 | 1.698% | 16.1656 | 0.2643% | 119.9867 | 1.962% | 226 | 6099.8344 | 5996.0133 | 1.732% | 0.2696%
2017-08-09 | 6 | 6117 | 103.8254 | 1.697% | 16.1666 | 0.2643% | 119.992 | 1.962% | 227 | 6100.8334 | 5997.008 | 1.731% | 0.2696%
2017-07-30 | 9 | 6118 | 103.8296 | 1.697% | 16.1675 | 0.2643% | 119.9972 | 1.961% | 228 | 6101.8325 | 5998.0028 | 1.731% | 0.2695%
2017-07-01 | 7 | 6123 | 103.8509 | 1.696% | 16.1724 | 0.2641% | 120.0233 | 1.96% | 229 | 6106.8276 | 6002.9767 | 1.73% | 0.2694%
2017-07-02 | 4 | 6123 | 103.8509 | 1.696% | 16.1724 | 0.2641% | 120.0233 | 1.96% | 230 | 6106.8276 | 6002.9767 | 1.73% | 0.2694%
2017-08-03 | 3 | 6126 | 103.8637 | 1.695% | 16.1753 | 0.264% | 120.039 | 1.96% | 231 | 6109.8247 | 6005.961 | 1.729% | 0.2693%
2017-08-25 | 5 | 6127 | 103.868 | 1.695% | 16.1763 | 0.264% | 120.0443 | 1.959% | 232 | 6110.8237 | 6006.9557 | 1.729% | 0.2693%
2017-06-29 | 1 | 6128 | 103.8722 | 1.695% | 16.1773 | 0.264% | 120.0495 | 1.959% | 233 | 6111.8227 | 6007.9505 | 1.729% | 0.2693%
2017-06-03 | 1 | 6132 | 103.8892 | 1.694% | 16.1812 | 0.2639% | 120.0704 | 1.958% | 234 | 6115.8188 | 6011.9296 | 1.728% | 0.2692%
2017-08-04 | 5 | 6133 | 103.8935 | 1.694% | 16.1821 | 0.2639% | 120.0756 | 1.958% | 235 | 6116.8179 | 6012.9244 | 1.728% | 0.2691%
2017-07-10 | 5 | 6136 | 103.9063 | 1.693% | 16.1851 | 0.2638% | 120.0913 | 1.957% | 236 | 6119.8149 | 6015.9087 | 1.727% | 0.269%
2017-06-26 | 7 | 6137 | 103.9105 | 1.693% | 16.186 | 0.2637% | 120.0966 | 1.957% | 237 | 6120.814 | 6016.9034 | 1.727% | 0.269%
2017-06-15 | 5 | 6147 | 103.9531 | 1.691% | 16.1958 | 0.2635% | 120.1489 | 1.955% | 238 | 6130.8042 | 6026.8511 | 1.725% | 0.2687%
2017-07-05 | 5 | 6150 | 103.9659 | 1.691% | 16.1987 | 0.2634% | 120.1646 | 1.954% | 239 | 6133.8013 | 6029.8354 | 1.724% | 0.2686%
2017-06-10 | 9 | 6151 | 103.9701 | 1.69% | 16.1997 | 0.2634% | 120.1698 | 1.954% | 240 | 6134.8003 | 6030.8302 | 1.724% | 0.2686%
2017-07-09 | 8 | 6155 | 103.9872 | 1.689% | 16.2035 | 0.2633% | 120.1907 | 1.953% | 241 | 6138.7965 | 6034.8093 | 1.723% | 0.2685%
2017-08-04 | 4 | 6155 | 103.9872 | 1.689% | 16.2035 | 0.2633% | 120.1907 | 1.953% | 242 | 6138.7965 | 6034.8093 | 1.723% | 0.2685%
2017-06-05 | 2 | 6158 | 103.9999 | 1.689% | 16.2065 | 0.2632% | 120.2064 | 1.952% | 243 | 6141.7935 | 6037.7936 | 1.722% | 0.2684%
2017-07-16 | 6 | 6170 | 104.051 | 1.686% | 16.2181 | 0.2629% | 120.2692 | 1.949% | 244 | 6153.7819 | 6049.7308 | 1.72% | 0.2681%
2017-06-25 | 8 | 6173 | 104.0638 | 1.686% | 16.2211 | 0.2628% | 120.2848 | 1.949% | 245 | 6156.7789 | 6052.7152 | 1.719% | 0.268%
2017-08-26 | 3 | 6173 | 104.0638 | 1.686% | 16.2211 | 0.2628% | 120.2848 | 1.949% | 246 | 6156.7789 | 6052.7152 | 1.719% | 0.268%
2017-07-16 | 7 | 6178 | 104.0851 | 1.685% | 16.2259 | 0.2626% | 120.311 | 1.947% | 247 | 6161.7741 | 6057.689 | 1.718% | 0.2679%
2017-07-19 | 3 | 6179 | 104.0893 | 1.685% | 16.2269 | 0.2626% | 120.3162 | 1.947% | 248 | 6162.7731 | 6058.6838 | 1.718% | 0.2678%
2017-06-15 | 4 | 6180 | 104.0936 | 1.684% | 16.2279 | 0.2626% | 120.3215 | 1.947% | 249 | 6163.7721 | 6059.6785 | 1.718% | 0.2678%
2017-08-01 | 1 | 6181 | 104.0978 | 1.684% | 16.2289 | 0.2626% | 120.3267 | 1.947% | 250 | 6164.7711 | 6060.6733 | 1.718% | 0.2678%
2017-07-17 | 3 | 6183 | 104.1063 | 1.684% | 16.2308 | 0.2625% | 120.3371 | 1.946% | 251 | 6166.7692 | 6062.6629 | 1.717% | 0.2677%
2017-07-19 | 6 | 6187 | 104.1234 | 1.683% | 16.2347 | 0.2624% | 120.3581 | 1.945% | 252 | 6170.7653 | 6066.6419 | 1.716% | 0.2676%
2017-07-11 | 4 | 6189 | 104.1319 | 1.683% | 16.2366 | 0.2623% | 120.3685 | 1.945% | 253 | 6172.7634 | 6068.6315 | 1.716% | 0.2676%
2017-07-04 | 3 | 6195 | 104.1574 | 1.681% | 16.2425 | 0.2622% | 120.3999 | 1.944% | 254 | 6178.7575 | 6074.6001 | 1.715% | 0.2674%
2017-07-16 | 5 | 6197 | 104.1659 | 1.681% | 16.2444 | 0.2621% | 120.4104 | 1.943% | 255 | 6180.7556 | 6076.5896 | 1.714% | 0.2673%
2017-06-22 | 3 | 6198 | 104.1702 | 1.681% | 16.2454 | 0.2621% | 120.4156 | 1.943% | 256 | 6181.7546 | 6077.5844 | 1.714% | 0.2673%
2017-08-31 | 2 | 6198 | 104.1702 | 1.681% | 16.2454 | 0.2621% | 120.4156 | 1.943% | 257 | 6181.7546 | 6077.5844 | 1.714% | 0.2673%
2017-07-05 | 4 | 6203 | 104.1915 | 1.68% | 16.2503 | 0.262% | 120.4417 | 1.942% | 258 | 6186.7497 | 6082.5583 | 1.713% | 0.2672%
2017-07-11 | 5 | 6207 | 104.2085 | 1.679% | 16.2542 | 0.2619% | 120.4627 | 1.941% | 259 | 6190.7458 | 6086.5373 | 1.712% | 0.2671%
2017-08-29 | 1 | 6208 | 104.2128 | 1.679% | 16.2551 | 0.2618% | 120.4679 | 1.941% | 260 | 6191.7449 | 6087.5321 | 1.712% | 0.267%
2017-06-18 | 3 | 6217 | 104.2511 | 1.677% | 16.2639 | 0.2616% | 120.515 | 1.938% | 261 | 6200.7361 | 6096.485 | 1.71% | 0.2668%
2017-07-09 | 3 | 6220 | 104.2639 | 1.676% | 16.2668 | 0.2615% | 120.5307 | 1.938% | 262 | 6203.7332 | 6099.4693 | 1.709% | 0.2667%
2017-08-03 | 6 | 6223 | 104.2766 | 1.676% | 16.2697 | 0.2614% | 120.5464 | 1.937% | 263 | 6206.7303 | 6102.4536 | 1.709% | 0.2666%
2017-08-20 | 6 | 6227 | 104.2937 | 1.675% | 16.2736 | 0.2613% | 120.5673 | 1.936% | 264 | 6210.7264 | 6106.4327 | 1.708% | 0.2665%
2017-07-06 | 5 | 6228 | 104.2979 | 1.675% | 16.2746 | 0.2613% | 120.5725 | 1.936% | 265 | 6211.7254 | 6107.4275 | 1.708% | 0.2665%
2017-06-17 | 3 | 6239 | 104.3447 | 1.672% | 16.2853 | 0.261% | 120.63 | 1.933% | 266 | 6222.7147 | 6118.37 | 1.705% | 0.2662%
2017-08-11 | 4 | 6240 | 104.349 | 1.672% | 16.2863 | 0.261% | 120.6353 | 1.933% | 267 | 6223.7137 | 6119.3647 | 1.705% | 0.2661%
2017-08-26 | 8 | 6241 | 104.3533 | 1.672% | 16.2872 | 0.261% | 120.6405 | 1.933% | 268 | 6224.7128 | 6120.3595 | 1.705% | 0.2661%
2017-08-20 | 5 | 6243 | 104.3618 | 1.672% | 16.2892 | 0.2609% | 120.651 | 1.933% | 269 | 6226.7108 | 6122.349 | 1.705% | 0.2661%
2017-06-23 | 4 | 6253 | 104.4043 | 1.67% | 16.2989 | 0.2607% | 120.7033 | 1.93% | 270 | 6236.7011 | 6132.2967 | 1.703% | 0.2658%
2017-07-31 | 8 | 6253 | 104.4043 | 1.67% | 16.2989 | 0.2607% | 120.7033 | 1.93% | 271 | 6236.7011 | 6132.2967 | 1.703% | 0.2658%
2017-08-02 | 7 | 6254 | 104.4086 | 1.669% | 16.2999 | 0.2606% | 120.7085 | 1.93% | 272 | 6237.7001 | 6133.2915 | 1.702% | 0.2658%
2017-07-01 | 3 | 6259 | 104.4299 | 1.668% | 16.3048 | 0.2605% | 120.7346 | 1.929% | 273 | 6242.6952 | 6138.2654 | 1.701% | 0.2656%
2017-08-25 | 3 | 6259 | 104.4299 | 1.668% | 16.3048 | 0.2605% | 120.7346 | 1.929% | 274 | 6242.6952 | 6138.2654 | 1.701% | 0.2656%
2017-08-11 | 5 | 6262 | 104.4426 | 1.668% | 16.3077 | 0.2604% | 120.7503 | 1.928% | 275 | 6245.6923 | 6141.2497 | 1.701% | 0.2655%
2017-08-20 | 7 | 6262 | 104.4426 | 1.668% | 16.3077 | 0.2604% | 120.7503 | 1.928% | 276 | 6245.6923 | 6141.2497 | 1.701% | 0.2655%
2017-06-04 | 1 | 6273 | 104.4895 | 1.666% | 16.3184 | 0.2601% | 120.8079 | 1.926% | 277 | 6256.6816 | 6152.1921 | 1.698% | 0.2652%
2017-06-08 | 9 | 6273 | 104.4895 | 1.666% | 16.3184 | 0.2601% | 120.8079 | 1.926% | 278 | 6256.6816 | 6152.1921 | 1.698% | 0.2652%
2017-06-05 | 6 | 6274 | 104.4937 | 1.666% | 16.3194 | 0.2601% | 120.8131 | 1.926% | 279 | 6257.6806 | 6153.1869 | 1.698% | 0.2652%
2017-06-03 | 9 | 6275 | 104.498 | 1.665% | 16.3203 | 0.2601% | 120.8183 | 1.925% | 280 | 6258.6797 | 6154.1817 | 1.698% | 0.2652%
2017-06-01 | 1 | 6278 | 104.5108 | 1.665% | 16.3232 | 0.26% | 120.834 | 1.925% | 281 | 6261.6768 | 6157.166 | 1.697% | 0.2651%
2017-07-04 | 8 | 6282 | 104.5278 | 1.664% | 16.3271 | 0.2599% | 120.8549 | 1.924% | 282 | 6265.6729 | 6161.1451 | 1.697% | 0.265%
2017-08-14 | 4 | 6284 | 104.5363 | 1.664% | 16.3291 | 0.2599% | 120.8654 | 1.923% | 283 | 6267.6709 | 6163.1346 | 1.696% | 0.2649%
2017-07-20 | 5 | 6286 | 104.5448 | 1.663% | 16.331 | 0.2598% | 120.8758 | 1.923% | 284 | 6269.669 | 6165.1242 | 1.696% | 0.2649%
2017-06-12 | 7 | 6287 | 104.5491 | 1.663% | 16.332 | 0.2598% | 120.8811 | 1.923% | 285 | 6270.668 | 6166.1189 | 1.696% | 0.2649%
2017-07-06 | 4 | 6294 | 104.5789 | 1.662% | 16.3388 | 0.2596% | 120.9177 | 1.921% | 286 | 6277.6612 | 6173.0823 | 1.694% | 0.2647%
2017-07-30 | 1 | 6302 | 104.6129 | 1.66% | 16.3466 | 0.2594% | 120.9595 | 1.919% | 287 | 6285.6534 | 6181.0405 | 1.692% | 0.2645%
2017-06-27 | 1 | 6304 | 104.6214 | 1.66% | 16.3486 | 0.2593% | 120.97 | 1.919% | 288 | 6287.6514 | 6183.03 | 1.692% | 0.2644%
2017-06-09 | 9 | 6306 | 104.63 | 1.659% | 16.3505 | 0.2593% | 120.9805 | 1.918% | 289 | 6289.6495 | 6185.0195 | 1.692% | 0.2644%
2017-07-10 | 3 | 6306 | 104.63 | 1.659% | 16.3505 | 0.2593% | 120.9805 | 1.918% | 290 | 6289.6495 | 6185.0195 | 1.692% | 0.2644%
2017-06-23 | 5 | 6307 | 104.6342 | 1.659% | 16.3515 | 0.2593% | 120.9857 | 1.918% | 291 | 6290.6485 | 6186.0143 | 1.691% | 0.2643%
2017-07-18 | 5 | 6311 | 104.6512 | 1.658% | 16.3554 | 0.2592% | 121.0066 | 1.917% | 292 | 6294.6446 | 6189.9934 | 1.691% | 0.2642%
2017-08-27 | 9 | 6311 | 104.6512 | 1.658% | 16.3554 | 0.2592% | 121.0066 | 1.917% | 293 | 6294.6446 | 6189.9934 | 1.691% | 0.2642%
2017-07-18 | 4 | 6312 | 104.6555 | 1.658% | 16.3563 | 0.2591% | 121.0118 | 1.917% | 294 | 6295.6437 | 6190.9882 | 1.69% | 0.2642%
2017-08-10 | 7 | 6313 | 104.6598 | 1.658% | 16.3573 | 0.2591% | 121.0171 | 1.917% | 295 | 6296.6427 | 6191.9829 | 1.69% | 0.2642%
2017-06-28 | 8 | 6317 | 104.6768 | 1.657% | 16.3612 | 0.259% | 121.038 | 1.916% | 296 | 6300.6388 | 6195.962 | 1.689% | 0.2641%
2017-08-31 | 6 | 6321 | 104.6938 | 1.656% | 16.3651 | 0.2589% | 121.0589 | 1.915% | 297 | 6304.6349 | 6199.9411 | 1.689% | 0.264%
2017-06-16 | 3 | 6323 | 104.7023 | 1.656% | 16.367 | 0.2588% | 121.0694 | 1.915% | 298 | 6306.633 | 6201.9306 | 1.688% | 0.2639%
2017-07-02 | 8 | 6325 | 104.7108 | 1.656% | 16.369 | 0.2588% | 121.0798 | 1.914% | 299 | 6308.631 | 6203.9202 | 1.688% | 0.2638%
2017-08-04 | 3 | 6328 | 104.7236 | 1.655% | 16.3719 | 0.2587% | 121.0955 | 1.914% | 300 | 6311.6281 | 6206.9045 | 1.687% | 0.2638%
2017-06-13 | 2 | 6332 | 104.7406 | 1.654% | 16.3758 | 0.2586% | 121.1164 | 1.913% | 301 | 6315.6242 | 6210.8836 | 1.686% | 0.2637%
2017-08-29 | 24 | 6335 | 104.7534 | 1.654% | 16.3787 | 0.2585% | 121.1321 | 1.912% | 302 | 6318.6213 | 6213.8679 | 1.686% | 0.2636%
2017-06-14 | 2 | 6336 | 104.7577 | 1.653% | 16.3797 | 0.2585% | 121.1374 | 1.912% | 303 | 6319.6203 | 6214.8626 | 1.686% | 0.2636%
2017-08-14 | 5 | 6336 | 104.7577 | 1.653% | 16.3797 | 0.2585% | 121.1374 | 1.912% | 304 | 6319.6203 | 6214.8626 | 1.686% | 0.2636%
2017-07-20 | 4 | 6337 | 104.7619 | 1.653% | 16.3807 | 0.2585% | 121.1426 | 1.912% | 305 | 6320.6193 | 6215.8574 | 1.685% | 0.2635%
2017-06-23 | 3 | 6338 | 104.7662 | 1.653% | 16.3816 | 0.2585% | 121.1478 | 1.911% | 306 | 6321.6184 | 6216.8522 | 1.685% | 0.2635%
2017-08-06 | 2 | 6341 | 104.7789 | 1.652% | 16.3846 | 0.2584% | 121.1635 | 1.911% | 307 | 6324.6154 | 6219.8365 | 1.685% | 0.2634%
2017-06-29 | 8 | 6342 | 104.7832 | 1.652% | 16.3855 | 0.2584% | 121.1687 | 1.911% | 308 | 6325.6145 | 6220.8313 | 1.684% | 0.2634%
2017-06-16 | 6 | 6345 | 104.796 | 1.652% | 16.3885 | 0.2583% | 121.1844 | 1.91% | 309 | 6328.6115 | 6223.8156 | 1.684% | 0.2633%
2017-07-05 | 6 | 6347 | 104.8045 | 1.651% | 16.3904 | 0.2582% | 121.1949 | 1.909% | 310 | 6330.6096 | 6225.8051 | 1.683% | 0.2633%
2017-08-10 | 1 | 6349 | 104.813 | 1.651% | 16.3923 | 0.2582% | 121.2053 | 1.909% | 311 | 6332.6077 | 6227.7947 | 1.683% | 0.2632%
2017-07-16 | 4 | 6350 | 104.8173 | 1.651% | 16.3933 | 0.2582% | 121.2106 | 1.909% | 312 | 6333.6067 | 6228.7894 | 1.683% | 0.2632%
2017-08-30 | 7 | 6351 | 104.8215 | 1.65% | 16.3943 | 0.2581% | 121.2158 | 1.909% | 313 | 6334.6057 | 6229.7842 | 1.683% | 0.2632%
2017-06-21 | 1 | 6354 | 104.8343 | 1.65% | 16.3972 | 0.2581% | 121.2315 | 1.908% | 314 | 6337.6028 | 6232.7685 | 1.682% | 0.2631%
2017-06-25 | 2 | 6359 | 104.8556 | 1.649% | 16.4021 | 0.2579% | 121.2576 | 1.907% | 315 | 6342.5979 | 6237.7424 | 1.681% | 0.2629%
2017-08-14 | 3 | 6365 | 104.8811 | 1.648% | 16.4079 | 0.2578% | 121.289 | 1.906% | 316 | 6348.5921 | 6243.711 | 1.68% | 0.2628%
2017-06-02 | 7 | 6368 | 104.8939 | 1.647% | 16.4108 | 0.2577% | 121.3047 | 1.905% | 317 | 6351.5892 | 6246.6953 | 1.679% | 0.2627%
2017-07-27 | 5 | 6368 | 104.8939 | 1.647% | 16.4108 | 0.2577% | 121.3047 | 1.905% | 318 | 6351.5892 | 6246.6953 | 1.679% | 0.2627%
2017-07-11 | 3 | 6374 | 104.9194 | 1.646% | 16.4167 | 0.2576% | 121.3361 | 1.904% | 319 | 6357.5833 | 6252.6639 | 1.678% | 0.2626%
2017-08-20 | 4 | 6374 | 104.9194 | 1.646% | 16.4167 | 0.2576% | 121.3361 | 1.904% | 320 | 6357.5833 | 6252.6639 | 1.678% | 0.2626%
2017-08-13 | 5 | 6375 | 104.9237 | 1.646% | 16.4176 | 0.2575% | 121.3413 | 1.903% | 321 | 6358.5824 | 6253.6587 | 1.678% | 0.2625%
2017-06-22 | 6 | 6376 | 104.9279 | 1.646% | 16.4186 | 0.2575% | 121.3466 | 1.903% | 322 | 6359.5814 | 6254.6534 | 1.678% | 0.2625%
2017-08-01 | 8 | 6377 | 104.9322 | 1.645% | 16.4196 | 0.2575% | 121.3518 | 1.903% | 323 | 6360.5804 | 6255.6482 | 1.677% | 0.2625%
2017-08-13 | 6 | 6380 | 104.945 | 1.645% | 16.4225 | 0.2574% | 121.3675 | 1.902% | 324 | 6363.5775 | 6258.6325 | 1.677% | 0.2624%
2017-08-27 | 24 | 6383 | 104.9577 | 1.644% | 16.4254 | 0.2573% | 121.3832 | 1.902% | 325 | 6366.5746 | 6261.6168 | 1.676% | 0.2623%
2017-06-15 | 6 | 6384 | 104.962 | 1.644% | 16.4264 | 0.2573% | 121.3884 | 1.901% | 326 | 6367.5736 | 6262.6116 | 1.676% | 0.2623%
2017-06-15 | 3 | 6387 | 104.9748 | 1.644% | 16.4293 | 0.2572% | 121.4041 | 1.901% | 327 | 6370.5707 | 6265.5959 | 1.675% | 0.2622%
2017-06-30 | 7 | 6387 | 104.9748 | 1.644% | 16.4293 | 0.2572% | 121.4041 | 1.901% | 328 | 6370.5707 | 6265.5959 | 1.675% | 0.2622%
2017-08-25 | 6 | 6389 | 104.9833 | 1.643% | 16.4313 | 0.2572% | 121.4146 | 1.9% | 329 | 6372.5687 | 6267.5854 | 1.675% | 0.2622%
2017-06-04 | 9 | 6395 | 105.0088 | 1.642% | 16.4371 | 0.257% | 121.4459 | 1.899% | 330 | 6378.5629 | 6273.5541 | 1.674% | 0.262%
2017-07-02 | 3 | 6395 | 105.0088 | 1.642% | 16.4371 | 0.257% | 121.4459 | 1.899% | 331 | 6378.5629 | 6273.5541 | 1.674% | 0.262%
2017-06-13 | 7 | 6398 | 105.0216 | 1.641% | 16.44 | 0.257% | 121.4616 | 1.898% | 332 | 6381.56 | 6276.5384 | 1.673% | 0.2619%
2017-06-30 | 2 | 6398 | 105.0216 | 1.641% | 16.44 | 0.257% | 121.4616 | 1.898% | 333 | 6381.56 | 6276.5384 | 1.673% | 0.2619%
2017-06-02 | 1 | 6400 | 105.0301 | 1.641% | 16.442 | 0.2569% | 121.4721 | 1.898% | 334 | 6383.558 | 6278.5279 | 1.673% | 0.2619%
2017-06-07 | 7 | 6401 | 105.0344 | 1.641% | 16.4429 | 0.2569% | 121.4773 | 1.898% | 335 | 6384.5571 | 6279.5227 | 1.673% | 0.2619%
2017-07-03 | 5 | 6403 | 105.0429 | 1.641% | 16.4449 | 0.2568% | 121.4878 | 1.897% | 336 | 6386.5551 | 6281.5122 | 1.672% | 0.2618%
2017-07-06 | 6 | 6405 | 105.0514 | 1.64% | 16.4468 | 0.2568% | 121.4982 | 1.897% | 337 | 6388.5532 | 6283.5018 | 1.672% | 0.2617%
2017-06-06 | 1 | 6407 | 105.0599 | 1.64% | 16.4488 | 0.2567% | 121.5087 | 1.896% | 338 | 6390.5512 | 6285.4913 | 1.671% | 0.2617%
2017-08-05 | 6 | 6407 | 105.0599 | 1.64% | 16.4488 | 0.2567% | 121.5087 | 1.896% | 339 | 6390.5512 | 6285.4913 | 1.671% | 0.2617%
2017-07-01 | 8 | 6409 | 105.0684 | 1.639% | 16.4507 | 0.2567% | 121.5192 | 1.896% | 340 | 6392.5493 | 6287.4808 | 1.671% | 0.2616%
2017-08-04 | 6 | 6409 | 105.0684 | 1.639% | 16.4507 | 0.2567% | 121.5192 | 1.896% | 341 | 6392.5493 | 6287.4808 | 1.671% | 0.2616%
2017-08-11 | 3 | 6411 | 105.0769 | 1.639% | 16.4527 | 0.2566% | 121.5296 | 1.896% | 342 | 6394.5473 | 6289.4704 | 1.671% | 0.2616%
2017-06-07 | 1 | 6414 | 105.0897 | 1.638% | 16.4556 | 0.2566% | 121.5453 | 1.895% | 343 | 6397.5444 | 6292.4547 | 1.67% | 0.2615%
2017-07-05 | 3 | 6414 | 105.0897 | 1.638% | 16.4556 | 0.2566% | 121.5453 | 1.895% | 344 | 6397.5444 | 6292.4547 | 1.67% | 0.2615%
2017-07-27 | 4 | 6415 | 105.094 | 1.638% | 16.4566 | 0.2565% | 121.5505 | 1.895% | 345 | 6398.5434 | 6293.4495 | 1.67% | 0.2615%
2017-08-05 | 5 | 6415 | 105.094 | 1.638% | 16.4566 | 0.2565% | 121.5505 | 1.895% | 346 | 6398.5434 | 6293.4495 | 1.67% | 0.2615%
2017-06-14 | 7 | 6424 | 105.1323 | 1.637% | 16.4653 | 0.2563% | 121.5976 | 1.893% | 347 | 6407.5347 | 6302.4024 | 1.668% | 0.2613%
2017-06-18 | 8 | 6424 | 105.1323 | 1.637% | 16.4653 | 0.2563% | 121.5976 | 1.893% | 348 | 6407.5347 | 6302.4024 | 1.668% | 0.2613%
2017-08-09 | 1 | 6424 | 105.1323 | 1.637% | 16.4653 | 0.2563% | 121.5976 | 1.893% | 349 | 6407.5347 | 6302.4024 | 1.668% | 0.2613%
2017-07-17 | 6 | 6425 | 105.1365 | 1.636% | 16.4663 | 0.2563% | 121.6028 | 1.893% | 350 | 6408.5337 | 6303.3972 | 1.668% | 0.2612%
2017-06-26 | 1 | 6431 | 105.1621 | 1.635% | 16.4721 | 0.2561% | 121.6342 | 1.891% | 351 | 6414.5279 | 6309.3658 | 1.667% | 0.2611%
2017-06-08 | 10 | 6432 | 105.1663 | 1.635% | 16.4731 | 0.2561% | 121.6394 | 1.891% | 352 | 6415.5269 | 6310.3606 | 1.667% | 0.261%
2017-07-10 | 6 | 6432 | 105.1663 | 1.635% | 16.4731 | 0.2561% | 121.6394 | 1.891% | 353 | 6415.5269 | 6310.3606 | 1.667% | 0.261%
2017-08-13 | 7 | 6437 | 105.1876 | 1.634% | 16.478 | 0.256% | 121.6656 | 1.89% | 354 | 6420.522 | 6315.3344 | 1.666% | 0.2609%
2017-08-27 | 1 | 6437 | 105.1876 | 1.634% | 16.478 | 0.256% | 121.6656 | 1.89% | 355 | 6420.522 | 6315.3344 | 1.666% | 0.2609%
2017-08-07 | 4 | 6438 | 105.1919 | 1.634% | 16.479 | 0.256% | 121.6708 | 1.89% | 356 | 6421.521 | 6316.3292 | 1.665% | 0.2609%
2017-08-03 | 2 | 6440 | 105.2004 | 1.634% | 16.4809 | 0.2559% | 121.6813 | 1.889% | 357 | 6423.5191 | 6318.3187 | 1.665% | 0.2608%
2017-06-01 | 7 | 6441 | 105.2046 | 1.633% | 16.4819 | 0.2559% | 121.6865 | 1.889% | 358 | 6424.5181 | 6319.3135 | 1.665% | 0.2608%
2017-07-17 | 2 | 6441 | 105.2046 | 1.633% | 16.4819 | 0.2559% | 121.6865 | 1.889% | 359 | 6424.5181 | 6319.3135 | 1.665% | 0.2608%
2017-06-11 | 1 | 6443 | 105.2132 | 1.633% | 16.4838 | 0.2558% | 121.697 | 1.889% | 360 | 6426.5162 | 6321.303 | 1.664% | 0.2608%
2017-06-08 | 23 | 6448 | 105.2344 | 1.632% | 16.4887 | 0.2557% | 121.7231 | 1.888% | 361 | 6431.5113 | 6326.2769 | 1.663% | 0.2606%
2017-08-05 | 7 | 6454 | 105.26 | 1.631% | 16.4945 | 0.2556% | 121.7545 | 1.886% | 362 | 6437.5055 | 6332.2455 | 1.662% | 0.2605%
2017-06-22 | 2 | 6455 | 105.2642 | 1.631% | 16.4955 | 0.2555% | 121.7597 | 1.886% | 363 | 6438.5045 | 6333.2403 | 1.662% | 0.2605%
2017-08-26 | 2 | 6458 | 105.277 | 1.63% | 16.4984 | 0.2555% | 121.7754 | 1.886% | 364 | 6441.5016 | 6336.2246 | 1.662% | 0.2604%
2017-08-28 | 7 | 6460 | 105.2855 | 1.63% | 16.5004 | 0.2554% | 121.7859 | 1.885% | 365 | 6443.4996 | 6338.2141 | 1.661% | 0.2603%
2017-08-20 | 8 | 6469 | 105.3238 | 1.628% | 16.5091 | 0.2552% | 121.833 | 1.883% | 366 | 6452.4909 | 6347.167 | 1.659% | 0.2601%
2017-06-20 | 5 | 6472 | 105.3366 | 1.628% | 16.512 | 0.2551% | 121.8487 | 1.883% | 367 | 6455.488 | 6350.1513 | 1.659% | 0.26%
2017-08-13 | 4 | 6473 | 105.3409 | 1.627% | 16.513 | 0.2551% | 121.8539 | 1.882% | 368 | 6456.487 | 6351.1461 | 1.659% | 0.26%
2017-07-03 | 4 | 6475 | 105.3494 | 1.627% | 16.515 | 0.2551% | 121.8643 | 1.882% | 369 | 6458.485 | 6353.1357 | 1.658% | 0.2599%
2017-07-16 | 8 | 6475 | 105.3494 | 1.627% | 16.515 | 0.2551% | 121.8643 | 1.882% | 370 | 6458.485 | 6353.1357 | 1.658% | 0.2599%
2017-07-24 | 4 | 6477 | 105.3579 | 1.627% | 16.5169 | 0.255% | 121.8748 | 1.882% | 371 | 6460.4831 | 6355.1252 | 1.658% | 0.2599%
2017-06-11 | 9 | 6482 | 105.3792 | 1.626% | 16.5218 | 0.2549% | 121.901 | 1.881% | 372 | 6465.4782 | 6360.099 | 1.657% | 0.2598%
2017-06-20 | 4 | 6486 | 105.3962 | 1.625% | 16.5257 | 0.2548% | 121.9219 | 1.88% | 373 | 6469.4743 | 6364.0781 | 1.656% | 0.2597%
2017-07-04 | 2 | 6491 | 105.4175 | 1.624% | 16.5305 | 0.2547% | 121.948 | 1.879% | 374 | 6474.4695 | 6369.052 | 1.655% | 0.2595%
2017-08-07 | 5 | 6491 | 105.4175 | 1.624% | 16.5305 | 0.2547% | 121.948 | 1.879% | 375 | 6474.4695 | 6369.052 | 1.655% | 0.2595%
2017-07-18 | 3 | 6495 | 105.4345 | 1.623% | 16.5344 | 0.2546% | 121.9689 | 1.878% | 376 | 6478.4656 | 6373.0311 | 1.654% | 0.2594%
2017-06-18 | 2 | 6496 | 105.4388 | 1.623% | 16.5354 | 0.2545% | 121.9742 | 1.878% | 377 | 6479.4646 | 6374.0258 | 1.654% | 0.2594%
2017-07-19 | 2 | 6500 | 105.4558 | 1.622% | 16.5393 | 0.2545% | 121.9951 | 1.877% | 378 | 6483.4607 | 6378.0049 | 1.653% | 0.2593%
2017-07-11 | 6 | 6502 | 105.4643 | 1.622% | 16.5412 | 0.2544% | 122.0056 | 1.876% | 379 | 6485.4588 | 6379.9944 | 1.653% | 0.2593%
2017-08-02 | 1 | 6504 | 105.4728 | 1.622% | 16.5432 | 0.2544% | 122.016 | 1.876% | 380 | 6487.4568 | 6381.984 | 1.653% | 0.2592%
2017-07-24 | 5 | 6509 | 105.4941 | 1.621% | 16.548 | 0.2542% | 122.0422 | 1.875% | 381 | 6492.452 | 6386.9578 | 1.652% | 0.2591%
2017-06-05 | 1 | 6510 | 105.4984 | 1.621% | 16.549 | 0.2542% | 122.0474 | 1.875% | 382 | 6493.451 | 6387.9526 | 1.652% | 0.2591%
2017-07-20 | 6 | 6511 | 105.5026 | 1.62% | 16.55 | 0.2542% | 122.0526 | 1.875% | 383 | 6494.45 | 6388.9474 | 1.651% | 0.259%
2017-07-19 | 7 | 6514 | 105.5154 | 1.62% | 16.5529 | 0.2541% | 122.0683 | 1.874% | 384 | 6497.4471 | 6391.9317 | 1.651% | 0.259%
2017-07-30 | 24 | 6519 | 105.5367 | 1.619% | 16.5578 | 0.254% | 122.0945 | 1.873% | 385 | 6502.4422 | 6396.9055 | 1.65% | 0.2588%
2017-08-11 | 6 | 6520 | 105.5409 | 1.619% | 16.5588 | 0.254% | 122.0997 | 1.873% | 386 | 6503.4412 | 6397.9003 | 1.65% | 0.2588%
2017-06-19 | 4 | 6523 | 105.5537 | 1.618% | 16.5617 | 0.2539% | 122.1154 | 1.872% | 387 | 6506.4383 | 6400.8846 | 1.649% | 0.2587%
2017-08-31 | 1 | 6523 | 105.5537 | 1.618% | 16.5617 | 0.2539% | 122.1154 | 1.872% | 388 | 6506.4383 | 6400.8846 | 1.649% | 0.2587%
2017-08-25 | 2 | 6524 | 105.558 | 1.618% | 16.5626 | 0.2539% | 122.1206 | 1.872% | 389 | 6507.4374 | 6401.8794 | 1.649% | 0.2587%
2017-07-03 | 6 | 6530 | 105.5835 | 1.617% | 16.5685 | 0.2537% | 122.152 | 1.871% | 390 | 6513.4315 | 6407.848 | 1.648% | 0.2586%
2017-06-17 | 8 | 6534 | 105.6005 | 1.616% | 16.5724 | 0.2536% | 122.1729 | 1.87% | 391 | 6517.4276 | 6411.8271 | 1.647% | 0.2585%
2017-06-19 | 5 | 6535 | 105.6048 | 1.616% | 16.5734 | 0.2536% | 122.1781 | 1.87% | 392 | 6518.4266 | 6412.8219 | 1.647% | 0.2584%
2017-06-27 | 8 | 6535 | 105.6048 | 1.616% | 16.5734 | 0.2536% | 122.1781 | 1.87% | 393 | 6518.4266 | 6412.8219 | 1.647% | 0.2584%
2017-08-24 | 5 | 6537 | 105.6133 | 1.616% | 16.5753 | 0.2536% | 122.1886 | 1.869% | 394 | 6520.4247 | 6414.8114 | 1.646% | 0.2584%
2017-08-06 | 9 | 6544 | 105.6431 | 1.614% | 16.5821 | 0.2534% | 122.2252 | 1.868% | 395 | 6527.4179 | 6421.7748 | 1.645% | 0.2582%
2017-06-09 | 24 | 6551 | 105.6729 | 1.613% | 16.5889 | 0.2532% | 122.2618 | 1.866% | 396 | 6534.4111 | 6428.7382 | 1.644% | 0.258%
2017-08-30 | 8 | 6557 | 105.6985 | 1.612% | 16.5948 | 0.2531% | 122.2932 | 1.865% | 397 | 6540.4052 | 6434.7068 | 1.643% | 0.2579%
2017-06-12 | 1 | 6558 | 105.7027 | 1.612% | 16.5957 | 0.2531% | 122.2984 | 1.865% | 398 | 6541.4043 | 6435.7016 | 1.642% | 0.2579%
2017-08-24 | 4 | 6558 | 105.7027 | 1.612% | 16.5957 | 0.2531% | 122.2984 | 1.865% | 399 | 6541.4043 | 6435.7016 | 1.642% | 0.2579%
2017-08-14 | 2 | 6559 | 105.707 | 1.612% | 16.5967 | 0.253% | 122.3037 | 1.865% | 400 | 6542.4033 | 6436.6963 | 1.642% | 0.2578%
2017-06-17 | 2 | 6560 | 105.7112 | 1.611% | 16.5977 | 0.253% | 122.3089 | 1.864% | 401 | 6543.4023 | 6437.6911 | 1.642% | 0.2578%
2017-08-07 | 3 | 6560 | 105.7112 | 1.611% | 16.5977 | 0.253% | 122.3089 | 1.864% | 402 | 6543.4023 | 6437.6911 | 1.642% | 0.2578%
2017-06-06 | 7 | 6561 | 105.7155 | 1.611% | 16.5987 | 0.253% | 122.3141 | 1.864% | 403 | 6544.4013 | 6438.6859 | 1.642% | 0.2578%
2017-06-08 | 11 | 6564 | 105.7283 | 1.611% | 16.6016 | 0.2529% | 122.3298 | 1.864% | 404 | 6547.3984 | 6441.6702 | 1.641% | 0.2577%
2017-07-01 | 2 | 6565 | 105.7325 | 1.611% | 16.6025 | 0.2529% | 122.3351 | 1.863% | 405 | 6548.3975 | 6442.6649 | 1.641% | 0.2577%
2017-08-05 | 4 | 6565 | 105.7325 | 1.611% | 16.6025 | 0.2529% | 122.3351 | 1.863% | 406 | 6548.3975 | 6442.6649 | 1.641% | 0.2577%
2017-06-23 | 2 | 6567 | 105.741 | 1.61% | 16.6045 | 0.2528% | 122.3455 | 1.863% | 407 | 6550.3955 | 6444.6545 | 1.641% | 0.2576%
2017-08-12 | 5 | 6569 | 105.7495 | 1.61% | 16.6064 | 0.2528% | 122.356 | 1.863% | 408 | 6552.3936 | 6446.644 | 1.64% | 0.2576%
2017-06-21 | 7 | 6570 | 105.7538 | 1.61% | 16.6074 | 0.2528% | 122.3612 | 1.862% | 409 | 6553.3926 | 6447.6388 | 1.64% | 0.2576%
2017-07-06 | 3 | 6575 | 105.7751 | 1.609% | 16.6123 | 0.2527% | 122.3874 | 1.861% | 410 | 6558.3877 | 6452.6126 | 1.639% | 0.2575%
2017-07-20 | 3 | 6581 | 105.8006 | 1.608% | 16.6181 | 0.2525% | 122.4187 | 1.86% | 411 | 6564.3819 | 6458.5813 | 1.638% | 0.2573%
2017-07-27 | 6 | 6582 | 105.8049 | 1.607% | 16.6191 | 0.2525% | 122.424 | 1.86% | 412 | 6565.3809 | 6459.576 | 1.638% | 0.2573%
2017-07-09 | 2 | 6586 | 105.8219 | 1.607% | 16.623 | 0.2524% | 122.4449 | 1.859% | 413 | 6569.377 | 6463.5551 | 1.637% | 0.2572%
2017-08-11 | 2 | 6590 | 105.8389 | 1.606% | 16.6269 | 0.2523% | 122.4658 | 1.858% | 414 | 6573.3731 | 6467.5342 | 1.636% | 0.2571%
2017-08-22 | 4 | 6595 | 105.8602 | 1.605% | 16.6317 | 0.2522% | 122.492 | 1.857% | 415 | 6578.3683 | 6472.508 | 1.636% | 0.257%
2017-08-12 | 6 | 6596 | 105.8645 | 1.605% | 16.6327 | 0.2522% | 122.4972 | 1.857% | 416 | 6579.3673 | 6473.5028 | 1.635% | 0.2569%
2017-08-22 | 5 | 6598 | 105.873 | 1.605% | 16.6347 | 0.2521% | 122.5076 | 1.857% | 417 | 6581.3653 | 6475.4924 | 1.635% | 0.2569%
2017-07-10 | 2 | 6599 | 105.8772 | 1.604% | 16.6356 | 0.2521% | 122.5129 | 1.857% | 418 | 6582.3644 | 6476.4871 | 1.635% | 0.2569%
2017-06-09 | 10 | 6600 | 105.8815 | 1.604% | 16.6366 | 0.2521% | 122.5181 | 1.856% | 419 | 6583.3634 | 6477.4819 | 1.635% | 0.2568%
2017-07-16 | 3 | 6601 | 105.8858 | 1.604% | 16.6376 | 0.252% | 122.5233 | 1.856% | 420 | 6584.3624 | 6478.4767 | 1.634% | 0.2568%
2017-07-18 | 6 | 6601 | 105.8858 | 1.604% | 16.6376 | 0.252% | 122.5233 | 1.856% | 421 | 6584.3624 | 6478.4767 | 1.634% | 0.2568%
2017-08-21 | 5 | 6608 | 105.9156 | 1.603% | 16.6444 | 0.2519% | 122.5599 | 1.855% | 422 | 6591.3556 | 6485.4401 | 1.633% | 0.2566%
2017-08-09 | 7 | 6610 | 105.9241 | 1.602% | 16.6463 | 0.2518% | 122.5704 | 1.854% | 423 | 6593.3537 | 6487.4296 | 1.633% | 0.2566%
2017-08-20 | 3 | 6612 | 105.9326 | 1.602% | 16.6483 | 0.2518% | 122.5809 | 1.854% | 424 | 6595.3517 | 6489.4191 | 1.632% | 0.2565%
2017-08-05 | 8 | 6617 | 105.9539 | 1.601% | 16.6531 | 0.2517% | 122.607 | 1.853% | 425 | 6600.3469 | 6494.393 | 1.631% | 0.2564%
2017-06-23 | 6 | 6625 | 105.9879 | 1.6% | 16.6609 | 0.2515% | 122.6489 | 1.851% | 426 | 6608.3391 | 6502.3511 | 1.63% | 0.2562%
2017-08-21 | 4 | 6627 | 105.9964 | 1.599% | 16.6629 | 0.2514% | 122.6593 | 1.851% | 427 | 6610.3371 | 6504.3407 | 1.63% | 0.2562%
2017-06-26 | 8 | 6631 | 106.0135 | 1.599% | 16.6668 | 0.2513% | 122.6802 | 1.85% | 428 | 6614.3332 | 6508.3198 | 1.629% | 0.2561%
2017-07-08 | 6 | 6632 | 106.0177 | 1.599% | 16.6677 | 0.2513% | 122.6855 | 1.85% | 429 | 6615.3323 | 6509.3145 | 1.629% | 0.2561%
2017-07-11 | 2 | 6632 | 106.0177 | 1.599% | 16.6677 | 0.2513% | 122.6855 | 1.85% | 430 | 6615.3323 | 6509.3145 | 1.629% | 0.2561%
2017-06-08 | 12 | 6634 | 106.0262 | 1.598% | 16.6697 | 0.2513% | 122.6959 | 1.85% | 431 | 6617.3303 | 6511.3041 | 1.628% | 0.256%
2017-07-05 | 7 | 6635 | 106.0305 | 1.598% | 16.6707 | 0.2513% | 122.7012 | 1.849% | 432 | 6618.3293 | 6512.2988 | 1.628% | 0.256%
2017-07-24 | 3 | 6636 | 106.0348 | 1.598% | 16.6716 | 0.2512% | 122.7064 | 1.849% | 433 | 6619.3284 | 6513.2936 | 1.628% | 0.256%
2017-08-12 | 4 | 6636 | 106.0348 | 1.598% | 16.6716 | 0.2512% | 122.7064 | 1.849% | 434 | 6619.3284 | 6513.2936 | 1.628% | 0.256%
2017-08-04 | 2 | 6638 | 106.0433 | 1.598% | 16.6736 | 0.2512% | 122.7169 | 1.849% | 435 | 6621.3264 | 6515.2831 | 1.628% | 0.2559%
2017-07-08 | 5 | 6648 | 106.0858 | 1.596% | 16.6833 | 0.251% | 122.7692 | 1.847% | 436 | 6631.3167 | 6525.2308 | 1.626% | 0.2557%
2017-07-08 | 7 | 6649 | 106.0901 | 1.596% | 16.6843 | 0.2509% | 122.7744 | 1.847% | 437 | 6632.3157 | 6526.2256 | 1.626% | 0.2556%
2017-08-13 | 8 | 6650 | 106.0943 | 1.595% | 16.6853 | 0.2509% | 122.7796 | 1.846% | 438 | 6633.3147 | 6527.2204 | 1.625% | 0.2556%
2017-06-07 | 23 | 6663 | 106.1497 | 1.593% | 16.6979 | 0.2506% | 122.8476 | 1.844% | 439 | 6646.3021 | 6540.1524 | 1.623% | 0.2553%
2017-08-02 | 8 | 6663 | 106.1497 | 1.593% | 16.6979 | 0.2506% | 122.8476 | 1.844% | 440 | 6646.3021 | 6540.1524 | 1.623% | 0.2553%
2017-08-13 | 3 | 6663 | 106.1497 | 1.593% | 16.6979 | 0.2506% | 122.8476 | 1.844% | 441 | 6646.3021 | 6540.1524 | 1.623% | 0.2553%
2017-07-27 | 3 | 6666 | 106.1625 | 1.593% | 16.7008 | 0.2505% | 122.8633 | 1.843% | 442 | 6649.2992 | 6543.1367 | 1.623% | 0.2552%
2017-06-16 | 2 | 6667 | 106.1667 | 1.592% | 16.7018 | 0.2505% | 122.8685 | 1.843% | 443 | 6650.2982 | 6544.1315 | 1.622% | 0.2552%
2017-08-03 | 7 | 6670 | 106.1795 | 1.592% | 16.7047 | 0.2504% | 122.8842 | 1.842% | 444 | 6653.2953 | 6547.1158 | 1.622% | 0.2551%
2017-08-14 | 6 | 6675 | 106.2008 | 1.591% | 16.7096 | 0.2503% | 122.9104 | 1.841% | 445 | 6658.2904 | 6552.0896 | 1.621% | 0.255%
2017-08-28 | 24 | 6676 | 106.205 | 1.591% | 16.7106 | 0.2503% | 122.9156 | 1.841% | 446 | 6659.2894 | 6553.0844 | 1.621% | 0.255%
2017-06-16 | 7 | 6677 | 106.2093 | 1.591% | 16.7115 | 0.2503% | 122.9208 | 1.841% | 447 | 6660.2885 | 6554.0792 | 1.621% | 0.255%
2017-06-20 | 6 | 6677 | 106.2093 | 1.591% | 16.7115 | 0.2503% | 122.9208 | 1.841% | 448 | 6660.2885 | 6554.0792 | 1.621% | 0.255%
2017-06-19 | 3 | 6678 | 106.2135 | 1.59% | 16.7125 | 0.2503% | 122.9261 | 1.841% | 449 | 6661.2875 | 6555.0739 | 1.62% | 0.255%
2017-08-28 | 8 | 6679 | 106.2178 | 1.59% | 16.7135 | 0.2502% | 122.9313 | 1.841% | 450 | 6662.2865 | 6556.0687 | 1.62% | 0.2549%
2017-08-24 | 3 | 6683 | 106.2348 | 1.59% | 16.7174 | 0.2501% | 122.9522 | 1.84% | 451 | 6666.2826 | 6560.0478 | 1.619% | 0.2548%
2017-07-03 | 7 | 6688 | 106.2561 | 1.589% | 16.7222 | 0.25% | 122.9784 | 1.839% | 452 | 6671.2778 | 6565.0216 | 1.619% | 0.2547%
2017-07-03 | 3 | 6691 | 106.2689 | 1.588% | 16.7252 | 0.25% | 122.994 | 1.838% | 453 | 6674.2748 | 6568.006 | 1.618% | 0.2546%
2017-06-15 | 2 | 6694 | 106.2817 | 1.588% | 16.7281 | 0.2499% | 123.0097 | 1.838% | 454 | 6677.2719 | 6570.9903 | 1.617% | 0.2546%
2017-08-12 | 7 | 6695 | 106.2859 | 1.588% | 16.7291 | 0.2499% | 123.015 | 1.837% | 455 | 6678.2709 | 6571.985 | 1.617% | 0.2546%
2017-08-10 | 8 | 6706 | 106.3327 | 1.586% | 16.7398 | 0.2496% | 123.0725 | 1.835% | 456 | 6689.2602 | 6582.9275 | 1.615% | 0.2543%
2017-06-20 | 3 | 6711 | 106.354 | 1.585% | 16.7446 | 0.2495% | 123.0987 | 1.834% | 457 | 6694.2554 | 6587.9013 | 1.614% | 0.2542%
2017-07-31 | 9 | 6718 | 106.3838 | 1.584% | 16.7514 | 0.2494% | 123.1353 | 1.833% | 458 | 6701.2486 | 6594.8647 | 1.613% | 0.254%
2017-07-06 | 7 | 6719 | 106.3881 | 1.583% | 16.7524 | 0.2493% | 123.1405 | 1.833% | 459 | 6702.2476 | 6595.8595 | 1.613% | 0.254%
2017-07-02 | 2 | 6722 | 106.4009 | 1.583% | 16.7553 | 0.2493% | 123.1562 | 1.832% | 460 | 6705.2447 | 6598.8438 | 1.612% | 0.2539%
2017-06-07 | 8 | 6724 | 106.4094 | 1.583% | 16.7573 | 0.2492% | 123.1666 | 1.832% | 461 | 6707.2427 | 6600.8334 | 1.612% | 0.2539%
2017-08-30 | 9 | 6728 | 106.4264 | 1.582% | 16.7612 | 0.2491% | 123.1876 | 1.831% | 462 | 6711.2388 | 6604.8124 | 1.611% | 0.2538%
2017-06-08 | 13 | 6738 | 106.469 | 1.58% | 16.7709 | 0.2489% | 123.2399 | 1.829% | 463 | 6721.2291 | 6614.7601 | 1.61% | 0.2535%
2017-07-26 | 5 | 6744 | 106.4945 | 1.579% | 16.7767 | 0.2488% | 123.2712 | 1.828% | 464 | 6727.2233 | 6620.7288 | 1.609% | 0.2534%
2017-08-29 | 7 | 6750 | 106.52 | 1.578% | 16.7826 | 0.2486% | 123.3026 | 1.827% | 465 | 6733.2174 | 6626.6974 | 1.607% | 0.2533%
2017-07-08 | 4 | 6754 | 106.5371 | 1.577% | 16.7865 | 0.2485% | 123.3235 | 1.826% | 466 | 6737.2135 | 6630.6765 | 1.607% | 0.2532%
2017-06-15 | 7 | 6763 | 106.5754 | 1.576% | 16.7952 | 0.2483% | 123.3706 | 1.824% | 467 | 6746.2048 | 6639.6294 | 1.605% | 0.253%
2017-06-14 | 1 | 6765 | 106.5839 | 1.576% | 16.7972 | 0.2483% | 123.3811 | 1.824% | 468 | 6748.2028 | 6641.6189 | 1.605% | 0.2529%
2017-07-18 | 2 | 6770 | 106.6052 | 1.575% | 16.802 | 0.2482% | 123.4072 | 1.823% | 469 | 6753.198 | 6646.5928 | 1.604% | 0.2528%
2017-07-05 | 2 | 6771 | 106.6094 | 1.575% | 16.803 | 0.2482% | 123.4125 | 1.823% | 470 | 6754.197 | 6647.5875 | 1.604% | 0.2528%
2017-06-25 | 1 | 6773 | 106.618 | 1.574% | 16.805 | 0.2481% | 123.4229 | 1.822% | 471 | 6756.195 | 6649.5771 | 1.603% | 0.2527%
2017-07-29 | 5 | 6787 | 106.6776 | 1.572% | 16.8186 | 0.2478% | 123.4961 | 1.82% | 472 | 6770.1814 | 6663.5039 | 1.601% | 0.2524%
2017-07-24 | 6 | 6790 | 106.6903 | 1.571% | 16.8215 | 0.2477% | 123.5118 | 1.819% | 473 | 6773.1785 | 6666.4882 | 1.6% | 0.2523%
2017-07-10 | 7 | 6792 | 106.6988 | 1.571% | 16.8235 | 0.2477% | 123.5223 | 1.819% | 474 | 6775.1765 | 6668.4777 | 1.6% | 0.2523%
2017-07-26 | 4 | 6793 | 106.7031 | 1.571% | 16.8244 | 0.2477% | 123.5275 | 1.818% | 475 | 6776.1756 | 6669.4725 | 1.6% | 0.2523%
2017-06-02 | 8 | 6795 | 106.7116 | 1.57% | 16.8264 | 0.2476% | 123.538 | 1.818% | 476 | 6778.1736 | 6671.462 | 1.6% | 0.2522%
2017-06-27 | 24 | 6798 | 106.7244 | 1.57% | 16.8293 | 0.2476% | 123.5537 | 1.818% | 477 | 6781.1707 | 6674.4463 | 1.599% | 0.2521%
2017-06-28 | 9 | 6801 | 106.7372 | 1.569% | 16.8322 | 0.2475% | 123.5694 | 1.817% | 478 | 6784.1678 | 6677.4306 | 1.598% | 0.2521%
2017-08-12 | 3 | 6802 | 106.7414 | 1.569% | 16.8332 | 0.2475% | 123.5746 | 1.817% | 479 | 6785.1668 | 6678.4254 | 1.598% | 0.2521%
2017-08-22 | 3 | 6802 | 106.7414 | 1.569% | 16.8332 | 0.2475% | 123.5746 | 1.817% | 480 | 6785.1668 | 6678.4254 | 1.598% | 0.2521%
2017-06-13 | 1 | 6803 | 106.7457 | 1.569% | 16.8342 | 0.2475% | 123.5798 | 1.817% | 481 | 6786.1658 | 6679.4202 | 1.598% | 0.252%
2017-08-16 | 5 | 6804 | 106.7499 | 1.569% | 16.8351 | 0.2474% | 123.5851 | 1.816% | 482 | 6787.1649 | 6680.4149 | 1.598% | 0.252%
2017-07-17 | 1 | 6807 | 106.7627 | 1.568% | 16.8381 | 0.2474% | 123.6007 | 1.816% | 483 | 6790.1619 | 6683.3993 | 1.597% | 0.2519%
2017-08-07 | 6 | 6811 | 106.7797 | 1.568% | 16.8419 | 0.2473% | 123.6217 | 1.815% | 484 | 6794.1581 | 6687.3783 | 1.597% | 0.2518%
2017-07-20 | 7 | 6815 | 106.7967 | 1.567% | 16.8458 | 0.2472% | 123.6426 | 1.814% | 485 | 6798.1542 | 6691.3574 | 1.596% | 0.2518%
2017-06-22 | 1 | 6816 | 106.801 | 1.567% | 16.8468 | 0.2472% | 123.6478 | 1.814% | 486 | 6799.1532 | 6692.3522 | 1.596% | 0.2517%
2017-08-04 | 7 | 6821 | 106.8223 | 1.566% | 16.8517 | 0.2471% | 123.674 | 1.813% | 487 | 6804.1483 | 6697.326 | 1.595% | 0.2516%
2017-06-22 | 7 | 6823 | 106.8308 | 1.566% | 16.8536 | 0.247% | 123.6844 | 1.813% | 488 | 6806.1464 | 6699.3156 | 1.595% | 0.2516%
2017-08-21 | 3 | 6824 | 106.8351 | 1.566% | 16.8546 | 0.247% | 123.6897 | 1.813% | 489 | 6807.1454 | 6700.3103 | 1.594% | 0.2515%
2017-08-05 | 3 | 6825 | 106.8393 | 1.565% | 16.8556 | 0.247% | 123.6949 | 1.812% | 490 | 6808.1444 | 6701.3051 | 1.594% | 0.2515%
2017-06-25 | 9 | 6827 | 106.8478 | 1.565% | 16.8575 | 0.2469% | 123.7053 | 1.812% | 491 | 6810.1425 | 6703.2947 | 1.594% | 0.2515%
2017-08-24 | 6 | 6830 | 106.8606 | 1.565% | 16.8604 | 0.2469% | 123.721 | 1.811% | 492 | 6813.1396 | 6706.279 | 1.593% | 0.2514%
2017-06-02 | 24 | 6834 | 106.8776 | 1.564% | 16.8643 | 0.2468% | 123.742 | 1.811% | 493 | 6817.1357 | 6710.258 | 1.593% | 0.2513%
2017-08-16 | 4 | 6838 | 106.8947 | 1.563% | 16.8682 | 0.2467% | 123.7629 | 1.81% | 494 | 6821.1318 | 6714.2371 | 1.592% | 0.2512%
2017-07-29 | 6 | 6841 | 106.9074 | 1.563% | 16.8711 | 0.2466% | 123.7786 | 1.809% | 495 | 6824.1289 | 6717.2214 | 1.592% | 0.2512%
2017-06-28 | 24 | 6844 | 106.9202 | 1.562% | 16.8741 | 0.2466% | 123.7943 | 1.809% | 496 | 6827.1259 | 6720.2057 | 1.591% | 0.2511%
2017-07-04 | 9 | 6844 | 106.9202 | 1.562% | 16.8741 | 0.2466% | 123.7943 | 1.809% | 497 | 6827.1259 | 6720.2057 | 1.591% | 0.2511%
2017-07-30 | 10 | 6844 | 106.9202 | 1.562% | 16.8741 | 0.2466% | 123.7943 | 1.809% | 498 | 6827.1259 | 6720.2057 | 1.591% | 0.2511%
2017-07-22 | 7 | 6846 | 106.9287 | 1.562% | 16.876 | 0.2465% | 123.8047 | 1.808% | 499 | 6829.124 | 6722.1953 | 1.591% | 0.251%
2017-07-22 | 5 | 6847 | 106.933 | 1.562% | 16.877 | 0.2465% | 123.8099 | 1.808% | 500 | 6830.123 | 6723.1901 | 1.591% | 0.251%
2017-08-08 | 4 | 6848 | 106.9372 | 1.562% | 16.8779 | 0.2465% | 123.8152 | 1.808% | 501 | 6831.1221 | 6724.1848 | 1.59% | 0.251%
2017-08-22 | 6 | 6849 | 106.9415 | 1.561% | 16.8789 | 0.2464% | 123.8204 | 1.808% | 502 | 6832.1211 | 6725.1796 | 1.59% | 0.251%
2017-07-19 | 1 | 6850 | 106.9457 | 1.561% | 16.8799 | 0.2464% | 123.8256 | 1.808% | 503 | 6833.1201 | 6726.1744 | 1.59% | 0.251%
2017-08-07 | 2 | 6851 | 106.95 | 1.561% | 16.8809 | 0.2464% | 123.8309 | 1.807% | 504 | 6834.1191 | 6727.1691 | 1.59% | 0.2509%
2017-06-29 | 9 | 6853 | 106.9585 | 1.561% | 16.8828 | 0.2464% | 123.8413 | 1.807% | 505 | 6836.1172 | 6729.1587 | 1.589% | 0.2509%
2017-07-07 | 5 | 6854 | 106.9628 | 1.561% | 16.8838 | 0.2463% | 123.8466 | 1.807% | 506 | 6837.1162 | 6730.1534 | 1.589% | 0.2509%
2017-07-29 | 4 | 6857 | 106.9755 | 1.56% | 16.8867 | 0.2463% | 123.8622 | 1.806% | 507 | 6840.1133 | 6733.1378 | 1.589% | 0.2508%
2017-07-25 | 5 | 6858 | 106.9798 | 1.56% | 16.8877 | 0.2462% | 123.8675 | 1.806% | 508 | 6841.1123 | 6734.1325 | 1.589% | 0.2508%
2017-08-01 | 9 | 6859 | 106.9841 | 1.56% | 16.8887 | 0.2462% | 123.8727 | 1.806% | 509 | 6842.1113 | 6735.1273 | 1.588% | 0.2508%
2017-06-20 | 24 | 6860 | 106.9883 | 1.56% | 16.8896 | 0.2462% | 123.8779 | 1.806% | 510 | 6843.1104 | 6736.1221 | 1.588% | 0.2507%
2017-08-17 | 5 | 6861 | 106.9926 | 1.559% | 16.8906 | 0.2462% | 123.8832 | 1.806% | 511 | 6844.1094 | 6737.1168 | 1.588% | 0.2507%
2017-08-26 | 9 | 6863 | 107.0011 | 1.559% | 16.8925 | 0.2461% | 123.8936 | 1.805% | 512 | 6846.1075 | 6739.1064 | 1.588% | 0.2507%
2017-07-22 | 6 | 6864 | 107.0053 | 1.559% | 16.8935 | 0.2461% | 123.8989 | 1.805% | 513 | 6847.1065 | 6740.1011 | 1.588% | 0.2506%
2017-06-12 | 8 | 6867 | 107.0181 | 1.558% | 16.8964 | 0.2461% | 123.9145 | 1.804% | 514 | 6850.1036 | 6743.0855 | 1.587% | 0.2506%
2017-06-19 | 6 | 6869 | 107.0266 | 1.558% | 16.8984 | 0.246% | 123.925 | 1.804% | 515 | 6852.1016 | 6745.075 | 1.587% | 0.2505%
2017-08-26 | 1 | 6869 | 107.0266 | 1.558% | 16.8984 | 0.246% | 123.925 | 1.804% | 516 | 6852.1016 | 6745.075 | 1.587% | 0.2505%
2017-08-21 | 6 | 6870 | 107.0309 | 1.558% | 16.8994 | 0.246% | 123.9302 | 1.804% | 517 | 6853.1006 | 6746.0698 | 1.587% | 0.2505%
2017-06-30 | 1 | 6871 | 107.0351 | 1.558% | 16.9003 | 0.246% | 123.9355 | 1.804% | 518 | 6854.0997 | 6747.0645 | 1.586% | 0.2505%
2017-06-24 | 5 | 6874 | 107.0479 | 1.557% | 16.9033 | 0.2459% | 123.9512 | 1.803% | 519 | 6857.0967 | 6750.0488 | 1.586% | 0.2504%
2017-06-05 | 7 | 6876 | 107.0564 | 1.557% | 16.9052 | 0.2459% | 123.9616 | 1.803% | 520 | 6859.0948 | 6752.0384 | 1.586% | 0.2504%
2017-08-06 | 1 | 6879 | 107.0692 | 1.556% | 16.9081 | 0.2458% | 123.9773 | 1.802% | 521 | 6862.0919 | 6755.0227 | 1.585% | 0.2503%
2017-07-28 | 5 | 6880 | 107.0735 | 1.556% | 16.9091 | 0.2458% | 123.9825 | 1.802% | 522 | 6863.0909 | 6756.0175 | 1.585% | 0.2503%
2017-06-10 | 10 | 6883 | 107.0862 | 1.556% | 16.912 | 0.2457% | 123.9982 | 1.802% | 523 | 6866.088 | 6759.0018 | 1.584% | 0.2502%
2017-06-24 | 7 | 6883 | 107.0862 | 1.556% | 16.912 | 0.2457% | 123.9982 | 1.802% | 524 | 6866.088 | 6759.0018 | 1.584% | 0.2502%
2017-07-17 | 7 | 6884 | 107.0905 | 1.556% | 16.913 | 0.2457% | 124.0035 | 1.801% | 525 | 6867.087 | 6759.9965 | 1.584% | 0.2502%
2017-08-08 | 5 | 6885 | 107.0947 | 1.555% | 16.914 | 0.2457% | 124.0087 | 1.801% | 526 | 6868.086 | 6760.9913 | 1.584% | 0.2502%
2017-06-07 | 9 | 6886 | 107.099 | 1.555% | 16.9149 | 0.2456% | 124.0139 | 1.801% | 527 | 6869.0851 | 6761.9861 | 1.584% | 0.2501%
2017-07-25 | 4 | 6888 | 107.1075 | 1.555% | 16.9169 | 0.2456% | 124.0244 | 1.801% | 528 | 6871.0831 | 6763.9756 | 1.583% | 0.2501%
2017-08-25 | 1 | 6890 | 107.116 | 1.555% | 16.9188 | 0.2456% | 124.0348 | 1.8% | 529 | 6873.0812 | 6765.9652 | 1.583% | 0.2501%
2017-08-12 | 8 | 6892 | 107.1245 | 1.554% | 16.9208 | 0.2455% | 124.0453 | 1.8% | 530 | 6875.0792 | 6767.9547 | 1.583% | 0.25%
2017-07-11 | 7 | 6893 | 107.1288 | 1.554% | 16.9217 | 0.2455% | 124.0505 | 1.8% | 531 | 6876.0783 | 6768.9495 | 1.583% | 0.25%
2017-07-09 | 9 | 6894 | 107.133 | 1.554% | 16.9227 | 0.2455% | 124.0558 | 1.799% | 532 | 6877.0773 | 6769.9442 | 1.582% | 0.25%
2017-08-17 | 4 | 6895 | 107.1373 | 1.554% | 16.9237 | 0.2454% | 124.061 | 1.799% | 533 | 6878.0763 | 6770.939 | 1.582% | 0.2499%
2017-08-25 | 7 | 6896 | 107.1416 | 1.554% | 16.9247 | 0.2454% | 124.0662 | 1.799% | 534 | 6879.0753 | 6771.9338 | 1.582% | 0.2499%
2017-06-24 | 6 | 6900 | 107.1586 | 1.553% | 16.9286 | 0.2453% | 124.0871 | 1.798% | 535 | 6883.0714 | 6775.9129 | 1.581% | 0.2498%
2017-07-24 | 2 | 6901 | 107.1628 | 1.553% | 16.9295 | 0.2453% | 124.0924 | 1.798% | 536 | 6884.0705 | 6776.9076 | 1.581% | 0.2498%
2017-07-12 | 5 | 6903 | 107.1714 | 1.553% | 16.9315 | 0.2453% | 124.1028 | 1.798% | 537 | 6886.0685 | 6778.8972 | 1.581% | 0.2498%
2017-06-18 | 1 | 6906 | 107.1841 | 1.552% | 16.9344 | 0.2452% | 124.1185 | 1.797% | 538 | 6889.0656 | 6781.8815 | 1.58% | 0.2497%
2017-07-06 | 2 | 6911 | 107.2054 | 1.551% | 16.9393 | 0.2451% | 124.1447 | 1.796% | 539 | 6894.0607 | 6786.8553 | 1.58% | 0.2496%
2017-07-28 | 4 | 6915 | 107.2224 | 1.551% | 16.9432 | 0.245% | 124.1656 | 1.796% | 540 | 6898.0568 | 6790.8344 | 1.579% | 0.2495%
2017-07-21 | 5 | 6916 | 107.2267 | 1.55% | 16.9441 | 0.245% | 124.1708 | 1.795% | 541 | 6899.0559 | 6791.8292 | 1.579% | 0.2495%
2017-06-08 | 14 | 6919 | 107.2395 | 1.55% | 16.947 | 0.2449% | 124.1865 | 1.795% | 542 | 6902.053 | 6794.8135 | 1.578% | 0.2494%
2017-06-21 | 8 | 6919 | 107.2395 | 1.55% | 16.947 | 0.2449% | 124.1865 | 1.795% | 543 | 6902.053 | 6794.8135 | 1.578% | 0.2494%
2017-08-03 | 1 | 6919 | 107.2395 | 1.55% | 16.947 | 0.2449% | 124.1865 | 1.795% | 544 | 6902.053 | 6794.8135 | 1.578% | 0.2494%
2017-07-07 | 4 | 6920 | 107.2437 | 1.55% | 16.948 | 0.2449% | 124.1917 | 1.795% | 545 | 6903.052 | 6795.8083 | 1.578% | 0.2494%
2017-06-13 | 8 | 6921 | 107.248 | 1.55% | 16.949 | 0.2449% | 124.197 | 1.794% | 546 | 6904.051 | 6796.803 | 1.578% | 0.2494%
2017-06-23 | 1 | 6923 | 107.2565 | 1.549% | 16.9509 | 0.2448% | 124.2074 | 1.794% | 547 | 6906.0491 | 6798.7926 | 1.578% | 0.2493%
2017-08-08 | 24 | 6925 | 107.265 | 1.549% | 16.9529 | 0.2448% | 124.2179 | 1.794% | 548 | 6908.0471 | 6800.7821 | 1.577% | 0.2493%
2017-08-28 | 9 | 6925 | 107.265 | 1.549% | 16.9529 | 0.2448% | 124.2179 | 1.794% | 549 | 6908.0471 | 6800.7821 | 1.577% | 0.2493%
2017-07-01 | 1 | 6927 | 107.2735 | 1.549% | 16.9548 | 0.2448% | 124.2284 | 1.793% | 550 | 6910.0452 | 6802.7716 | 1.577% | 0.2492%
2017-07-12 | 4 | 6929 | 107.282 | 1.548% | 16.9568 | 0.2447% | 124.2388 | 1.793% | 551 | 6912.0432 | 6804.7612 | 1.577% | 0.2492%
2017-07-29 | 24 | 6930 | 107.2863 | 1.548% | 16.9577 | 0.2447% | 124.244 | 1.793% | 552 | 6913.0423 | 6805.756 | 1.576% | 0.2492%
2017-08-18 | 4 | 6934 | 107.3033 | 1.547% | 16.9616 | 0.2446% | 124.265 | 1.792% | 553 | 6917.0384 | 6809.735 | 1.576% | 0.2491%
2017-08-20 | 2 | 6934 | 107.3033 | 1.547% | 16.9616 | 0.2446% | 124.265 | 1.792% | 554 | 6917.0384 | 6809.735 | 1.576% | 0.2491%
2017-06-01 | 8 | 6939 | 107.3246 | 1.547% | 16.9665 | 0.2445% | 124.2911 | 1.791% | 555 | 6922.0335 | 6814.7089 | 1.575% | 0.249%
2017-07-31 | 24 | 6940 | 107.3289 | 1.547% | 16.9675 | 0.2445% | 124.2963 | 1.791% | 556 | 6923.0325 | 6815.7037 | 1.575% | 0.2489%
2017-08-09 | 8 | 6940 | 107.3289 | 1.547% | 16.9675 | 0.2445% | 124.2963 | 1.791% | 557 | 6923.0325 | 6815.7037 | 1.575% | 0.2489%
2017-08-27 | 10 | 6941 | 107.3331 | 1.546% | 16.9685 | 0.2445% | 124.3016 | 1.791% | 558 | 6924.0315 | 6816.6984 | 1.575% | 0.2489%
2017-07-29 | 7 | 6943 | 107.3416 | 1.546% | 16.9704 | 0.2444% | 124.312 | 1.79% | 559 | 6926.0296 | 6818.688 | 1.574% | 0.2489%
2017-07-20 | 2 | 6946 | 107.3544 | 1.546% | 16.9733 | 0.2444% | 124.3277 | 1.79% | 560 | 6929.0267 | 6821.6723 | 1.574% | 0.2488%
2017-06-19 | 2 | 6948 | 107.3629 | 1.545% | 16.9753 | 0.2443% | 124.3382 | 1.79% | 561 | 6931.0247 | 6823.6618 | 1.573% | 0.2488%
2017-08-15 | 4 | 6949 | 107.3672 | 1.545% | 16.9762 | 0.2443% | 124.3434 | 1.789% | 562 | 6932.0238 | 6824.6566 | 1.573% | 0.2487%
2017-08-11 | 7 | 6953 | 107.3842 | 1.544% | 16.9801 | 0.2442% | 124.3643 | 1.789% | 563 | 6936.0199 | 6828.6357 | 1.573% | 0.2487%
2017-06-09 | 11 | 6956 | 107.397 | 1.544% | 16.9831 | 0.2441% | 124.38 | 1.788% | 564 | 6939.0169 | 6831.62 | 1.572% | 0.2486%
2017-08-14 | 1 | 6957 | 107.4012 | 1.544% | 16.984 | 0.2441% | 124.3853 | 1.788% | 565 | 6940.016 | 6832.6147 | 1.572% | 0.2486%
2017-08-18 | 5 | 6958 | 107.4055 | 1.544% | 16.985 | 0.2441% | 124.3905 | 1.788% | 566 | 6941.015 | 6833.6095 | 1.572% | 0.2486%
2017-07-26 | 6 | 6962 | 107.4225 | 1.543% | 16.9889 | 0.244% | 124.4114 | 1.787% | 567 | 6945.0111 | 6837.5886 | 1.571% | 0.2485%
2017-08-15 | 5 | 6962 | 107.4225 | 1.543% | 16.9889 | 0.244% | 124.4114 | 1.787% | 568 | 6945.0111 | 6837.5886 | 1.571% | 0.2485%
2017-06-28 | 10 | 6971 | 107.4608 | 1.542% | 16.9976 | 0.2438% | 124.4585 | 1.785% | 569 | 6954.0024 | 6846.5415 | 1.57% | 0.2483%
2017-06-03 | 24 | 6973 | 107.4693 | 1.541% | 16.9996 | 0.2438% | 124.4689 | 1.785% | 570 | 6956.0004 | 6848.5311 | 1.569% | 0.2482%
2017-07-27 | 2 | 6974 | 107.4736 | 1.541% | 17.0006 | 0.2438% | 124.4742 | 1.785% | 571 | 6956.9994 | 6849.5258 | 1.569% | 0.2482%
2017-08-09 | 24 | 6974 | 107.4736 | 1.541% | 17.0006 | 0.2438% | 124.4742 | 1.785% | 572 | 6956.9994 | 6849.5258 | 1.569% | 0.2482%
2017-08-24 | 2 | 6976 | 107.4821 | 1.541% | 17.0025 | 0.2437% | 124.4846 | 1.784% | 573 | 6958.9975 | 6851.5154 | 1.569% | 0.2482%
2017-07-01 | 9 | 6978 | 107.4906 | 1.54% | 17.0045 | 0.2437% | 124.4951 | 1.784% | 574 | 6960.9955 | 6853.5049 | 1.568% | 0.2481%
2017-07-27 | 7 | 6978 | 107.4906 | 1.54% | 17.0045 | 0.2437% | 124.4951 | 1.784% | 575 | 6960.9955 | 6853.5049 | 1.568% | 0.2481%
2017-07-16 | 2 | 6980 | 107.4991 | 1.54% | 17.0064 | 0.2436% | 124.5056 | 1.784% | 576 | 6962.9936 | 6855.4944 | 1.568% | 0.2481%
2017-08-30 | 10 | 6982 | 107.5077 | 1.54% | 17.0084 | 0.2436% | 124.516 | 1.783% | 577 | 6964.9916 | 6857.484 | 1.568% | 0.248%
2017-06-27 | 9 | 6985 | 107.5204 | 1.539% | 17.0113 | 0.2435% | 124.5317 | 1.783% | 578 | 6967.9887 | 6860.4683 | 1.567% | 0.248%
2017-06-17 | 1 | 6986 | 107.5247 | 1.539% | 17.0122 | 0.2435% | 124.5369 | 1.783% | 579 | 6968.9878 | 6861.4631 | 1.567% | 0.2479%
2017-07-04 | 1 | 6986 | 107.5247 | 1.539% | 17.0122 | 0.2435% | 124.5369 | 1.783% | 580 | 6968.9878 | 6861.4631 | 1.567% | 0.2479%
2017-06-03 | 10 | 6990 | 107.5417 | 1.539% | 17.0161 | 0.2434% | 124.5579 | 1.782% | 581 | 6972.9839 | 6865.4421 | 1.566% | 0.2479%
2017-07-21 | 4 | 6990 | 107.5417 | 1.539% | 17.0161 | 0.2434% | 124.5579 | 1.782% | 582 | 6972.9839 | 6865.4421 | 1.566% | 0.2479%
2017-08-29 | 23 | 6991 | 107.546 | 1.538% | 17.0171 | 0.2434% | 124.5631 | 1.782% | 583 | 6973.9829 | 6866.4369 | 1.566% | 0.2478%
2017-06-20 | 2 | 6996 | 107.5673 | 1.538% | 17.022 | 0.2433% | 124.5892 | 1.781% | 584 | 6978.978 | 6871.4108 | 1.565% | 0.2477%
2017-08-11 | 1 | 6997 | 107.5715 | 1.537% | 17.023 | 0.2433% | 124.5945 | 1.781% | 585 | 6979.977 | 6872.4055 | 1.565% | 0.2477%
2017-06-30 | 8 | 6999 | 107.58 | 1.537% | 17.0249 | 0.2432% | 124.6049 | 1.78% | 586 | 6981.9751 | 6874.3951 | 1.565% | 0.2477%
2017-08-26 | 24 | 7000 | 107.5843 | 1.537% | 17.0259 | 0.2432% | 124.6102 | 1.78% | 587 | 6982.9741 | 6875.3898 | 1.565% | 0.2476%
2017-07-26 | 3 | 7002 | 107.5928 | 1.537% | 17.0278 | 0.2432% | 124.6206 | 1.78% | 588 | 6984.9722 | 6877.3794 | 1.564% | 0.2476%
2017-06-06 | 8 | 7005 | 107.6056 | 1.536% | 17.0307 | 0.2431% | 124.6363 | 1.779% | 589 | 6987.9693 | 6880.3637 | 1.564% | 0.2475%
2017-07-08 | 3 | 7005 | 107.6056 | 1.536% | 17.0307 | 0.2431% | 124.6363 | 1.779% | 590 | 6987.9693 | 6880.3637 | 1.564% | 0.2475%
2017-08-13 | 2 | 7010 | 107.6269 | 1.535% | 17.0356 | 0.243% | 124.6625 | 1.778% | 591 | 6992.9644 | 6885.3375 | 1.563% | 0.2474%
2017-06-06 | 24 | 7013 | 107.6396 | 1.535% | 17.0385 | 0.243% | 124.6781 | 1.778% | 592 | 6995.9615 | 6888.3219 | 1.563% | 0.2474%
2017-06-24 | 4 | 7017 | 107.6567 | 1.534% | 17.0424 | 0.2429% | 124.6991 | 1.777% | 593 | 6999.9576 | 6892.3009 | 1.562% | 0.2473%
2017-06-26 | 24 | 7017 | 107.6567 | 1.534% | 17.0424 | 0.2429% | 124.6991 | 1.777% | 594 | 6999.9576 | 6892.3009 | 1.562% | 0.2473%
2017-08-16 | 6 | 7021 | 107.6737 | 1.534% | 17.0463 | 0.2428% | 124.72 | 1.776% | 595 | 7003.9537 | 6896.28 | 1.561% | 0.2472%
2017-07-07 | 6 | 7022 | 107.6779 | 1.533% | 17.0473 | 0.2428% | 124.7252 | 1.776% | 596 | 7004.9527 | 6897.2748 | 1.561% | 0.2472%
2017-07-22 | 4 | 7024 | 107.6865 | 1.533% | 17.0492 | 0.2427% | 124.7357 | 1.776% | 597 | 7006.9508 | 6899.2643 | 1.561% | 0.2471%
2017-08-29 | 8 | 7025 | 107.6907 | 1.533% | 17.0502 | 0.2427% | 124.7409 | 1.776% | 598 | 7007.9498 | 6900.2591 | 1.561% | 0.2471%
2017-07-29 | 3 | 7028 | 107.7035 | 1.532% | 17.0531 | 0.2426% | 124.7566 | 1.775% | 599 | 7010.9469 | 6903.2434 | 1.56% | 0.247%
2017-08-08 | 3 | 7028 | 107.7035 | 1.532% | 17.0531 | 0.2426% | 124.7566 | 1.775% | 600 | 7010.9469 | 6903.2434 | 1.56% | 0.247%
2017-06-20 | 7 | 7029 | 107.7077 | 1.532% | 17.0541 | 0.2426% | 124.7618 | 1.775% | 601 | 7011.9459 | 6904.2382 | 1.56% | 0.247%
2017-06-08 | 22 | 7030 | 107.712 | 1.532% | 17.0551 | 0.2426% | 124.7671 | 1.775% | 602 | 7012.9449 | 6905.2329 | 1.56% | 0.247%
2017-06-05 | 24 | 7035 | 107.7333 | 1.531% | 17.0599 | 0.2425% | 124.7932 | 1.774% | 603 | 7017.9401 | 6910.2068 | 1.559% | 0.2469%
2017-06-08 | 15 | 7038 | 107.7461 | 1.531% | 17.0629 | 0.2424% | 124.8089 | 1.773% | 604 | 7020.9371 | 6913.1911 | 1.559% | 0.2468%
2017-07-11 | 1 | 7038 | 107.7461 | 1.531% | 17.0629 | 0.2424% | 124.8089 | 1.773% | 605 | 7020.9371 | 6913.1911 | 1.559% | 0.2468%
2017-08-04 | 1 | 7046 | 107.7801 | 1.53% | 17.0706 | 0.2423% | 124.8507 | 1.772% | 606 | 7028.9294 | 6921.1493 | 1.557% | 0.2466%
2017-06-01 | 24 | 7048 | 107.7886 | 1.529% | 17.0726 | 0.2422% | 124.8612 | 1.772% | 607 | 7030.9274 | 6923.1388 | 1.557% | 0.2466%
2017-07-10 | 1 | 7048 | 107.7886 | 1.529% | 17.0726 | 0.2422% | 124.8612 | 1.772% | 608 | 7030.9274 | 6923.1388 | 1.557% | 0.2466%
2017-08-03 | 8 | 7048 | 107.7886 | 1.529% | 17.0726 | 0.2422% | 124.8612 | 1.772% | 609 | 7030.9274 | 6923.1388 | 1.557% | 0.2466%
2017-08-05 | 9 | 7056 | 107.8227 | 1.528% | 17.0804 | 0.2421% | 124.903 | 1.77% | 610 | 7038.9196 | 6931.097 | 1.556% | 0.2464%
2017-06-14 | 8 | 7058 | 107.8312 | 1.528% | 17.0823 | 0.242% | 124.9135 | 1.77% | 611 | 7040.9177 | 6933.0865 | 1.555% | 0.2464%
2017-08-12 | 2 | 7061 | 107.844 | 1.527% | 17.0852 | 0.242% | 124.9292 | 1.769% | 612 | 7043.9148 | 6936.0708 | 1.555% | 0.2463%
2017-08-16 | 3 | 7062 | 107.8482 | 1.527% | 17.0862 | 0.2419% | 124.9344 | 1.769% | 613 | 7044.9138 | 6937.0656 | 1.555% | 0.2463%
2017-07-03 | 2 | 7065 | 107.861 | 1.527% | 17.0891 | 0.2419% | 124.9501 | 1.769% | 614 | 7047.9109 | 6940.0499 | 1.554% | 0.2462%
2017-07-16 | 9 | 7067 | 107.8695 | 1.526% | 17.0911 | 0.2418% | 124.9606 | 1.768% | 615 | 7049.9089 | 6942.0394 | 1.554% | 0.2462%
2017-08-31 | 7 | 7074 | 107.8993 | 1.525% | 17.0979 | 0.2417% | 124.9972 | 1.767% | 616 | 7056.9021 | 6949.0028 | 1.553% | 0.246%
2017-08-18 | 3 | 7075 | 107.9036 | 1.525% | 17.0989 | 0.2417% | 125.0024 | 1.767% | 617 | 7057.9011 | 6949.9976 | 1.553% | 0.246%
2017-06-23 | 7 | 7078 | 107.9163 | 1.525% | 17.1018 | 0.2416% | 125.0181 | 1.766% | 618 | 7060.8982 | 6952.9819 | 1.552% | 0.246%
2017-06-08 | 21 | 7079 | 107.9206 | 1.525% | 17.1028 | 0.2416% | 125.0233 | 1.766% | 619 | 7061.8972 | 6953.9767 | 1.552% | 0.2459%
2017-07-21 | 6 | 7079 | 107.9206 | 1.525% | 17.1028 | 0.2416% | 125.0233 | 1.766% | 620 | 7061.8972 | 6953.9767 | 1.552% | 0.2459%
2017-07-25 | 6 | 7080 | 107.9248 | 1.524% | 17.1037 | 0.2416% | 125.0286 | 1.766% | 621 | 7062.8963 | 6954.9714 | 1.552% | 0.2459%
2017-07-23 | 7 | 7089 | 107.9632 | 1.523% | 17.1125 | 0.2414% | 125.0756 | 1.764% | 622 | 7071.8875 | 6963.9244 | 1.55% | 0.2457%
2017-07-18 | 7 | 7093 | 107.9802 | 1.522% | 17.1164 | 0.2413% | 125.0966 | 1.764% | 623 | 7075.8836 | 6967.9034 | 1.55% | 0.2456%
2017-07-28 | 6 | 7093 | 107.9802 | 1.522% | 17.1164 | 0.2413% | 125.0966 | 1.764% | 624 | 7075.8836 | 6967.9034 | 1.55% | 0.2456%
2017-08-23 | 5 | 7095 | 107.9887 | 1.522% | 17.1183 | 0.2413% | 125.107 | 1.763% | 625 | 7077.8817 | 6969.893 | 1.549% | 0.2456%
2017-08-30 | 24 | 7095 | 107.9887 | 1.522% | 17.1183 | 0.2413% | 125.107 | 1.763% | 626 | 7077.8817 | 6969.893 | 1.549% | 0.2456%
2017-07-28 | 3 | 7099 | 108.0057 | 1.521% | 17.1222 | 0.2412% | 125.1279 | 1.763% | 627 | 7081.8778 | 6973.8721 | 1.549% | 0.2455%
2017-06-26 | 9 | 7101 | 108.0142 | 1.521% | 17.1242 | 0.2412% | 125.1384 | 1.762% | 628 | 7083.8758 | 6975.8616 | 1.548% | 0.2455%
2017-08-22 | 2 | 7106 | 108.0355 | 1.52% | 17.129 | 0.2411% | 125.1645 | 1.761% | 629 | 7088.871 | 6980.8355 | 1.548% | 0.2454%
2017-06-25 | 24 | 7107 | 108.0398 | 1.52% | 17.13 | 0.241% | 125.1698 | 1.761% | 630 | 7089.87 | 6981.8302 | 1.547% | 0.2454%
2017-07-09 | 1 | 7113 | 108.0653 | 1.519% | 17.1358 | 0.2409% | 125.2012 | 1.76% | 631 | 7095.8642 | 6987.7988 | 1.546% | 0.2452%
2017-08-15 | 3 | 7122 | 108.1036 | 1.518% | 17.1446 | 0.2407% | 125.2482 | 1.759% | 632 | 7104.8554 | 6996.7518 | 1.545% | 0.245%
2017-07-03 | 8 | 7123 | 108.1079 | 1.518% | 17.1456 | 0.2407% | 125.2535 | 1.758% | 633 | 7105.8544 | 6997.7465 | 1.545% | 0.245%
2017-08-23 | 4 | 7123 | 108.1079 | 1.518% | 17.1456 | 0.2407% | 125.2535 | 1.758% | 634 | 7105.8544 | 6997.7465 | 1.545% | 0.245%
2017-07-12 | 6 | 7124 | 108.1121 | 1.518% | 17.1465 | 0.2407% | 125.2587 | 1.758% | 635 | 7106.8535 | 6998.7413 | 1.545% | 0.245%
2017-08-27 | 23 | 7125 | 108.1164 | 1.517% | 17.1475 | 0.2407% | 125.2639 | 1.758% | 636 | 7107.8525 | 6999.7361 | 1.545% | 0.245%
2017-07-19 | 8 | 7128 | 108.1292 | 1.517% | 17.1504 | 0.2406% | 125.2796 | 1.758% | 637 | 7110.8496 | 7002.7204 | 1.544% | 0.2449%
2017-06-10 | 24 | 7129 | 108.1334 | 1.517% | 17.1514 | 0.2406% | 125.2848 | 1.757% | 638 | 7111.8486 | 7003.7152 | 1.544% | 0.2449%
2017-08-17 | 3 | 7132 | 108.1462 | 1.516% | 17.1543 | 0.2405% | 125.3005 | 1.757% | 639 | 7114.8457 | 7006.6995 | 1.543% | 0.2448%
2017-07-24 | 7 | 7133 | 108.1505 | 1.516% | 17.1553 | 0.2405% | 125.3058 | 1.757% | 640 | 7115.8447 | 7007.6942 | 1.543% | 0.2448%
2017-06-04 | 24 | 7134 | 108.1547 | 1.516% | 17.1563 | 0.2405% | 125.311 | 1.757% | 641 | 7116.8437 | 7008.689 | 1.543% | 0.2448%
2017-08-10 | 9 | 7144 | 108.1973 | 1.515% | 17.166 | 0.2403% | 125.3633 | 1.755% | 642 | 7126.834 | 7018.6367 | 1.542% | 0.2446%
2017-08-05 | 2 | 7145 | 108.2015 | 1.514% | 17.167 | 0.2403% | 125.3685 | 1.755% | 643 | 7127.833 | 7019.6315 | 1.541% | 0.2446%
2017-07-23 | 6 | 7146 | 108.2058 | 1.514% | 17.168 | 0.2402% | 125.3738 | 1.754% | 644 | 7128.832 | 7020.6262 | 1.541% | 0.2445%
2017-07-29 | 8 | 7148 | 108.2143 | 1.514% | 17.1699 | 0.2402% | 125.3842 | 1.754% | 645 | 7130.8301 | 7022.6158 | 1.541% | 0.2445%
2017-06-07 | 10 | 7152 | 108.2313 | 1.513% | 17.1738 | 0.2401% | 125.4051 | 1.753% | 646 | 7134.8262 | 7026.5949 | 1.54% | 0.2444%
2017-06-08 | 20 | 7152 | 108.2313 | 1.513% | 17.1738 | 0.2401% | 125.4051 | 1.753% | 647 | 7134.8262 | 7026.5949 | 1.54% | 0.2444%
2017-08-17 | 6 | 7156 | 108.2484 | 1.513% | 17.1777 | 0.24% | 125.4261 | 1.753% | 648 | 7138.8223 | 7030.5739 | 1.54% | 0.2443%
2017-07-25 | 3 | 7159 | 108.2611 | 1.512% | 17.1806 | 0.24% | 125.4417 | 1.752% | 649 | 7141.8194 | 7033.5583 | 1.539% | 0.2443%
2017-06-08 | 16 | 7162 | 108.2739 | 1.512% | 17.1835 | 0.2399% | 125.4574 | 1.752% | 650 | 7144.8165 | 7036.5426 | 1.539% | 0.2442%
2017-08-02 | 9 | 7168 | 108.2995 | 1.511% | 17.1894 | 0.2398% | 125.4888 | 1.751% | 651 | 7150.8106 | 7042.5112 | 1.538% | 0.2441%
2017-07-31 | 10 | 7170 | 108.308 | 1.511% | 17.1913 | 0.2398% | 125.4993 | 1.75% | 652 | 7152.8087 | 7044.5007 | 1.537% | 0.244%
2017-07-12 | 3 | 7171 | 108.3122 | 1.51% | 17.1923 | 0.2397% | 125.5045 | 1.75% | 653 | 7153.8077 | 7045.4955 | 1.537% | 0.244%
2017-08-08 | 6 | 7174 | 108.325 | 1.51% | 17.1952 | 0.2397% | 125.5202 | 1.75% | 654 | 7156.8048 | 7048.4798 | 1.537% | 0.244%
2017-06-16 | 1 | 7176 | 108.3335 | 1.51% | 17.1971 | 0.2396% | 125.5307 | 1.749% | 655 | 7158.8029 | 7050.4693 | 1.537% | 0.2439%
2017-07-08 | 8 | 7178 | 108.342 | 1.509% | 17.1991 | 0.2396% | 125.5411 | 1.749% | 656 | 7160.8009 | 7052.4589 | 1.536% | 0.2439%
2017-08-04 | 8 | 7184 | 108.3676 | 1.508% | 17.2049 | 0.2395% | 125.5725 | 1.748% | 657 | 7166.7951 | 7058.4275 | 1.535% | 0.2438%
2017-06-15 | 1 | 7185 | 108.3718 | 1.508% | 17.2059 | 0.2395% | 125.5777 | 1.748% | 658 | 7167.7941 | 7059.4223 | 1.535% | 0.2437%
2017-08-01 | 24 | 7185 | 108.3718 | 1.508% | 17.2059 | 0.2395% | 125.5777 | 1.748% | 659 | 7167.7941 | 7059.4223 | 1.535% | 0.2437%
2017-07-02 | 1 | 7188 | 108.3846 | 1.508% | 17.2088 | 0.2394% | 125.5934 | 1.747% | 660 | 7170.7912 | 7062.4066 | 1.535% | 0.2437%
2017-08-19 | 6 | 7192 | 108.4016 | 1.507% | 17.2127 | 0.2393% | 125.6143 | 1.747% | 661 | 7174.7873 | 7066.3857 | 1.534% | 0.2436%
2017-07-07 | 3 | 7193 | 108.4059 | 1.507% | 17.2137 | 0.2393% | 125.6196 | 1.746% | 662 | 7175.7863 | 7067.3804 | 1.534% | 0.2436%
2017-08-21 | 2 | 7193 | 108.4059 | 1.507% | 17.2137 | 0.2393% | 125.6196 | 1.746% | 663 | 7175.7863 | 7067.3804 | 1.534% | 0.2436%
2017-07-15 | 7 | 7194 | 108.4101 | 1.507% | 17.2147 | 0.2393% | 125.6248 | 1.746% | 664 | 7176.7853 | 7068.3752 | 1.534% | 0.2435%
2017-06-02 | 9 | 7195 | 108.4144 | 1.507% | 17.2156 | 0.2393% | 125.63 | 1.746% | 665 | 7177.7844 | 7069.37 | 1.534% | 0.2435%
2017-07-18 | 1 | 7196 | 108.4187 | 1.507% | 17.2166 | 0.2393% | 125.6353 | 1.746% | 666 | 7178.7834 | 7070.3647 | 1.533% | 0.2435%
2017-07-02 | 9 | 7200 | 108.4357 | 1.506% | 17.2205 | 0.2392% | 125.6562 | 1.745% | 667 | 7182.7795 | 7074.3438 | 1.533% | 0.2434%
2017-06-17 | 9 | 7204 | 108.4527 | 1.505% | 17.2244 | 0.2391% | 125.6771 | 1.745% | 668 | 7186.7756 | 7078.3229 | 1.532% | 0.2433%
2017-06-21 | 9 | 7207 | 108.4655 | 1.505% | 17.2273 | 0.239% | 125.6928 | 1.744% | 669 | 7189.7727 | 7081.3072 | 1.532% | 0.2433%
2017-07-05 | 8 | 7208 | 108.4697 | 1.505% | 17.2283 | 0.239% | 125.698 | 1.744% | 670 | 7190.7717 | 7082.302 | 1.532% | 0.2433%
2017-06-24 | 3 | 7210 | 108.4782 | 1.505% | 17.2302 | 0.239% | 125.7085 | 1.744% | 671 | 7192.7698 | 7084.2915 | 1.531% | 0.2432%
2017-07-23 | 5 | 7211 | 108.4825 | 1.504% | 17.2312 | 0.239% | 125.7137 | 1.743% | 672 | 7193.7688 | 7085.2863 | 1.531% | 0.2432%
2017-08-25 | 8 | 7211 | 108.4825 | 1.504% | 17.2312 | 0.239% | 125.7137 | 1.743% | 673 | 7193.7688 | 7085.2863 | 1.531% | 0.2432%
2017-08-19 | 7 | 7217 | 108.508 | 1.504% | 17.237 | 0.2388% | 125.7451 | 1.742% | 674 | 7199.763 | 7091.2549 | 1.53% | 0.2431%
2017-08-19 | 5 | 7219 | 108.5166 | 1.503% | 17.239 | 0.2388% | 125.7556 | 1.742% | 675 | 7201.761 | 7093.2444 | 1.53% | 0.243%
2017-08-08 | 2 | 7224 | 108.5378 | 1.502% | 17.2439 | 0.2387% | 125.7817 | 1.741% | 676 | 7206.7561 | 7098.2183 | 1.529% | 0.2429%
2017-08-29 | 9 | 7224 | 108.5378 | 1.502% | 17.2439 | 0.2387% | 125.7817 | 1.741% | 677 | 7206.7561 | 7098.2183 | 1.529% | 0.2429%
2017-08-20 | 9 | 7225 | 108.5421 | 1.502% | 17.2448 | 0.2387% | 125.7869 | 1.741% | 678 | 7207.7552 | 7099.2131 | 1.529% | 0.2429%
2017-07-06 | 8 | 7227 | 108.5506 | 1.502% | 17.2468 | 0.2386% | 125.7974 | 1.741% | 679 | 7209.7532 | 7101.2026 | 1.529% | 0.2429%
2017-08-15 | 6 | 7232 | 108.5719 | 1.501% | 17.2516 | 0.2385% | 125.8235 | 1.74% | 680 | 7214.7484 | 7106.1765 | 1.528% | 0.2428%
2017-07-15 | 6 | 7235 | 108.5847 | 1.501% | 17.2546 | 0.2385% | 125.8392 | 1.739% | 681 | 7217.7454 | 7109.1608 | 1.527% | 0.2427%
2017-07-13 | 5 | 7237 | 108.5932 | 1.501% | 17.2565 | 0.2384% | 125.8497 | 1.739% | 682 | 7219.7435 | 7111.1503 | 1.527% | 0.2427%
2017-08-09 | 9 | 7238 | 108.5974 | 1.5% | 17.2575 | 0.2384% | 125.8549 | 1.739% | 683 | 7220.7425 | 7112.1451 | 1.527% | 0.2426%
2017-08-28 | 10 | 7238 | 108.5974 | 1.5% | 17.2575 | 0.2384% | 125.8549 | 1.739% | 684 | 7220.7425 | 7112.1451 | 1.527% | 0.2426%
2017-08-31 | 24 | 7238 | 108.5974 | 1.5% | 17.2575 | 0.2384% | 125.8549 | 1.739% | 685 | 7220.7425 | 7112.1451 | 1.527% | 0.2426%
2017-06-04 | 10 | 7240 | 108.606 | 1.5% | 17.2594 | 0.2384% | 125.8654 | 1.738% | 686 | 7222.7406 | 7114.1346 | 1.527% | 0.2426%
2017-08-14 | 7 | 7243 | 108.6187 | 1.5% | 17.2623 | 0.2383% | 125.8811 | 1.738% | 687 | 7225.7377 | 7117.1189 | 1.526% | 0.2425%
2017-06-08 | 17 | 7244 | 108.623 | 1.499% | 17.2633 | 0.2383% | 125.8863 | 1.738% | 688 | 7226.7367 | 7118.1137 | 1.526% | 0.2425%
2017-06-09 | 23 | 7244 | 108.623 | 1.499% | 17.2633 | 0.2383% | 125.8863 | 1.738% | 689 | 7226.7367 | 7118.1137 | 1.526% | 0.2425%
2017-06-18 | 9 | 7251 | 108.6528 | 1.498% | 17.2701 | 0.2382% | 125.9229 | 1.737% | 690 | 7233.7299 | 7125.0771 | 1.525% | 0.2424%
2017-07-07 | 7 | 7259 | 108.6868 | 1.497% | 17.2779 | 0.238% | 125.9648 | 1.735% | 691 | 7241.7221 | 7133.0352 | 1.524% | 0.2422%
2017-07-26 | 7 | 7259 | 108.6868 | 1.497% | 17.2779 | 0.238% | 125.9648 | 1.735% | 692 | 7241.7221 | 7133.0352 | 1.524% | 0.2422%
2017-07-22 | 8 | 7261 | 108.6954 | 1.497% | 17.2799 | 0.238% | 125.9752 | 1.735% | 693 | 7243.7201 | 7135.0248 | 1.523% | 0.2422%
2017-08-06 | 10 | 7263 | 108.7039 | 1.497% | 17.2818 | 0.2379% | 125.9857 | 1.735% | 694 | 7245.7182 | 7137.0143 | 1.523% | 0.2421%
2017-08-18 | 6 | 7266 | 108.7166 | 1.496% | 17.2847 | 0.2379% | 126.0014 | 1.734% | 695 | 7248.7153 | 7139.9986 | 1.523% | 0.2421%
2017-06-16 | 8 | 7270 | 108.7337 | 1.496% | 17.2886 | 0.2378% | 126.0223 | 1.733% | 696 | 7252.7114 | 7143.9777 | 1.522% | 0.242%
2017-07-14 | 5 | 7276 | 108.7592 | 1.495% | 17.2945 | 0.2377% | 126.0537 | 1.732% | 697 | 7258.7055 | 7149.9463 | 1.521% | 0.2419%
2017-07-29 | 2 | 7282 | 108.7847 | 1.494% | 17.3003 | 0.2376% | 126.0851 | 1.731% | 698 | 7264.6997 | 7155.9149 | 1.52% | 0.2418%
2017-08-07 | 1 | 7283 | 108.789 | 1.494% | 17.3013 | 0.2376% | 126.0903 | 1.731% | 699 | 7265.6987 | 7156.9097 | 1.52% | 0.2417%
2017-08-07 | 7 | 7283 | 108.789 | 1.494% | 17.3013 | 0.2376% | 126.0903 | 1.731% | 700 | 7265.6987 | 7156.9097 | 1.52% | 0.2417%
2017-06-19 | 7 | 7286 | 108.8018 | 1.493% | 17.3042 | 0.2375% | 126.106 | 1.731% | 701 | 7268.6958 | 7159.894 | 1.52% | 0.2417%
2017-06-08 | 18 | 7287 | 108.806 | 1.493% | 17.3052 | 0.2375% | 126.1112 | 1.731% | 702 | 7269.6948 | 7160.8888 | 1.519% | 0.2417%
2017-07-24 | 1 | 7287 | 108.806 | 1.493% | 17.3052 | 0.2375% | 126.1112 | 1.731% | 703 | 7269.6948 | 7160.8888 | 1.519% | 0.2417%
2017-06-08 | 19 | 7296 | 108.8443 | 1.492% | 17.3139 | 0.2373% | 126.1583 | 1.729% | 704 | 7278.6861 | 7169.8417 | 1.518% | 0.2415%
2017-07-15 | 5 | 7296 | 108.8443 | 1.492% | 17.3139 | 0.2373% | 126.1583 | 1.729% | 705 | 7278.6861 | 7169.8417 | 1.518% | 0.2415%
2017-07-21 | 3 | 7297 | 108.8486 | 1.492% | 17.3149 | 0.2373% | 126.1635 | 1.729% | 706 | 7279.6851 | 7170.8365 | 1.518% | 0.2415%
2017-07-05 | 1 | 7298 | 108.8529 | 1.492% | 17.3159 | 0.2373% | 126.1687 | 1.729% | 707 | 7280.6841 | 7171.8313 | 1.518% | 0.2414%
2017-07-10 | 8 | 7298 | 108.8529 | 1.492% | 17.3159 | 0.2373% | 126.1687 | 1.729% | 708 | 7280.6841 | 7171.8313 | 1.518% | 0.2414%
2017-07-30 | 23 | 7305 | 108.8827 | 1.491% | 17.3227 | 0.2371% | 126.2053 | 1.728% | 709 | 7287.6773 | 7178.7947 | 1.517% | 0.2413%
2017-06-06 | 9 | 7310 | 108.9039 | 1.49% | 17.3276 | 0.237% | 126.2315 | 1.727% | 710 | 7292.6724 | 7183.7685 | 1.516% | 0.2412%
2017-06-07 | 22 | 7311 | 108.9082 | 1.49% | 17.3285 | 0.237% | 126.2367 | 1.727% | 711 | 7293.6715 | 7184.7633 | 1.516% | 0.2412%
2017-08-11 | 8 | 7312 | 108.9125 | 1.49% | 17.3295 | 0.237% | 126.242 | 1.727% | 712 | 7294.6705 | 7185.758 | 1.516% | 0.2412%
2017-07-17 | 8 | 7314 | 108.921 | 1.489% | 17.3314 | 0.237% | 126.2524 | 1.726% | 713 | 7296.6686 | 7187.7476 | 1.515% | 0.2411%
2017-06-11 | 24 | 7315 | 108.9252 | 1.489% | 17.3324 | 0.2369% | 126.2576 | 1.726% | 714 | 7297.6676 | 7188.7424 | 1.515% | 0.2411%
2017-08-31 | 8 | 7317 | 108.9337 | 1.489% | 17.3344 | 0.2369% | 126.2681 | 1.726% | 715 | 7299.6656 | 7190.7319 | 1.515% | 0.2411%
2017-06-09 | 12 | 7320 | 108.9465 | 1.488% | 17.3373 | 0.2368% | 126.2838 | 1.725% | 716 | 7302.6627 | 7193.7162 | 1.514% | 0.241%
2017-08-28 | 23 | 7322 | 108.955 | 1.488% | 17.3392 | 0.2368% | 126.2943 | 1.725% | 717 | 7304.6608 | 7195.7057 | 1.514% | 0.241%
2017-06-15 | 8 | 7327 | 108.9763 | 1.487% | 17.3441 | 0.2367% | 126.3204 | 1.724% | 718 | 7309.6559 | 7200.6796 | 1.513% | 0.2409%
2017-08-30 | 11 | 7327 | 108.9763 | 1.487% | 17.3441 | 0.2367% | 126.3204 | 1.724% | 719 | 7309.6559 | 7200.6796 | 1.513% | 0.2409%
2017-06-22 | 8 | 7328 | 108.9806 | 1.487% | 17.3451 | 0.2367% | 126.3256 | 1.724% | 720 | 7310.6549 | 7201.6744 | 1.513% | 0.2408%
2017-07-22 | 3 | 7332 | 108.9976 | 1.487% | 17.349 | 0.2366% | 126.3466 | 1.723% | 721 | 7314.651 | 7205.6534 | 1.513% | 0.2408%
2017-06-24 | 24 | 7336 | 109.0146 | 1.486% | 17.3529 | 0.2365% | 126.3675 | 1.723% | 722 | 7318.6471 | 7209.6325 | 1.512% | 0.2407%
2017-07-13 | 4 | 7336 | 109.0146 | 1.486% | 17.3529 | 0.2365% | 126.3675 | 1.723% | 723 | 7318.6471 | 7209.6325 | 1.512% | 0.2407%
2017-07-30 | 11 | 7338 | 109.0231 | 1.486% | 17.3548 | 0.2365% | 126.3779 | 1.722% | 724 | 7320.6452 | 7211.6221 | 1.512% | 0.2407%
2017-08-23 | 3 | 7339 | 109.0274 | 1.486% | 17.3558 | 0.2365% | 126.3832 | 1.722% | 725 | 7321.6442 | 7212.6168 | 1.512% | 0.2406%
2017-06-01 | 9 | 7341 | 109.0359 | 1.485% | 17.3577 | 0.2364% | 126.3936 | 1.722% | 726 | 7323.6423 | 7214.6064 | 1.511% | 0.2406%
2017-06-24 | 8 | 7344 | 109.0487 | 1.485% | 17.3606 | 0.2364% | 126.4093 | 1.721% | 727 | 7326.6394 | 7217.5907 | 1.511% | 0.2405%
2017-08-18 | 2 | 7345 | 109.0529 | 1.485% | 17.3616 | 0.2364% | 126.4145 | 1.721% | 728 | 7327.6384 | 7218.5855 | 1.511% | 0.2405%
2017-06-11 | 10 | 7347 | 109.0615 | 1.484% | 17.3636 | 0.2363% | 126.425 | 1.721% | 729 | 7329.6364 | 7220.575 | 1.51% | 0.2405%
2017-07-26 | 2 | 7347 | 109.0615 | 1.484% | 17.3636 | 0.2363% | 126.425 | 1.721% | 730 | 7329.6364 | 7220.575 | 1.51% | 0.2405%
2017-06-07 | 11 | 7350 | 109.0742 | 1.484% | 17.3665 | 0.2363% | 126.4407 | 1.72% | 731 | 7332.6335 | 7223.5593 | 1.51% | 0.2404%
2017-07-21 | 7 | 7351 | 109.0785 | 1.484% | 17.3674 | 0.2363% | 126.4459 | 1.72% | 732 | 7333.6326 | 7224.5541 | 1.51% | 0.2404%
2017-07-14 | 4 | 7355 | 109.0955 | 1.483% | 17.3713 | 0.2362% | 126.4669 | 1.719% | 733 | 7337.6287 | 7228.5331 | 1.509% | 0.2403%
2017-08-23 | 6 | 7355 | 109.0955 | 1.483% | 17.3713 | 0.2362% | 126.4669 | 1.719% | 734 | 7337.6287 | 7228.5331 | 1.509% | 0.2403%
2017-07-20 | 8 | 7374 | 109.1764 | 1.481% | 17.3898 | 0.2358% | 126.5662 | 1.716% | 735 | 7356.6102 | 7247.4338 | 1.506% | 0.2399%
2017-08-13 | 9 | 7378 | 109.1934 | 1.48% | 17.3937 | 0.2358% | 126.5871 | 1.716% | 736 | 7360.6063 | 7251.4129 | 1.506% | 0.2399%
2017-06-05 | 8 | 7380 | 109.2019 | 1.48% | 17.3957 | 0.2357% | 126.5976 | 1.715% | 737 | 7362.6043 | 7253.4024 | 1.506% | 0.2398%
2017-08-03 | 9 | 7382 | 109.2104 | 1.479% | 17.3976 | 0.2357% | 126.6081 | 1.715% | 738 | 7364.6024 | 7255.3919 | 1.505% | 0.2398%
2017-08-21 | 7 | 7382 | 109.2104 | 1.479% | 17.3976 | 0.2357% | 126.6081 | 1.715% | 739 | 7364.6024 | 7255.3919 | 1.505% | 0.2398%
2017-07-28 | 2 | 7383 | 109.2147 | 1.479% | 17.3986 | 0.2357% | 126.6133 | 1.715% | 740 | 7365.6014 | 7256.3867 | 1.505% | 0.2398%
2017-08-29 | 10 | 7384 | 109.219 | 1.479% | 17.3996 | 0.2356% | 126.6185 | 1.715% | 741 | 7366.6004 | 7257.3815 | 1.505% | 0.2397%
2017-06-20 | 8 | 7388 | 109.236 | 1.479% | 17.4035 | 0.2356% | 126.6394 | 1.714% | 742 | 7370.5965 | 7261.3606 | 1.504% | 0.2397%
2017-08-01 | 10 | 7389 | 109.2402 | 1.478% | 17.4044 | 0.2355% | 126.6447 | 1.714% | 743 | 7371.5956 | 7262.3553 | 1.504% | 0.2397%
2017-06-20 | 1 | 7394 | 109.2615 | 1.478% | 17.4093 | 0.2355% | 126.6708 | 1.713% | 744 | 7376.5907 | 7267.3292 | 1.503% | 0.2396%
2017-07-23 | 4 | 7395 | 109.2658 | 1.478% | 17.4103 | 0.2354% | 126.6761 | 1.713% | 745 | 7377.5897 | 7268.3239 | 1.503% | 0.2395%
2017-08-24 | 7 | 7405 | 109.3084 | 1.476% | 17.42 | 0.2352% | 126.7284 | 1.711% | 746 | 7387.58 | 7278.2716 | 1.502% | 0.2393%
2017-07-08 | 2 | 7406 | 109.3126 | 1.476% | 17.421 | 0.2352% | 126.7336 | 1.711% | 747 | 7388.579 | 7279.2664 | 1.502% | 0.2393%
2017-08-15 | 2 | 7406 | 109.3126 | 1.476% | 17.421 | 0.2352% | 126.7336 | 1.711% | 748 | 7388.579 | 7279.2664 | 1.502% | 0.2393%
2017-06-29 | 10 | 7407 | 109.3169 | 1.476% | 17.4219 | 0.2352% | 126.7388 | 1.711% | 749 | 7389.5781 | 7280.2612 | 1.502% | 0.2393%
2017-07-25 | 7 | 7411 | 109.3339 | 1.475% | 17.4258 | 0.2351% | 126.7597 | 1.71% | 750 | 7393.5742 | 7284.2403 | 1.501% | 0.2392%
2017-08-12 | 9 | 7411 | 109.3339 | 1.475% | 17.4258 | 0.2351% | 126.7597 | 1.71% | 751 | 7393.5742 | 7284.2403 | 1.501% | 0.2392%
2017-08-19 | 8 | 7416 | 109.3552 | 1.475% | 17.4307 | 0.235% | 126.7859 | 1.71% | 752 | 7398.5693 | 7289.2141 | 1.5% | 0.2391%
2017-06-12 | 9 | 7418 | 109.3637 | 1.474% | 17.4327 | 0.235% | 126.7963 | 1.709% | 753 | 7400.5673 | 7291.2037 | 1.5% | 0.2391%
2017-08-17 | 2 | 7418 | 109.3637 | 1.474% | 17.4327 | 0.235% | 126.7963 | 1.709% | 754 | 7400.5673 | 7291.2037 | 1.5% | 0.2391%
2017-08-22 | 7 | 7419 | 109.368 | 1.474% | 17.4336 | 0.235% | 126.8016 | 1.709% | 755 | 7401.5664 | 7292.1984 | 1.5% | 0.2391%
2017-07-13 | 6 | 7420 | 109.3722 | 1.474% | 17.4346 | 0.235% | 126.8068 | 1.709% | 756 | 7402.5654 | 7293.1932 | 1.5% | 0.2391%
2017-07-27 | 8 | 7420 | 109.3722 | 1.474% | 17.4346 | 0.235% | 126.8068 | 1.709% | 757 | 7402.5654 | 7293.1932 | 1.5% | 0.2391%
2017-06-19 | 1 | 7423 | 109.385 | 1.474% | 17.4375 | 0.2349% | 126.8225 | 1.709% | 758 | 7405.5625 | 7296.1775 | 1.499% | 0.239%
2017-07-16 | 24 | 7426 | 109.3978 | 1.473% | 17.4404 | 0.2349% | 126.8382 | 1.708% | 759 | 7408.5596 | 7299.1618 | 1.499% | 0.2389%
2017-08-16 | 2 | 7426 | 109.3978 | 1.473% | 17.4404 | 0.2349% | 126.8382 | 1.708% | 760 | 7408.5596 | 7299.1618 | 1.499% | 0.2389%
2017-08-19 | 4 | 7427 | 109.402 | 1.473% | 17.4414 | 0.2348% | 126.8434 | 1.708% | 761 | 7409.5586 | 7300.1566 | 1.499% | 0.2389%
2017-06-13 | 9 | 7437 | 109.4446 | 1.472% | 17.4511 | 0.2347% | 126.8957 | 1.706% | 762 | 7419.5489 | 7310.1043 | 1.497% | 0.2387%
2017-07-11 | 8 | 7438 | 109.4488 | 1.471% | 17.4521 | 0.2346% | 126.901 | 1.706% | 763 | 7420.5479 | 7311.099 | 1.497% | 0.2387%
2017-07-18 | 8 | 7442 | 109.4659 | 1.471% | 17.456 | 0.2346% | 126.9219 | 1.705% | 764 | 7424.544 | 7315.0781 | 1.496% | 0.2386%
2017-08-13 | 1 | 7442 | 109.4659 | 1.471% | 17.456 | 0.2346% | 126.9219 | 1.705% | 765 | 7424.544 | 7315.0781 | 1.496% | 0.2386%
2017-07-16 | 1 | 7450 | 109.4999 | 1.47% | 17.4638 | 0.2344% | 126.9637 | 1.704% | 766 | 7432.5362 | 7323.0363 | 1.495% | 0.2385%
2017-08-24 | 1 | 7450 | 109.4999 | 1.47% | 17.4638 | 0.2344% | 126.9637 | 1.704% | 767 | 7432.5362 | 7323.0363 | 1.495% | 0.2385%
2017-06-07 | 21 | 7454 | 109.5169 | 1.469% | 17.4677 | 0.2343% | 126.9846 | 1.704% | 768 | 7436.5323 | 7327.0154 | 1.495% | 0.2384%
2017-07-27 | 1 | 7455 | 109.5212 | 1.469% | 17.4687 | 0.2343% | 126.9899 | 1.703% | 769 | 7437.5313 | 7328.0101 | 1.495% | 0.2384%
2017-08-12 | 1 | 7455 | 109.5212 | 1.469% | 17.4687 | 0.2343% | 126.9899 | 1.703% | 770 | 7437.5313 | 7328.0101 | 1.495% | 0.2384%
2017-06-07 | 20 | 7458 | 109.534 | 1.469% | 17.4716 | 0.2343% | 127.0056 | 1.703% | 771 | 7440.5284 | 7330.9944 | 1.494% | 0.2383%
2017-07-23 | 8 | 7464 | 109.5595 | 1.468% | 17.4774 | 0.2342% | 127.0369 | 1.702% | 772 | 7446.5226 | 7336.9631 | 1.493% | 0.2382%
2017-07-28 | 7 | 7464 | 109.5595 | 1.468% | 17.4774 | 0.2342% | 127.0369 | 1.702% | 773 | 7446.5226 | 7336.9631 | 1.493% | 0.2382%
2017-07-12 | 7 | 7472 | 109.5936 | 1.467% | 17.4852 | 0.234% | 127.0788 | 1.701% | 774 | 7454.5148 | 7344.9212 | 1.492% | 0.2381%
2017-08-20 | 1 | 7473 | 109.5978 | 1.467% | 17.4862 | 0.234% | 127.084 | 1.701% | 775 | 7455.5138 | 7345.916 | 1.492% | 0.238%
2017-06-21 | 10 | 7474 | 109.6021 | 1.466% | 17.4871 | 0.234% | 127.0892 | 1.7% | 776 | 7456.5129 | 7346.9108 | 1.492% | 0.238%
2017-07-20 | 1 | 7478 | 109.6191 | 1.466% | 17.491 | 0.2339% | 127.1102 | 1.7% | 777 | 7460.509 | 7350.8898 | 1.491% | 0.2379%
2017-06-13 | 24 | 7483 | 109.6404 | 1.465% | 17.4959 | 0.2338% | 127.1363 | 1.699% | 778 | 7465.5041 | 7355.8637 | 1.491% | 0.2378%
2017-07-14 | 6 | 7486 | 109.6532 | 1.465% | 17.4988 | 0.2338% | 127.152 | 1.699% | 779 | 7468.5012 | 7358.848 | 1.49% | 0.2378%
2017-08-25 | 24 | 7486 | 109.6532 | 1.465% | 17.4988 | 0.2338% | 127.152 | 1.699% | 780 | 7468.5012 | 7358.848 | 1.49% | 0.2378%
2017-08-16 | 7 | 7487 | 109.6574 | 1.465% | 17.4998 | 0.2337% | 127.1572 | 1.698% | 781 | 7469.5002 | 7359.8428 | 1.49% | 0.2378%
2017-06-30 | 24 | 7492 | 109.6787 | 1.464% | 17.5047 | 0.2336% | 127.1834 | 1.698% | 782 | 7474.4953 | 7364.8166 | 1.489% | 0.2377%
2017-07-18 | 24 | 7496 | 109.6957 | 1.463% | 17.5086 | 0.2336% | 127.2043 | 1.697% | 783 | 7478.4914 | 7368.7957 | 1.489% | 0.2376%
2017-07-15 | 4 | 7497 | 109.7 | 1.463% | 17.5095 | 0.2336% | 127.2095 | 1.697% | 784 | 7479.4905 | 7369.7905 | 1.489% | 0.2376%
2017-06-25 | 10 | 7499 | 109.7085 | 1.463% | 17.5115 | 0.2335% | 127.22 | 1.696% | 785 | 7481.4885 | 7371.78 | 1.488% | 0.2375%
2017-08-24 | 24 | 7500 | 109.7128 | 1.463% | 17.5125 | 0.2335% | 127.2252 | 1.696% | 786 | 7482.4875 | 7372.7748 | 1.488% | 0.2375%
2017-08-31 | 9 | 7500 | 109.7128 | 1.463% | 17.5125 | 0.2335% | 127.2252 | 1.696% | 787 | 7482.4875 | 7372.7748 | 1.488% | 0.2375%
2017-06-17 | 24 | 7505 | 109.7341 | 1.462% | 17.5173 | 0.2334% | 127.2514 | 1.696% | 788 | 7487.4827 | 7377.7486 | 1.487% | 0.2374%
2017-07-06 | 1 | 7508 | 109.7468 | 1.462% | 17.5202 | 0.2334% | 127.2671 | 1.695% | 789 | 7490.4798 | 7380.7329 | 1.487% | 0.2374%
2017-07-25 | 2 | 7508 | 109.7468 | 1.462% | 17.5202 | 0.2334% | 127.2671 | 1.695% | 790 | 7490.4798 | 7380.7329 | 1.487% | 0.2374%
2017-06-07 | 12 | 7512 | 109.7639 | 1.461% | 17.5241 | 0.2333% | 127.288 | 1.694% | 791 | 7494.4759 | 7384.712 | 1.486% | 0.2373%
2017-08-08 | 1 | 7513 | 109.7681 | 1.461% | 17.5251 | 0.2333% | 127.2932 | 1.694% | 792 | 7495.4749 | 7385.7068 | 1.486% | 0.2373%
2017-08-29 | 11 | 7520 | 109.7979 | 1.46% | 17.5319 | 0.2331% | 127.3298 | 1.693% | 793 | 7502.4681 | 7392.6702 | 1.485% | 0.2372%
2017-08-13 | 24 | 7523 | 109.8107 | 1.46% | 17.5348 | 0.2331% | 127.3455 | 1.693% | 794 | 7505.4652 | 7395.6545 | 1.485% | 0.2371%
2017-08-27 | 11 | 7523 | 109.8107 | 1.46% | 17.5348 | 0.2331% | 127.3455 | 1.693% | 795 | 7505.4652 | 7395.6545 | 1.485% | 0.2371%
2017-06-22 | 24 | 7526 | 109.8234 | 1.459% | 17.5378 | 0.233% | 127.3612 | 1.692% | 796 | 7508.4622 | 7398.6388 | 1.484% | 0.237%
2017-06-29 | 24 | 7531 | 109.8447 | 1.459% | 17.5426 | 0.2329% | 127.3874 | 1.692% | 797 | 7513.4574 | 7403.6126 | 1.484% | 0.2369%
2017-07-12 | 2 | 7534 | 109.8575 | 1.458% | 17.5455 | 0.2329% | 127.403 | 1.691% | 798 | 7516.4545 | 7406.597 | 1.483% | 0.2369%
2017-06-21 | 24 | 7539 | 109.8788 | 1.457% | 17.5504 | 0.2328% | 127.4292 | 1.69% | 799 | 7521.4496 | 7411.5708 | 1.483% | 0.2368%
2017-06-20 | 23 | 7543 | 109.8958 | 1.457% | 17.5543 | 0.2327% | 127.4501 | 1.69% | 800 | 7525.4457 | 7415.5499 | 1.482% | 0.2367%
2017-07-29 | 9 | 7543 | 109.8958 | 1.457% | 17.5543 | 0.2327% | 127.4501 | 1.69% | 801 | 7525.4457 | 7415.5499 | 1.482% | 0.2367%
2017-06-12 | 24 | 7548 | 109.9171 | 1.456% | 17.5592 | 0.2326% | 127.4763 | 1.689% | 802 | 7530.4408 | 7420.5237 | 1.481% | 0.2366%
2017-07-01 | 10 | 7550 | 109.9256 | 1.456% | 17.5611 | 0.2326% | 127.4867 | 1.689% | 803 | 7532.4389 | 7422.5133 | 1.481% | 0.2366%
2017-08-05 | 24 | 7561 | 109.9724 | 1.454% | 17.5718 | 0.2324% | 127.5443 | 1.687% | 804 | 7543.4282 | 7433.4557 | 1.479% | 0.2364%
2017-06-27 | 10 | 7567 | 109.998 | 1.454% | 17.5777 | 0.2323% | 127.5756 | 1.686% | 805 | 7549.4223 | 7439.4244 | 1.479% | 0.2363%
2017-06-23 | 8 | 7568 | 110.0022 | 1.454% | 17.5786 | 0.2323% | 127.5809 | 1.686% | 806 | 7550.4214 | 7440.4191 | 1.478% | 0.2363%
2017-06-01 | 10 | 7570 | 110.0108 | 1.453% | 17.5806 | 0.2322% | 127.5913 | 1.685% | 807 | 7552.4194 | 7442.4087 | 1.478% | 0.2362%
2017-08-08 | 23 | 7570 | 110.0108 | 1.453% | 17.5806 | 0.2322% | 127.5913 | 1.685% | 808 | 7552.4194 | 7442.4087 | 1.478% | 0.2362%
2017-06-24 | 2 | 7572 | 110.0193 | 1.453% | 17.5825 | 0.2322% | 127.6018 | 1.685% | 809 | 7554.4175 | 7444.3982 | 1.478% | 0.2362%
2017-07-29 | 23 | 7572 | 110.0193 | 1.453% | 17.5825 | 0.2322% | 127.6018 | 1.685% | 810 | 7554.4175 | 7444.3982 | 1.478% | 0.2362%
2017-08-28 | 11 | 7572 | 110.0193 | 1.453% | 17.5825 | 0.2322% | 127.6018 | 1.685% | 811 | 7554.4175 | 7444.3982 | 1.478% | 0.2362%
2017-06-10 | 11 | 7576 | 110.0363 | 1.452% | 17.5864 | 0.2321% | 127.6227 | 1.685% | 812 | 7558.4136 | 7448.3773 | 1.477% | 0.2361%
2017-07-15 | 8 | 7576 | 110.0363 | 1.452% | 17.5864 | 0.2321% | 127.6227 | 1.685% | 813 | 7558.4136 | 7448.3773 | 1.477% | 0.2361%
2017-07-07 | 2 | 7594 | 110.1129 | 1.45% | 17.6039 | 0.2318% | 127.7168 | 1.682% | 814 | 7576.3961 | 7466.2832 | 1.475% | 0.2358%
2017-07-03 | 24 | 7604 | 110.1555 | 1.449% | 17.6137 | 0.2316% | 127.7692 | 1.68% | 815 | 7586.3863 | 7476.2308 | 1.473% | 0.2356%
2017-08-02 | 24 | 7604 | 110.1555 | 1.449% | 17.6137 | 0.2316% | 127.7692 | 1.68% | 816 | 7586.3863 | 7476.2308 | 1.473% | 0.2356%
2017-07-14 | 3 | 7605 | 110.1597 | 1.449% | 17.6146 | 0.2316% | 127.7744 | 1.68% | 817 | 7587.3854 | 7477.2256 | 1.473% | 0.2356%
2017-07-13 | 3 | 7606 | 110.164 | 1.448% | 17.6156 | 0.2316% | 127.7796 | 1.68% | 818 | 7588.3844 | 7478.2204 | 1.473% | 0.2356%
2017-08-10 | 10 | 7606 | 110.164 | 1.448% | 17.6156 | 0.2316% | 127.7796 | 1.68% | 819 | 7588.3844 | 7478.2204 | 1.473% | 0.2356%
2017-08-25 | 9 | 7608 | 110.1725 | 1.448% | 17.6176 | 0.2316% | 127.7901 | 1.68% | 820 | 7590.3824 | 7480.2099 | 1.473% | 0.2355%
2017-08-22 | 1 | 7610 | 110.181 | 1.448% | 17.6195 | 0.2315% | 127.8005 | 1.679% | 821 | 7592.3805 | 7482.1995 | 1.473% | 0.2355%
2017-08-04 | 9 | 7611 | 110.1853 | 1.448% | 17.6205 | 0.2315% | 127.8058 | 1.679% | 822 | 7593.3795 | 7483.1942 | 1.472% | 0.2355%
2017-08-26 | 10 | 7611 | 110.1853 | 1.448% | 17.6205 | 0.2315% | 127.8058 | 1.679% | 823 | 7593.3795 | 7483.1942 | 1.472% | 0.2355%
2017-07-03 | 1 | 7617 | 110.2108 | 1.447% | 17.6263 | 0.2314% | 127.8371 | 1.678% | 824 | 7599.3737 | 7489.1629 | 1.472% | 0.2354%
2017-06-14 | 9 | 7624 | 110.2406 | 1.446% | 17.6331 | 0.2313% | 127.8738 | 1.677% | 825 | 7606.3669 | 7496.1262 | 1.471% | 0.2352%
2017-06-09 | 13 | 7628 | 110.2577 | 1.445% | 17.637 | 0.2312% | 127.8947 | 1.677% | 826 | 7610.363 | 7500.1053 | 1.47% | 0.2352%
2017-08-14 | 8 | 7629 | 110.2619 | 1.445% | 17.638 | 0.2312% | 127.8999 | 1.676% | 827 | 7611.362 | 7501.1001 | 1.47% | 0.2351%
2017-08-09 | 10 | 7630 | 110.2662 | 1.445% | 17.639 | 0.2312% | 127.9051 | 1.676% | 828 | 7612.361 | 7502.0949 | 1.47% | 0.2351%
2017-08-10 | 24 | 7633 | 110.2789 | 1.445% | 17.6419 | 0.2311% | 127.9208 | 1.676% | 829 | 7615.3581 | 7505.0792 | 1.469% | 0.2351%
2017-06-16 | 24 | 7634 | 110.2832 | 1.445% | 17.6429 | 0.2311% | 127.9261 | 1.676% | 830 | 7616.3571 | 7506.0739 | 1.469% | 0.235%
2017-07-09 | 10 | 7647 | 110.3385 | 1.443% | 17.6555 | 0.2309% | 127.994 | 1.674% | 831 | 7629.3445 | 7519.006 | 1.467% | 0.2348%
2017-08-08 | 7 | 7649 | 110.3471 | 1.443% | 17.6575 | 0.2308% | 128.0045 | 1.673% | 832 | 7631.3425 | 7520.9955 | 1.467% | 0.2348%
2017-08-17 | 7 | 7649 | 110.3471 | 1.443% | 17.6575 | 0.2308% | 128.0045 | 1.673% | 833 | 7631.3425 | 7520.9955 | 1.467% | 0.2348%
2017-08-05 | 1 | 7651 | 110.3556 | 1.442% | 17.6594 | 0.2308% | 128.015 | 1.673% | 834 | 7633.3406 | 7522.985 | 1.467% | 0.2347%
2017-06-30 | 9 | 7652 | 110.3598 | 1.442% | 17.6604 | 0.2308% | 128.0202 | 1.673% | 835 | 7634.3396 | 7523.9798 | 1.467% | 0.2347%
2017-06-07 | 19 | 7655 | 110.3726 | 1.442% | 17.6633 | 0.2307% | 128.0359 | 1.673% | 836 | 7637.3367 | 7526.9641 | 1.466% | 0.2347%
2017-06-26 | 10 | 7656 | 110.3769 | 1.442% | 17.6643 | 0.2307% | 128.0411 | 1.672% | 837 | 7638.3357 | 7527.9589 | 1.466% | 0.2346%
2017-06-06 | 10 | 7659 | 110.3896 | 1.441% | 17.6672 | 0.2307% | 128.0568 | 1.672% | 838 | 7641.3328 | 7530.9432 | 1.466% | 0.2346%
2017-08-02 | 10 | 7662 | 110.4024 | 1.441% | 17.6701 | 0.2306% | 128.0725 | 1.672% | 839 | 7644.3299 | 7533.9275 | 1.465% | 0.2345%
2017-06-28 | 23 | 7665 | 110.4152 | 1.441% | 17.673 | 0.2306% | 128.0882 | 1.671% | 840 | 7647.327 | 7536.9118 | 1.465% | 0.2345%
2017-08-26 | 23 | 7665 | 110.4152 | 1.441% | 17.673 | 0.2306% | 128.0882 | 1.671% | 841 | 7647.327 | 7536.9118 | 1.465% | 0.2345%
2017-07-26 | 8 | 7666 | 110.4194 | 1.44% | 17.674 | 0.2306% | 128.0934 | 1.671% | 842 | 7648.326 | 7537.9066 | 1.465% | 0.2345%
2017-08-05 | 10 | 7672 | 110.445 | 1.44% | 17.6798 | 0.2304% | 128.1248 | 1.67% | 843 | 7654.3202 | 7543.8752 | 1.464% | 0.2344%
2017-07-24 | 8 | 7676 | 110.462 | 1.439% | 17.6837 | 0.2304% | 128.1457 | 1.669% | 844 | 7658.3163 | 7547.8543 | 1.463% | 0.2343%
2017-06-27 | 23 | 7677 | 110.4662 | 1.439% | 17.6847 | 0.2304% | 128.1509 | 1.669% | 845 | 7659.3153 | 7548.8491 | 1.463% | 0.2343%
2017-06-20 | 9 | 7678 | 110.4705 | 1.439% | 17.6857 | 0.2303% | 128.1562 | 1.669% | 846 | 7660.3143 | 7549.8438 | 1.463% | 0.2343%
2017-08-23 | 2 | 7678 | 110.4705 | 1.439% | 17.6857 | 0.2303% | 128.1562 | 1.669% | 847 | 7660.3143 | 7549.8438 | 1.463% | 0.2343%
2017-06-07 | 13 | 7686 | 110.5046 | 1.438% | 17.6935 | 0.2302% | 128.198 | 1.668% | 848 | 7668.3065 | 7557.802 | 1.462% | 0.2341%
2017-08-29 | 12 | 7690 | 110.5216 | 1.437% | 17.6974 | 0.2301% | 128.2189 | 1.667% | 849 | 7672.3026 | 7561.7811 | 1.462% | 0.234%
2017-07-23 | 3 | 7696 | 110.5471 | 1.436% | 17.7032 | 0.23% | 128.2503 | 1.666% | 850 | 7678.2968 | 7567.7497 | 1.461% | 0.2339%
2017-07-21 | 2 | 7697 | 110.5514 | 1.436% | 17.7042 | 0.23% | 128.2556 | 1.666% | 851 | 7679.2958 | 7568.7444 | 1.461% | 0.2339%
2017-06-02 | 10 | 7701 | 110.5684 | 1.436% | 17.7081 | 0.2299% | 128.2765 | 1.666% | 852 | 7683.2919 | 7572.7235 | 1.46% | 0.2338%
2017-06-02 | 23 | 7701 | 110.5684 | 1.436% | 17.7081 | 0.2299% | 128.2765 | 1.666% | 853 | 7683.2919 | 7572.7235 | 1.46% | 0.2338%
2017-08-29 | 22 | 7702 | 110.5727 | 1.436% | 17.709 | 0.2299% | 128.2817 | 1.666% | 854 | 7684.291 | 7573.7183 | 1.46% | 0.2338%
2017-08-24 | 8 | 7704 | 110.5812 | 1.435% | 17.711 | 0.2299% | 128.2922 | 1.665% | 855 | 7686.289 | 7575.7078 | 1.46% | 0.2338%
2017-08-21 | 1 | 7705 | 110.5854 | 1.435% | 17.7119 | 0.2299% | 128.2974 | 1.665% | 856 | 7687.2881 | 7576.7026 | 1.46% | 0.2338%
2017-07-31 | 11 | 7717 | 110.6365 | 1.434% | 17.7236 | 0.2297% | 128.3602 | 1.663% | 857 | 7699.2764 | 7588.6398 | 1.458% | 0.2336%
2017-08-07 | 8 | 7717 | 110.6365 | 1.434% | 17.7236 | 0.2297% | 128.3602 | 1.663% | 858 | 7699.2764 | 7588.6398 | 1.458% | 0.2336%
2017-08-03 | 24 | 7719 | 110.645 | 1.433% | 17.7256 | 0.2296% | 128.3706 | 1.663% | 859 | 7701.2744 | 7590.6294 | 1.458% | 0.2335%
2017-07-10 | 24 | 7720 | 110.6493 | 1.433% | 17.7265 | 0.2296% | 128.3758 | 1.663% | 860 | 7702.2735 | 7591.6242 | 1.458% | 0.2335%
2017-07-29 | 1 | 7720 | 110.6493 | 1.433% | 17.7265 | 0.2296% | 128.3758 | 1.663% | 861 | 7702.2735 | 7591.6242 | 1.458% | 0.2335%
2017-07-16 | 10 | 7722 | 110.6578 | 1.433% | 17.7285 | 0.2296% | 128.3863 | 1.663% | 862 | 7704.2715 | 7593.6137 | 1.457% | 0.2335%
2017-07-22 | 2 | 7725 | 110.6706 | 1.433% | 17.7314 | 0.2295% | 128.402 | 1.662% | 863 | 7707.2686 | 7596.598 | 1.457% | 0.2334%
2017-06-03 | 11 | 7730 | 110.6919 | 1.432% | 17.7363 | 0.2294% | 128.4281 | 1.661% | 864 | 7712.2637 | 7601.5719 | 1.456% | 0.2333%
2017-07-13 | 7 | 7732 | 110.7004 | 1.432% | 17.7382 | 0.2294% | 128.4386 | 1.661% | 865 | 7714.2618 | 7603.5614 | 1.456% | 0.2333%
2017-07-19 | 9 | 7732 | 110.7004 | 1.432% | 17.7382 | 0.2294% | 128.4386 | 1.661% | 866 | 7714.2618 | 7603.5614 | 1.456% | 0.2333%
2017-08-21 | 8 | 7732 | 110.7004 | 1.432% | 17.7382 | 0.2294% | 128.4386 | 1.661% | 867 | 7714.2618 | 7603.5614 | 1.456% | 0.2333%
2017-07-17 | 9 | 7733 | 110.7046 | 1.432% | 17.7392 | 0.2294% | 128.4438 | 1.661% | 868 | 7715.2608 | 7604.5562 | 1.456% | 0.2333%
2017-06-21 | 11 | 7737 | 110.7217 | 1.431% | 17.7431 | 0.2293% | 128.4648 | 1.66% | 869 | 7719.2569 | 7608.5352 | 1.455% | 0.2332%
2017-06-28 | 11 | 7737 | 110.7217 | 1.431% | 17.7431 | 0.2293% | 128.4648 | 1.66% | 870 | 7719.2569 | 7608.5352 | 1.455% | 0.2332%
2017-08-19 | 3 | 7737 | 110.7217 | 1.431% | 17.7431 | 0.2293% | 128.4648 | 1.66% | 871 | 7719.2569 | 7608.5352 | 1.455% | 0.2332%
2017-07-04 | 10 | 7739 | 110.7302 | 1.431% | 17.745 | 0.2293% | 128.4752 | 1.66% | 872 | 7721.255 | 7610.5248 | 1.455% | 0.2332%
2017-07-03 | 9 | 7740 | 110.7344 | 1.431% | 17.746 | 0.2293% | 128.4804 | 1.66% | 873 | 7722.254 | 7611.5196 | 1.455% | 0.2331%
2017-08-09 | 23 | 7741 | 110.7387 | 1.431% | 17.747 | 0.2293% | 128.4857 | 1.66% | 874 | 7723.253 | 7612.5143 | 1.455% | 0.2331%
2017-08-18 | 1 | 7745 | 110.7557 | 1.43% | 17.7509 | 0.2292% | 128.5066 | 1.659% | 875 | 7727.2491 | 7616.4934 | 1.454% | 0.2331%
2017-07-18 | 9 | 7752 | 110.7855 | 1.429% | 17.7577 | 0.2291% | 128.5432 | 1.658% | 876 | 7734.2423 | 7623.4568 | 1.453% | 0.2329%
2017-07-30 | 12 | 7752 | 110.7855 | 1.429% | 17.7577 | 0.2291% | 128.5432 | 1.658% | 877 | 7734.2423 | 7623.4568 | 1.453% | 0.2329%
2017-08-30 | 12 | 7757 | 110.8068 | 1.428% | 17.7626 | 0.229% | 128.5694 | 1.657% | 878 | 7739.2374 | 7628.4306 | 1.453% | 0.2328%
2017-08-15 | 7 | 7760 | 110.8196 | 1.428% | 17.7655 | 0.2289% | 128.5851 | 1.657% | 879 | 7742.2345 | 7631.4149 | 1.452% | 0.2328%
2017-08-18 | 7 | 7764 | 110.8366 | 1.428% | 17.7694 | 0.2289% | 128.606 | 1.656% | 880 | 7746.2306 | 7635.394 | 1.452% | 0.2327%
2017-07-09 | 24 | 7768 | 110.8536 | 1.427% | 17.7733 | 0.2288% | 128.6269 | 1.656% | 881 | 7750.2267 | 7639.3731 | 1.451% | 0.2327%
2017-07-31 | 23 | 7775 | 110.8834 | 1.426% | 17.7801 | 0.2287% | 128.6635 | 1.655% | 882 | 7757.2199 | 7646.3365 | 1.45% | 0.2325%
2017-06-03 | 23 | 7777 | 110.8919 | 1.426% | 17.782 | 0.2286% | 128.674 | 1.655% | 883 | 7759.218 | 7648.326 | 1.45% | 0.2325%
2017-08-22 | 8 | 7780 | 110.9047 | 1.426% | 17.7849 | 0.2286% | 128.6897 | 1.654% | 884 | 7762.2151 | 7651.3103 | 1.449% | 0.2324%
2017-08-29 | 13 | 7785 | 110.926 | 1.425% | 17.7898 | 0.2285% | 128.7158 | 1.653% | 885 | 7767.2102 | 7656.2842 | 1.449% | 0.2324%
2017-07-28 | 8 | 7787 | 110.9345 | 1.425% | 17.7917 | 0.2285% | 128.7263 | 1.653% | 886 | 7769.2083 | 7658.2737 | 1.449% | 0.2323%
2017-07-14 | 7 | 7789 | 110.943 | 1.424% | 17.7937 | 0.2284% | 128.7367 | 1.653% | 887 | 7771.2063 | 7660.2633 | 1.448% | 0.2323%
2017-07-15 | 3 | 7793 | 110.9601 | 1.424% | 17.7976 | 0.2284% | 128.7576 | 1.652% | 888 | 7775.2024 | 7664.2424 | 1.448% | 0.2322%
2017-06-05 | 9 | 7798 | 110.9813 | 1.423% | 17.8025 | 0.2283% | 128.7838 | 1.651% | 889 | 7780.1975 | 7669.2162 | 1.447% | 0.2321%
2017-08-03 | 10 | 7801 | 110.9941 | 1.423% | 17.8054 | 0.2282% | 128.7995 | 1.651% | 890 | 7783.1946 | 7672.2005 | 1.447% | 0.2321%
2017-06-07 | 14 | 7808 | 111.0239 | 1.422% | 17.8122 | 0.2281% | 128.8361 | 1.65% | 891 | 7790.1878 | 7679.1639 | 1.446% | 0.232%
2017-06-09 | 22 | 7815 | 111.0537 | 1.421% | 17.819 | 0.228% | 128.8727 | 1.649% | 892 | 7797.181 | 7686.1273 | 1.445% | 0.2318%
2017-06-07 | 15 | 7816 | 111.058 | 1.421% | 17.82 | 0.228% | 128.8779 | 1.649% | 893 | 7798.18 | 7687.1221 | 1.445% | 0.2318%
2017-06-16 | 9 | 7820 | 111.075 | 1.42% | 17.8239 | 0.2279% | 128.8989 | 1.648% | 894 | 7802.1761 | 7691.1011 | 1.444% | 0.2317%
2017-06-07 | 18 | 7821 | 111.0793 | 1.42% | 17.8248 | 0.2279% | 128.9041 | 1.648% | 895 | 7803.1752 | 7692.0959 | 1.444% | 0.2317%
2017-06-06 | 23 | 7822 | 111.0835 | 1.42% | 17.8258 | 0.2279% | 128.9093 | 1.648% | 896 | 7804.1742 | 7693.0907 | 1.444% | 0.2317%
2017-07-10 | 9 | 7824 | 111.092 | 1.42% | 17.8278 | 0.2279% | 128.9198 | 1.648% | 897 | 7806.1722 | 7695.0802 | 1.444% | 0.2317%
2017-07-05 | 9 | 7825 | 111.0963 | 1.42% | 17.8287 | 0.2278% | 128.925 | 1.648% | 898 | 7807.1713 | 7696.075 | 1.444% | 0.2317%
2017-06-22 | 9 | 7827 | 111.1048 | 1.42% | 17.8307 | 0.2278% | 128.9355 | 1.647% | 899 | 7809.1693 | 7698.0645 | 1.443% | 0.2316%
2017-07-28 | 1 | 7835 | 111.1389 | 1.418% | 17.8385 | 0.2277% | 128.9773 | 1.646% | 900 | 7817.1615 | 7706.0227 | 1.442% | 0.2315%
2017-08-15 | 1 | 7839 | 111.1559 | 1.418% | 17.8424 | 0.2276% | 128.9982 | 1.646% | 901 | 7821.1576 | 7710.0018 | 1.442% | 0.2314%
2017-08-30 | 23 | 7841 | 111.1644 | 1.418% | 17.8443 | 0.2276% | 129.0087 | 1.645% | 902 | 7823.1557 | 7711.9913 | 1.441% | 0.2314%
2017-06-15 | 9 | 7844 | 111.1772 | 1.417% | 17.8472 | 0.2275% | 129.0244 | 1.645% | 903 | 7826.1528 | 7714.9756 | 1.441% | 0.2313%
2017-08-11 | 9 | 7846 | 111.1857 | 1.417% | 17.8492 | 0.2275% | 129.0348 | 1.645% | 904 | 7828.1508 | 7716.9652 | 1.441% | 0.2313%
2017-06-19 | 8 | 7847 | 111.1899 | 1.417% | 17.8501 | 0.2275% | 129.0401 | 1.644% | 905 | 7829.1499 | 7717.9599 | 1.441% | 0.2313%
2017-08-31 | 10 | 7850 | 111.2027 | 1.417% | 17.8531 | 0.2274% | 129.0558 | 1.644% | 906 | 7832.1469 | 7720.9442 | 1.44% | 0.2312%
2017-06-26 | 23 | 7854 | 111.2197 | 1.416% | 17.8569 | 0.2274% | 129.0767 | 1.643% | 907 | 7836.1431 | 7724.9233 | 1.44% | 0.2312%
2017-06-07 | 16 | 7865 | 111.2666 | 1.415% | 17.8677 | 0.2272% | 129.1342 | 1.642% | 908 | 7847.1323 | 7735.8658 | 1.438% | 0.231%
2017-07-26 | 1 | 7872 | 111.2964 | 1.414% | 17.8745 | 0.2271% | 129.1708 | 1.641% | 909 | 7854.1255 | 7742.8292 | 1.437% | 0.2309%
2017-06-15 | 24 | 7874 | 111.3049 | 1.414% | 17.8764 | 0.227% | 129.1813 | 1.641% | 910 | 7856.1236 | 7744.8187 | 1.437% | 0.2308%
2017-06-25 | 23 | 7878 | 111.3219 | 1.413% | 17.8803 | 0.227% | 129.2022 | 1.64% | 911 | 7860.1197 | 7748.7978 | 1.437% | 0.2307%
2017-07-25 | 8 | 7880 | 111.3304 | 1.413% | 17.8823 | 0.2269% | 129.2127 | 1.64% | 912 | 7862.1177 | 7750.7873 | 1.436% | 0.2307%
2017-07-08 | 24 | 7881 | 111.3347 | 1.413% | 17.8832 | 0.2269% | 129.2179 | 1.64% | 913 | 7863.1168 | 7751.7821 | 1.436% | 0.2307%
2017-07-07 | 8 | 7886 | 111.356 | 1.412% | 17.8881 | 0.2268% | 129.244 | 1.639% | 914 | 7868.1119 | 7756.756 | 1.436% | 0.2306%
2017-07-17 | 24 | 7886 | 111.356 | 1.412% | 17.8881 | 0.2268% | 129.244 | 1.639% | 915 | 7868.1119 | 7756.756 | 1.436% | 0.2306%
2017-07-21 | 8 | 7886 | 111.356 | 1.412% | 17.8881 | 0.2268% | 129.244 | 1.639% | 916 | 7868.1119 | 7756.756 | 1.436% | 0.2306%
2017-06-05 | 23 | 7888 | 111.3645 | 1.412% | 17.89 | 0.2268% | 129.2545 | 1.639% | 917 | 7870.11 | 7758.7455 | 1.435% | 0.2306%
2017-08-16 | 8 | 7891 | 111.3772 | 1.411% | 17.893 | 0.2268% | 129.2702 | 1.638% | 918 | 7873.107 | 7761.7298 | 1.435% | 0.2305%
2017-06-14 | 24 | 7896 | 111.3985 | 1.411% | 17.8978 | 0.2267% | 129.2963 | 1.637% | 919 | 7878.1022 | 7766.7037 | 1.434% | 0.2304%
2017-06-10 | 23 | 7899 | 111.4113 | 1.41% | 17.9007 | 0.2266% | 129.312 | 1.637% | 920 | 7881.0993 | 7769.688 | 1.434% | 0.2304%
2017-07-01 | 24 | 7902 | 111.4241 | 1.41% | 17.9037 | 0.2266% | 129.3277 | 1.637% | 921 | 7884.0963 | 7772.6723 | 1.434% | 0.2303%
2017-06-04 | 23 | 7908 | 111.4496 | 1.409% | 17.9095 | 0.2265% | 129.3591 | 1.636% | 922 | 7890.0905 | 7778.6409 | 1.433% | 0.2302%
2017-06-17 | 10 | 7909 | 111.4539 | 1.409% | 17.9105 | 0.2265% | 129.3643 | 1.636% | 923 | 7891.0895 | 7779.6357 | 1.433% | 0.2302%
2017-06-07 | 17 | 7913 | 111.4709 | 1.409% | 17.9144 | 0.2264% | 129.3853 | 1.635% | 924 | 7895.0856 | 7783.6147 | 1.432% | 0.2302%
2017-08-06 | 24 | 7913 | 111.4709 | 1.409% | 17.9144 | 0.2264% | 129.3853 | 1.635% | 925 | 7895.0856 | 7783.6147 | 1.432% | 0.2302%
2017-08-27 | 22 | 7914 | 111.4752 | 1.409% | 17.9153 | 0.2264% | 129.3905 | 1.635% | 926 | 7896.0847 | 7784.6095 | 1.432% | 0.2301%
2017-08-06 | 11 | 7916 | 111.4837 | 1.408% | 17.9173 | 0.2263% | 129.4009 | 1.635% | 927 | 7898.0827 | 7786.5991 | 1.432% | 0.2301%
2017-08-23 | 7 | 7922 | 111.5092 | 1.408% | 17.9231 | 0.2262% | 129.4323 | 1.634% | 928 | 7904.0769 | 7792.5677 | 1.431% | 0.23%
2017-08-28 | 12 | 7923 | 111.5135 | 1.407% | 17.9241 | 0.2262% | 129.4376 | 1.634% | 929 | 7905.0759 | 7793.5624 | 1.431% | 0.23%
2017-07-08 | 1 | 7928 | 111.5347 | 1.407% | 17.929 | 0.2261% | 129.4637 | 1.633% | 930 | 7910.071 | 7798.5363 | 1.43% | 0.2299%
2017-06-01 | 23 | 7934 | 111.5603 | 1.406% | 17.9348 | 0.226% | 129.4951 | 1.632% | 931 | 7916.0652 | 7804.5049 | 1.429% | 0.2298%
2017-08-27 | 12 | 7937 | 111.5731 | 1.406% | 17.9377 | 0.226% | 129.5108 | 1.632% | 932 | 7919.0623 | 7807.4892 | 1.429% | 0.2298%
2017-08-29 | 14 | 7937 | 111.5731 | 1.406% | 17.9377 | 0.226% | 129.5108 | 1.632% | 933 | 7919.0623 | 7807.4892 | 1.429% | 0.2298%
2017-06-04 | 11 | 7939 | 111.5816 | 1.405% | 17.9397 | 0.226% | 129.5212 | 1.631% | 934 | 7921.0603 | 7809.4788 | 1.429% | 0.2297%
2017-06-20 | 10 | 7942 | 111.5943 | 1.405% | 17.9426 | 0.2259% | 129.5369 | 1.631% | 935 | 7924.0574 | 7812.4631 | 1.428% | 0.2297%
2017-08-17 | 1 | 7945 | 111.6071 | 1.405% | 17.9455 | 0.2259% | 129.5526 | 1.631% | 936 | 7927.0545 | 7815.4474 | 1.428% | 0.2296%
2017-08-16 | 1 | 7958 | 111.6625 | 1.403% | 17.9582 | 0.2257% | 129.6206 | 1.629% | 937 | 7940.0418 | 7828.3794 | 1.426% | 0.2294%
2017-08-08 | 8 | 7960 | 111.671 | 1.403% | 17.9601 | 0.2256% | 129.6311 | 1.629% | 938 | 7942.0399 | 7830.3689 | 1.426% | 0.2294%
2017-07-14 | 2 | 7963 | 111.6837 | 1.403% | 17.963 | 0.2256% | 129.6468 | 1.628% | 939 | 7945.037 | 7833.3532 | 1.426% | 0.2293%
2017-07-23 | 24 | 7976 | 111.7391 | 1.401% | 17.9757 | 0.2254% | 129.7148 | 1.626% | 940 | 7958.0243 | 7846.2852 | 1.424% | 0.2291%
2017-06-21 | 12 | 7978 | 111.7476 | 1.401% | 17.9776 | 0.2253% | 129.7252 | 1.626% | 941 | 7960.0224 | 7848.2748 | 1.424% | 0.2291%
2017-08-28 | 22 | 7984 | 111.7731 | 1.4% | 17.9835 | 0.2252% | 129.7566 | 1.625% | 942 | 7966.0165 | 7854.2434 | 1.423% | 0.229%
2017-08-31 | 23 | 7990 | 111.7987 | 1.399% | 17.9893 | 0.2251% | 129.788 | 1.624% | 943 | 7972.0107 | 7860.212 | 1.422% | 0.2289%
2017-06-23 | 9 | 7995 | 111.82 | 1.399% | 17.9942 | 0.2251% | 129.8141 | 1.624% | 944 | 7977.0058 | 7865.1859 | 1.422% | 0.2288%
2017-07-13 | 2 | 8000 | 111.8412 | 1.398% | 17.999 | 0.225% | 129.8403 | 1.623% | 945 | 7982.001 | 7870.1597 | 1.421% | 0.2287%
2017-08-01 | 11 | 8001 | 111.8455 | 1.398% | 18 | 0.225% | 129.8455 | 1.623% | 946 | 7983 | 7871.1545 | 1.421% | 0.2287%
2017-08-29 | 20 | 8002 | 111.8498 | 1.398% | 18.001 | 0.225% | 129.8507 | 1.623% | 947 | 7983.999 | 7872.1493 | 1.421% | 0.2287%
2017-07-18 | 10 | 8005 | 111.8625 | 1.397% | 18.0039 | 0.2249% | 129.8664 | 1.622% | 948 | 7986.9961 | 7875.1336 | 1.42% | 0.2286%
2017-07-08 | 9 | 8008 | 111.8753 | 1.397% | 18.0068 | 0.2249% | 129.8821 | 1.622% | 949 | 7989.9932 | 7878.1179 | 1.42% | 0.2286%
2017-07-12 | 1 | 8008 | 111.8753 | 1.397% | 18.0068 | 0.2249% | 129.8821 | 1.622% | 950 | 7989.9932 | 7878.1179 | 1.42% | 0.2286%
2017-07-25 | 1 | 8010 | 111.8838 | 1.397% | 18.0088 | 0.2248% | 129.8926 | 1.622% | 951 | 7991.9912 | 7880.1074 | 1.42% | 0.2285%
2017-06-13 | 10 | 8014 | 111.9008 | 1.396% | 18.0127 | 0.2248% | 129.9135 | 1.621% | 952 | 7995.9873 | 7884.0865 | 1.419% | 0.2285%
2017-06-18 | 10 | 8015 | 111.9051 | 1.396% | 18.0136 | 0.2247% | 129.9187 | 1.621% | 953 | 7996.9864 | 7885.0813 | 1.419% | 0.2285%
2017-06-25 | 11 | 8019 | 111.9221 | 1.396% | 18.0175 | 0.2247% | 129.9397 | 1.62% | 954 | 8000.9825 | 7889.0603 | 1.419% | 0.2284%
2017-08-24 | 9 | 8019 | 111.9221 | 1.396% | 18.0175 | 0.2247% | 129.9397 | 1.62% | 955 | 8000.9825 | 7889.0603 | 1.419% | 0.2284%
2017-07-29 | 10 | 8021 | 111.9306 | 1.395% | 18.0195 | 0.2247% | 129.9501 | 1.62% | 956 | 8002.9805 | 7891.0499 | 1.418% | 0.2284%
2017-06-19 | 24 | 8024 | 111.9434 | 1.395% | 18.0224 | 0.2246% | 129.9658 | 1.62% | 957 | 8005.9776 | 7894.0342 | 1.418% | 0.2283%
2017-07-04 | 24 | 8029 | 111.9647 | 1.395% | 18.0273 | 0.2245% | 129.992 | 1.619% | 958 | 8010.9727 | 7899.008 | 1.417% | 0.2282%
2017-07-30 | 22 | 8029 | 111.9647 | 1.395% | 18.0273 | 0.2245% | 129.992 | 1.619% | 959 | 8010.9727 | 7899.008 | 1.417% | 0.2282%
2017-06-09 | 14 | 8034 | 111.986 | 1.394% | 18.0321 | 0.2244% | 130.0181 | 1.618% | 960 | 8015.9679 | 7903.9819 | 1.417% | 0.2281%
2017-07-02 | 10 | 8037 | 111.9988 | 1.394% | 18.035 | 0.2244% | 130.0338 | 1.618% | 961 | 8018.965 | 7906.9662 | 1.416% | 0.2281%
2017-08-12 | 10 | 8037 | 111.9988 | 1.394% | 18.035 | 0.2244% | 130.0338 | 1.618% | 962 | 8018.965 | 7906.9662 | 1.416% | 0.2281%
2017-07-06 | 9 | 8040 | 112.0115 | 1.393% | 18.038 | 0.2244% | 130.0495 | 1.618% | 963 | 8021.962 | 7909.9505 | 1.416% | 0.228%
2017-08-09 | 11 | 8042 | 112.02 | 1.393% | 18.0399 | 0.2243% | 130.0599 | 1.617% | 964 | 8023.9601 | 7911.9401 | 1.416% | 0.228%
2017-06-24 | 23 | 8049 | 112.0498 | 1.392% | 18.0467 | 0.2242% | 130.0966 | 1.616% | 965 | 8030.9533 | 7918.9034 | 1.415% | 0.2279%
2017-06-12 | 10 | 8051 | 112.0584 | 1.392% | 18.0487 | 0.2242% | 130.107 | 1.616% | 966 | 8032.9513 | 7920.893 | 1.415% | 0.2279%
2017-08-29 | 15 | 8054 | 112.0711 | 1.391% | 18.0516 | 0.2241% | 130.1227 | 1.616% | 967 | 8035.9484 | 7923.8773 | 1.414% | 0.2278%
2017-08-17 | 8 | 8056 | 112.0796 | 1.391% | 18.0535 | 0.2241% | 130.1332 | 1.615% | 968 | 8037.9465 | 7925.8668 | 1.414% | 0.2278%
2017-08-14 | 9 | 8060 | 112.0967 | 1.391% | 18.0574 | 0.224% | 130.1541 | 1.615% | 969 | 8041.9426 | 7929.8459 | 1.414% | 0.2277%
2017-08-01 | 23 | 8065 | 112.118 | 1.39% | 18.0623 | 0.224% | 130.1802 | 1.614% | 970 | 8046.9377 | 7934.8198 | 1.413% | 0.2276%
2017-07-27 | 9 | 8067 | 112.1265 | 1.39% | 18.0642 | 0.2239% | 130.1907 | 1.614% | 971 | 8048.9358 | 7936.8093 | 1.413% | 0.2276%
2017-08-29 | 19 | 8067 | 112.1265 | 1.39% | 18.0642 | 0.2239% | 130.1907 | 1.614% | 972 | 8048.9358 | 7936.8093 | 1.413% | 0.2276%
2017-06-24 | 1 | 8068 | 112.1307 | 1.39% | 18.0652 | 0.2239% | 130.1959 | 1.614% | 973 | 8049.9348 | 7937.8041 | 1.413% | 0.2276%
2017-08-11 | 24 | 8076 | 112.1648 | 1.389% | 18.073 | 0.2238% | 130.2378 | 1.613% | 974 | 8057.927 | 7945.7622 | 1.412% | 0.2275%
2017-07-12 | 8 | 8077 | 112.169 | 1.389% | 18.074 | 0.2238% | 130.243 | 1.613% | 975 | 8058.926 | 7946.757 | 1.412% | 0.2274%
2017-08-29 | 16 | 8077 | 112.169 | 1.389% | 18.074 | 0.2238% | 130.243 | 1.613% | 976 | 8058.926 | 7946.757 | 1.412% | 0.2274%
2017-07-11 | 9 | 8078 | 112.1733 | 1.389% | 18.0749 | 0.2238% | 130.2482 | 1.612% | 977 | 8059.9251 | 7947.7518 | 1.411% | 0.2274%
2017-06-11 | 11 | 8081 | 112.1861 | 1.388% | 18.0779 | 0.2237% | 130.2639 | 1.612% | 978 | 8062.9221 | 7950.7361 | 1.411% | 0.2274%
2017-07-01 | 11 | 8088 | 112.2159 | 1.387% | 18.0847 | 0.2236% | 130.3005 | 1.611% | 979 | 8069.9153 | 7957.6995 | 1.41% | 0.2273%
2017-08-12 | 24 | 8089 | 112.2201 | 1.387% | 18.0856 | 0.2236% | 130.3058 | 1.611% | 980 | 8070.9144 | 7958.6942 | 1.41% | 0.2272%
2017-07-22 | 9 | 8095 | 112.2457 | 1.387% | 18.0915 | 0.2235% | 130.3371 | 1.61% | 981 | 8076.9085 | 7964.6629 | 1.409% | 0.2271%
2017-06-09 | 21 | 8104 | 112.284 | 1.386% | 18.1002 | 0.2233% | 130.3842 | 1.609% | 982 | 8085.8998 | 7973.6158 | 1.408% | 0.227%
2017-08-07 | 9 | 8104 | 112.284 | 1.386% | 18.1002 | 0.2233% | 130.3842 | 1.609% | 983 | 8085.8998 | 7973.6158 | 1.408% | 0.227%
2017-06-06 | 11 | 8105 | 112.2882 | 1.385% | 18.1012 | 0.2233% | 130.3894 | 1.609% | 984 | 8086.8988 | 7974.6106 | 1.408% | 0.227%
2017-08-29 | 21 | 8110 | 112.3095 | 1.385% | 18.1061 | 0.2233% | 130.4156 | 1.608% | 985 | 8091.8939 | 7979.5844 | 1.407% | 0.2269%
2017-07-17 | 10 | 8116 | 112.3351 | 1.384% | 18.1119 | 0.2232% | 130.447 | 1.607% | 986 | 8097.8881 | 7985.553 | 1.407% | 0.2268%
2017-08-20 | 10 | 8118 | 112.3436 | 1.384% | 18.1139 | 0.2231% | 130.4574 | 1.607% | 987 | 8099.8861 | 7987.5426 | 1.406% | 0.2268%
2017-08-13 | 10 | 8119 | 112.3478 | 1.384% | 18.1148 | 0.2231% | 130.4627 | 1.607% | 988 | 8100.8852 | 7988.5373 | 1.406% | 0.2268%
2017-06-29 | 11 | 8120 | 112.3521 | 1.384% | 18.1158 | 0.2231% | 130.4679 | 1.607% | 989 | 8101.8842 | 7989.5321 | 1.406% | 0.2267%
2017-08-07 | 24 | 8121 | 112.3563 | 1.384% | 18.1168 | 0.2231% | 130.4731 | 1.607% | 990 | 8102.8832 | 7990.5269 | 1.406% | 0.2267%
2017-06-30 | 23 | 8122 | 112.3606 | 1.383% | 18.1178 | 0.2231% | 130.4784 | 1.606% | 991 | 8103.8822 | 7991.5216 | 1.406% | 0.2267%
2017-07-07 | 1 | 8123 | 112.3649 | 1.383% | 18.1187 | 0.2231% | 130.4836 | 1.606% | 992 | 8104.8813 | 7992.5164 | 1.406% | 0.2267%
2017-06-24 | 9 | 8124 | 112.3691 | 1.383% | 18.1197 | 0.223% | 130.4888 | 1.606% | 993 | 8105.8803 | 7993.5112 | 1.406% | 0.2267%
2017-08-10 | 11 | 8126 | 112.3776 | 1.383% | 18.1216 | 0.223% | 130.4993 | 1.606% | 994 | 8107.8784 | 7995.5007 | 1.406% | 0.2266%
2017-08-04 | 10 | 8131 | 112.3989 | 1.382% | 18.1265 | 0.2229% | 130.5254 | 1.605% | 995 | 8112.8735 | 8000.4746 | 1.405% | 0.2266%
2017-08-29 | 18 | 8135 | 112.4159 | 1.382% | 18.1304 | 0.2229% | 130.5463 | 1.605% | 996 | 8116.8696 | 8004.4537 | 1.404% | 0.2265%
2017-08-23 | 24 | 8137 | 112.4245 | 1.382% | 18.1324 | 0.2228% | 130.5568 | 1.604% | 997 | 8118.8676 | 8006.4432 | 1.404% | 0.2265%
2017-06-18 | 24 | 8139 | 112.433 | 1.381% | 18.1343 | 0.2228% | 130.5673 | 1.604% | 998 | 8120.8657 | 8008.4327 | 1.404% | 0.2264%
2017-07-26 | 9 | 8139 | 112.433 | 1.381% | 18.1343 | 0.2228% | 130.5673 | 1.604% | 999 | 8120.8657 | 8008.4327 | 1.404% | 0.2264%
2017-07-15 | 24 | 8140 | 112.4372 | 1.381% | 18.1353 | 0.2228% | 130.5725 | 1.604% | 1000 | 8121.8647 | 8009.4275 | 1.404% | 0.2264%
2017-08-08 | 22 | 8146 | 112.4628 | 1.381% | 18.1411 | 0.2227% | 130.6039 | 1.603% | 1001 | 8127.8589 | 8015.3961 | 1.403% | 0.2263%
2017-08-19 | 24 | 8152 | 112.4883 | 1.38% | 18.147 | 0.2226% | 130.6353 | 1.602% | 1002 | 8133.853 | 8021.3647 | 1.402% | 0.2262%
2017-07-30 | 13 | 8154 | 112.4968 | 1.38% | 18.1489 | 0.2226% | 130.6457 | 1.602% | 1003 | 8135.8511 | 8023.3543 | 1.402% | 0.2262%
2017-08-23 | 1 | 8154 | 112.4968 | 1.38% | 18.1489 | 0.2226% | 130.6457 | 1.602% | 1004 | 8135.8511 | 8023.3543 | 1.402% | 0.2262%
2017-06-27 | 11 | 8155 | 112.5011 | 1.38% | 18.1499 | 0.2226% | 130.6509 | 1.602% | 1005 | 8136.8501 | 8024.3491 | 1.402% | 0.2262%
2017-07-16 | 23 | 8158 | 112.5138 | 1.379% | 18.1528 | 0.2225% | 130.6666 | 1.602% | 1006 | 8139.8472 | 8027.3334 | 1.402% | 0.2261%
2017-06-28 | 12 | 8160 | 112.5224 | 1.379% | 18.1547 | 0.2225% | 130.6771 | 1.601% | 1007 | 8141.8453 | 8029.3229 | 1.401% | 0.2261%
2017-08-25 | 10 | 8162 | 112.5309 | 1.379% | 18.1567 | 0.2225% | 130.6876 | 1.601% | 1008 | 8143.8433 | 8031.3124 | 1.401% | 0.2261%
2017-08-15 | 8 | 8165 | 112.5436 | 1.378% | 18.1596 | 0.2224% | 130.7033 | 1.601% | 1009 | 8146.8404 | 8034.2967 | 1.401% | 0.226%
2017-08-29 | 17 | 8168 | 112.5564 | 1.378% | 18.1625 | 0.2224% | 130.7189 | 1.6% | 1010 | 8149.8375 | 8037.2811 | 1.4% | 0.226%
2017-06-20 | 22 | 8173 | 112.5777 | 1.377% | 18.1674 | 0.2223% | 130.7451 | 1.6% | 1011 | 8154.8326 | 8042.2549 | 1.4% | 0.2259%
2017-07-20 | 9 | 8173 | 112.5777 | 1.377% | 18.1674 | 0.2223% | 130.7451 | 1.6% | 1012 | 8154.8326 | 8042.2549 | 1.4% | 0.2259%
2017-07-23 | 2 | 8183 | 112.6203 | 1.376% | 18.1771 | 0.2221% | 130.7974 | 1.598% | 1013 | 8164.8229 | 8052.2026 | 1.399% | 0.2257%
2017-06-10 | 12 | 8185 | 112.6288 | 1.376% | 18.1791 | 0.2221% | 130.8079 | 1.598% | 1014 | 8166.8209 | 8054.1921 | 1.398% | 0.2257%
2017-08-25 | 23 | 8190 | 112.6501 | 1.375% | 18.1839 | 0.222% | 130.834 | 1.597% | 1015 | 8171.8161 | 8059.166 | 1.398% | 0.2256%
2017-07-26 | 24 | 8192 | 112.6586 | 1.375% | 18.1859 | 0.222% | 130.8445 | 1.597% | 1016 | 8173.8141 | 8061.1555 | 1.398% | 0.2256%
2017-08-19 | 9 | 8194 | 112.6671 | 1.375% | 18.1878 | 0.222% | 130.8549 | 1.597% | 1017 | 8175.8122 | 8063.1451 | 1.397% | 0.2256%
2017-08-18 | 8 | 8195 | 112.6714 | 1.375% | 18.1888 | 0.2219% | 130.8602 | 1.597% | 1018 | 8176.8112 | 8064.1398 | 1.397% | 0.2256%
2017-06-17 | 23 | 8197 | 112.6799 | 1.375% | 18.1907 | 0.2219% | 130.8706 | 1.597% | 1019 | 8178.8093 | 8066.1294 | 1.397% | 0.2255%
2017-08-02 | 11 | 8197 | 112.6799 | 1.375% | 18.1907 | 0.2219% | 130.8706 | 1.597% | 1020 | 8178.8093 | 8066.1294 | 1.397% | 0.2255%
2017-06-11 | 23 | 8200 | 112.6926 | 1.374% | 18.1937 | 0.2219% | 130.8863 | 1.596% | 1021 | 8181.8063 | 8069.1137 | 1.397% | 0.2255%
2017-08-19 | 2 | 8202 | 112.7012 | 1.374% | 18.1956 | 0.2218% | 130.8968 | 1.596% | 1022 | 8183.8044 | 8071.1032 | 1.396% | 0.2254%
2017-08-13 | 23 | 8205 | 112.7139 | 1.374% | 18.1985 | 0.2218% | 130.9125 | 1.596% | 1023 | 8186.8015 | 8074.0875 | 1.396% | 0.2254%
2017-06-02 | 11 | 8209 | 112.731 | 1.373% | 18.2024 | 0.2217% | 130.9334 | 1.595% | 1024 | 8190.7976 | 8078.0666 | 1.396% | 0.2253%
2017-06-26 | 11 | 8210 | 112.7352 | 1.373% | 18.2034 | 0.2217% | 130.9386 | 1.595% | 1025 | 8191.7966 | 8079.0614 | 1.395% | 0.2253%
2017-07-19 | 24 | 8214 | 112.7522 | 1.373% | 18.2073 | 0.2217% | 130.9595 | 1.594% | 1026 | 8195.7927 | 8083.0405 | 1.395% | 0.2253%
2017-08-28 | 13 | 8223 | 112.7906 | 1.372% | 18.216 | 0.2215% | 131.0066 | 1.593% | 1027 | 8204.784 | 8091.9934 | 1.394% | 0.2251%
2017-07-31 | 12 | 8225 | 112.7991 | 1.371% | 18.218 | 0.2215% | 131.0171 | 1.593% | 1028 | 8206.782 | 8093.9829 | 1.394% | 0.2251%
2017-07-29 | 22 | 8228 | 112.8118 | 1.371% | 18.2209 | 0.2215% | 131.0327 | 1.593% | 1029 | 8209.7791 | 8096.9673 | 1.393% | 0.225%
2017-07-24 | 9 | 8229 | 112.8161 | 1.371% | 18.2219 | 0.2214% | 131.038 | 1.592% | 1030 | 8210.7781 | 8097.962 | 1.393% | 0.225%
2017-08-23 | 8 | 8237 | 112.8501 | 1.37% | 18.2297 | 0.2213% | 131.0798 | 1.591% | 1031 | 8218.7703 | 8105.9202 | 1.392% | 0.2249%
2017-06-05 | 10 | 8243 | 112.8757 | 1.369% | 18.2355 | 0.2212% | 131.1112 | 1.591% | 1032 | 8224.7645 | 8111.8888 | 1.391% | 0.2248%
2017-07-21 | 1 | 8244 | 112.8799 | 1.369% | 18.2365 | 0.2212% | 131.1164 | 1.59% | 1033 | 8225.7635 | 8112.8836 | 1.391% | 0.2248%
2017-07-16 | 11 | 8245 | 112.8842 | 1.369% | 18.2375 | 0.2212% | 131.1217 | 1.59% | 1034 | 8226.7625 | 8113.8783 | 1.391% | 0.2248%
2017-08-21 | 9 | 8250 | 112.9055 | 1.369% | 18.2423 | 0.2211% | 131.1478 | 1.59% | 1035 | 8231.7577 | 8118.8522 | 1.391% | 0.2247%
2017-08-30 | 13 | 8250 | 112.9055 | 1.369% | 18.2423 | 0.2211% | 131.1478 | 1.59% | 1036 | 8231.7577 | 8118.8522 | 1.391% | 0.2247%
2017-07-15 | 2 | 8251 | 112.9097 | 1.368% | 18.2433 | 0.2211% | 131.153 | 1.59% | 1037 | 8232.7567 | 8119.847 | 1.391% | 0.2247%
2017-08-04 | 24 | 8251 | 112.9097 | 1.368% | 18.2433 | 0.2211% | 131.153 | 1.59% | 1038 | 8232.7567 | 8119.847 | 1.391% | 0.2247%
2017-08-24 | 23 | 8256 | 112.931 | 1.368% | 18.2482 | 0.221% | 131.1792 | 1.589% | 1039 | 8237.7518 | 8124.8208 | 1.39% | 0.2246%
2017-06-22 | 23 | 8257 | 112.9353 | 1.368% | 18.2491 | 0.221% | 131.1844 | 1.589% | 1040 | 8238.7509 | 8125.8156 | 1.39% | 0.2246%
2017-07-22 | 1 | 8259 | 112.9438 | 1.368% | 18.2511 | 0.221% | 131.1949 | 1.589% | 1041 | 8240.7489 | 8127.8051 | 1.39% | 0.2246%
2017-06-20 | 11 | 8263 | 112.9608 | 1.367% | 18.255 | 0.2209% | 131.2158 | 1.588% | 1042 | 8244.745 | 8131.7842 | 1.389% | 0.2245%
2017-07-05 | 24 | 8263 | 112.9608 | 1.367% | 18.255 | 0.2209% | 131.2158 | 1.588% | 1043 | 8244.745 | 8131.7842 | 1.389% | 0.2245%
2017-07-03 | 23 | 8270 | 112.9906 | 1.366% | 18.2618 | 0.2208% | 131.2524 | 1.587% | 1044 | 8251.7382 | 8138.7476 | 1.388% | 0.2244%
2017-08-26 | 11 | 8280 | 113.0332 | 1.365% | 18.2715 | 0.2207% | 131.3047 | 1.586% | 1045 | 8261.7285 | 8148.6953 | 1.387% | 0.2242%
2017-08-08 | 9 | 8285 | 113.0545 | 1.365% | 18.2764 | 0.2206% | 131.3309 | 1.585% | 1046 | 8266.7236 | 8153.6691 | 1.387% | 0.2241%
2017-06-03 | 12 | 8307 | 113.1481 | 1.362% | 18.2978 | 0.2203% | 131.4459 | 1.582% | 1047 | 8288.7022 | 8175.5541 | 1.384% | 0.2238%
2017-06-14 | 10 | 8312 | 113.1694 | 1.362% | 18.3027 | 0.2202% | 131.4721 | 1.582% | 1048 | 8293.6973 | 8180.5279 | 1.383% | 0.2237%
2017-06-30 | 10 | 8315 | 113.1822 | 1.361% | 18.3056 | 0.2202% | 131.4878 | 1.581% | 1049 | 8296.6944 | 8183.5122 | 1.383% | 0.2237%
2017-07-28 | 9 | 8318 | 113.195 | 1.361% | 18.3085 | 0.2201% | 131.5035 | 1.581% | 1050 | 8299.6915 | 8186.4965 | 1.383% | 0.2236%
2017-08-22 | 9 | 8318 | 113.195 | 1.361% | 18.3085 | 0.2201% | 131.5035 | 1.581% | 1051 | 8299.6915 | 8186.4965 | 1.383% | 0.2236%
2017-07-13 | 8 | 8320 | 113.2035 | 1.361% | 18.3104 | 0.2201% | 131.5139 | 1.581% | 1052 | 8301.6896 | 8188.4861 | 1.382% | 0.2236%
2017-08-27 | 13 | 8321 | 113.2077 | 1.361% | 18.3114 | 0.2201% | 131.5191 | 1.581% | 1053 | 8302.6886 | 8189.4809 | 1.382% | 0.2236%
2017-07-02 | 24 | 8327 | 113.2333 | 1.36% | 18.3173 | 0.22% | 131.5505 | 1.58% | 1054 | 8308.6827 | 8195.4495 | 1.382% | 0.2235%
2017-07-18 | 23 | 8329 | 113.2418 | 1.36% | 18.3192 | 0.2199% | 131.561 | 1.58% | 1055 | 8310.6808 | 8197.439 | 1.381% | 0.2235%
2017-08-21 | 24 | 8335 | 113.2673 | 1.359% | 18.325 | 0.2199% | 131.5924 | 1.579% | 1056 | 8316.675 | 8203.4076 | 1.381% | 0.2234%
2017-07-23 | 9 | 8337 | 113.2758 | 1.359% | 18.327 | 0.2198% | 131.6028 | 1.579% | 1057 | 8318.673 | 8205.3972 | 1.381% | 0.2234%
2017-08-11 | 10 | 8340 | 113.2886 | 1.358% | 18.3299 | 0.2198% | 131.6185 | 1.578% | 1058 | 8321.6701 | 8208.3815 | 1.38% | 0.2233%
2017-07-28 | 24 | 8343 | 113.3014 | 1.358% | 18.3328 | 0.2197% | 131.6342 | 1.578% | 1059 | 8324.6672 | 8211.3658 | 1.38% | 0.2233%
2017-08-17 | 24 | 8343 | 113.3014 | 1.358% | 18.3328 | 0.2197% | 131.6342 | 1.578% | 1060 | 8324.6672 | 8211.3658 | 1.38% | 0.2233%
2017-08-10 | 23 | 8345 | 113.3099 | 1.358% | 18.3348 | 0.2197% | 131.6447 | 1.578% | 1061 | 8326.6652 | 8213.3553 | 1.38% | 0.2232%
2017-08-09 | 12 | 8346 | 113.3142 | 1.358% | 18.3357 | 0.2197% | 131.6499 | 1.577% | 1062 | 8327.6643 | 8214.3501 | 1.379% | 0.2232%
2017-08-31 | 11 | 8347 | 113.3184 | 1.358% | 18.3367 | 0.2197% | 131.6551 | 1.577% | 1063 | 8328.6633 | 8215.3449 | 1.379% | 0.2232%
2017-06-16 | 23 | 8352 | 113.3397 | 1.357% | 18.3416 | 0.2196% | 131.6813 | 1.577% | 1064 | 8333.6584 | 8220.3187 | 1.379% | 0.2231%
2017-06-21 | 23 | 8352 | 113.3397 | 1.357% | 18.3416 | 0.2196% | 131.6813 | 1.577% | 1065 | 8333.6584 | 8220.3187 | 1.379% | 0.2231%
2017-08-26 | 22 | 8352 | 113.3397 | 1.357% | 18.3416 | 0.2196% | 131.6813 | 1.577% | 1066 | 8333.6584 | 8220.3187 | 1.379% | 0.2231%
2017-07-14 | 8 | 8356 | 113.3567 | 1.357% | 18.3455 | 0.2195% | 131.7022 | 1.576% | 1067 | 8337.6545 | 8224.2978 | 1.378% | 0.2231%
2017-08-05 | 11 | 8366 | 113.3993 | 1.355% | 18.3552 | 0.2194% | 131.7545 | 1.575% | 1068 | 8347.6448 | 8234.2455 | 1.377% | 0.2229%
2017-08-05 | 23 | 8371 | 113.4206 | 1.355% | 18.3601 | 0.2193% | 131.7807 | 1.574% | 1069 | 8352.6399 | 8239.2193 | 1.377% | 0.2228%
2017-07-15 | 9 | 8375 | 113.4376 | 1.354% | 18.364 | 0.2193% | 131.8016 | 1.574% | 1070 | 8356.636 | 8243.1984 | 1.376% | 0.2228%
2017-06-09 | 15 | 8379 | 113.4546 | 1.354% | 18.3679 | 0.2192% | 131.8225 | 1.573% | 1071 | 8360.6321 | 8247.1775 | 1.376% | 0.2227%
2017-06-20 | 20 | 8380 | 113.4589 | 1.354% | 18.3688 | 0.2192% | 131.8277 | 1.573% | 1072 | 8361.6312 | 8248.1723 | 1.376% | 0.2227%
2017-06-20 | 21 | 8381 | 113.4632 | 1.354% | 18.3698 | 0.2192% | 131.833 | 1.573% | 1073 | 8362.6302 | 8249.167 | 1.375% | 0.2227%
2017-08-03 | 11 | 8384 | 113.4759 | 1.353% | 18.3727 | 0.2191% | 131.8486 | 1.573% | 1074 | 8365.6273 | 8252.1514 | 1.375% | 0.2226%
2017-07-10 | 10 | 8390 | 113.5015 | 1.353% | 18.3786 | 0.2191% | 131.88 | 1.572% | 1075 | 8371.6214 | 8258.12 | 1.374% | 0.2226%
2017-08-28 | 14 | 8391 | 113.5057 | 1.353% | 18.3795 | 0.219% | 131.8853 | 1.572% | 1076 | 8372.6205 | 8259.1147 | 1.374% | 0.2225%
2017-07-19 | 10 | 8392 | 113.51 | 1.353% | 18.3805 | 0.219% | 131.8905 | 1.572% | 1077 | 8373.6195 | 8260.1095 | 1.374% | 0.2225%
2017-06-22 | 10 | 8394 | 113.5185 | 1.352% | 18.3825 | 0.219% | 131.9009 | 1.571% | 1078 | 8375.6175 | 8262.0991 | 1.374% | 0.2225%
2017-08-24 | 10 | 8394 | 113.5185 | 1.352% | 18.3825 | 0.219% | 131.9009 | 1.571% | 1079 | 8375.6175 | 8262.0991 | 1.374% | 0.2225%
2017-07-09 | 11 | 8395 | 113.5227 | 1.352% | 18.3834 | 0.219% | 131.9062 | 1.571% | 1080 | 8376.6166 | 8263.0938 | 1.374% | 0.2225%
2017-08-28 | 19 | 8398 | 113.5355 | 1.352% | 18.3863 | 0.2189% | 131.9219 | 1.571% | 1081 | 8379.6137 | 8266.0781 | 1.374% | 0.2224%
2017-06-29 | 23 | 8400 | 113.544 | 1.352% | 18.3883 | 0.2189% | 131.9323 | 1.571% | 1082 | 8381.6117 | 8268.0677 | 1.373% | 0.2224%
2017-07-30 | 21 | 8409 | 113.5823 | 1.351% | 18.3971 | 0.2188% | 131.9794 | 1.57% | 1083 | 8390.6029 | 8277.0206 | 1.372% | 0.2223%
2017-08-08 | 20 | 8421 | 113.6334 | 1.349% | 18.4087 | 0.2186% | 132.0422 | 1.568% | 1084 | 8402.5913 | 8288.9578 | 1.371% | 0.2221%
2017-08-28 | 21 | 8424 | 113.6462 | 1.349% | 18.4117 | 0.2186% | 132.0579 | 1.568% | 1085 | 8405.5883 | 8291.9421 | 1.371% | 0.222%
2017-06-16 | 10 | 8432 | 113.6803 | 1.348% | 18.4194 | 0.2184% | 132.0997 | 1.567% | 1086 | 8413.5806 | 8299.9003 | 1.37% | 0.2219%
2017-06-19 | 9 | 8436 | 113.6973 | 1.348% | 18.4233 | 0.2184% | 132.1206 | 1.566% | 1087 | 8417.5767 | 8303.8794 | 1.369% | 0.2219%
2017-08-20 | 24 | 8436 | 113.6973 | 1.348% | 18.4233 | 0.2184% | 132.1206 | 1.566% | 1088 | 8417.5767 | 8303.8794 | 1.369% | 0.2219%
2017-06-23 | 10 | 8437 | 113.7015 | 1.348% | 18.4243 | 0.2184% | 132.1258 | 1.566% | 1089 | 8418.5757 | 8304.8742 | 1.369% | 0.2218%
2017-08-08 | 21 | 8438 | 113.7058 | 1.348% | 18.4253 | 0.2184% | 132.1311 | 1.566% | 1090 | 8419.5747 | 8305.8689 | 1.369% | 0.2218%
2017-06-13 | 23 | 8443 | 113.7271 | 1.347% | 18.4301 | 0.2183% | 132.1572 | 1.565% | 1091 | 8424.5699 | 8310.8428 | 1.368% | 0.2218%
2017-08-28 | 20 | 8443 | 113.7271 | 1.347% | 18.4301 | 0.2183% | 132.1572 | 1.565% | 1092 | 8424.5699 | 8310.8428 | 1.368% | 0.2218%
2017-07-29 | 11 | 8444 | 113.7313 | 1.347% | 18.4311 | 0.2183% | 132.1625 | 1.565% | 1093 | 8425.5689 | 8311.8375 | 1.368% | 0.2217%
2017-06-01 | 11 | 8447 | 113.7441 | 1.347% | 18.434 | 0.2182% | 132.1781 | 1.565% | 1094 | 8428.566 | 8314.8219 | 1.368% | 0.2217%
2017-08-14 | 10 | 8458 | 113.7909 | 1.345% | 18.4447 | 0.2181% | 132.2357 | 1.563% | 1095 | 8439.5553 | 8325.7643 | 1.367% | 0.2215%
2017-08-16 | 9 | 8458 | 113.7909 | 1.345% | 18.4447 | 0.2181% | 132.2357 | 1.563% | 1096 | 8439.5553 | 8325.7643 | 1.367% | 0.2215%
2017-06-21 | 13 | 8460 | 113.7995 | 1.345% | 18.4467 | 0.218% | 132.2461 | 1.563% | 1097 | 8441.5533 | 8327.7539 | 1.367% | 0.2215%
2017-07-26 | 10 | 8460 | 113.7995 | 1.345% | 18.4467 | 0.218% | 132.2461 | 1.563% | 1098 | 8441.5533 | 8327.7539 | 1.367% | 0.2215%
2017-08-09 | 22 | 8463 | 113.8122 | 1.345% | 18.4496 | 0.218% | 132.2618 | 1.563% | 1099 | 8444.5504 | 8330.7382 | 1.366% | 0.2215%
2017-06-15 | 10 | 8468 | 113.8335 | 1.344% | 18.4545 | 0.2179% | 132.288 | 1.562% | 1100 | 8449.5455 | 8335.712 | 1.366% | 0.2214%
2017-08-28 | 18 | 8470 | 113.842 | 1.344% | 18.4564 | 0.2179% | 132.2984 | 1.562% | 1101 | 8451.5436 | 8337.7016 | 1.365% | 0.2214%
2017-08-02 | 23 | 8472 | 113.8505 | 1.344% | 18.4584 | 0.2179% | 132.3089 | 1.562% | 1102 | 8453.5416 | 8339.6911 | 1.365% | 0.2213%
2017-06-27 | 22 | 8474 | 113.859 | 1.344% | 18.4603 | 0.2178% | 132.3194 | 1.561% | 1103 | 8455.5397 | 8341.6806 | 1.365% | 0.2213%
2017-07-01 | 12 | 8480 | 113.8846 | 1.343% | 18.4661 | 0.2178% | 132.3507 | 1.561% | 1104 | 8461.5339 | 8347.6493 | 1.364% | 0.2212%
2017-07-14 | 1 | 8480 | 113.8846 | 1.343% | 18.4661 | 0.2178% | 132.3507 | 1.561% | 1105 | 8461.5339 | 8347.6493 | 1.364% | 0.2212%
2017-06-02 | 22 | 8481 | 113.8888 | 1.343% | 18.4671 | 0.2177% | 132.356 | 1.561% | 1106 | 8462.5329 | 8348.644 | 1.364% | 0.2212%
2017-06-20 | 12 | 8487 | 113.9144 | 1.342% | 18.473 | 0.2177% | 132.3874 | 1.56% | 1107 | 8468.527 | 8354.6126 | 1.363% | 0.2211%
2017-07-10 | 23 | 8488 | 113.9186 | 1.342% | 18.4739 | 0.2176% | 132.3926 | 1.56% | 1108 | 8469.5261 | 8355.6074 | 1.363% | 0.2211%
2017-07-18 | 11 | 8495 | 113.9484 | 1.341% | 18.4807 | 0.2175% | 132.4292 | 1.559% | 1109 | 8476.5193 | 8362.5708 | 1.363% | 0.221%
2017-07-29 | 21 | 8498 | 113.9612 | 1.341% | 18.4837 | 0.2175% | 132.4449 | 1.559% | 1110 | 8479.5163 | 8365.5551 | 1.362% | 0.2209%
2017-06-09 | 20 | 8500 | 113.9697 | 1.341% | 18.4856 | 0.2175% | 132.4553 | 1.558% | 1111 | 8481.5144 | 8367.5447 | 1.362% | 0.2209%
2017-07-03 | 10 | 8501 | 113.974 | 1.341% | 18.4866 | 0.2175% | 132.4606 | 1.558% | 1112 | 8482.5134 | 8368.5394 | 1.362% | 0.2209%
2017-08-28 | 17 | 8504 | 113.9868 | 1.34% | 18.4895 | 0.2174% | 132.4763 | 1.558% | 1113 | 8485.5105 | 8371.5237 | 1.362% | 0.2209%
2017-06-06 | 12 | 8506 | 113.9953 | 1.34% | 18.4915 | 0.2174% | 132.4867 | 1.558% | 1114 | 8487.5085 | 8373.5133 | 1.361% | 0.2208%
2017-06-12 | 23 | 8507 | 113.9995 | 1.34% | 18.4924 | 0.2174% | 132.492 | 1.557% | 1115 | 8488.5076 | 8374.508 | 1.361% | 0.2208%
2017-08-07 | 10 | 8509 | 114.008 | 1.34% | 18.4944 | 0.2174% | 132.5024 | 1.557% | 1116 | 8490.5056 | 8376.4976 | 1.361% | 0.2208%
2017-06-25 | 12 | 8511 | 114.0166 | 1.34% | 18.4963 | 0.2173% | 132.5129 | 1.557% | 1117 | 8492.5037 | 8378.4871 | 1.361% | 0.2208%
2017-08-27 | 21 | 8528 | 114.0889 | 1.338% | 18.5129 | 0.2171% | 132.6018 | 1.555% | 1118 | 8509.4871 | 8395.3982 | 1.359% | 0.2205%
2017-07-09 | 23 | 8529 | 114.0932 | 1.338% | 18.5138 | 0.2171% | 132.607 | 1.555% | 1119 | 8510.4862 | 8396.393 | 1.359% | 0.2205%
2017-08-14 | 24 | 8530 | 114.0974 | 1.338% | 18.5148 | 0.2171% | 132.6122 | 1.555% | 1120 | 8511.4852 | 8397.3878 | 1.359% | 0.2205%
2017-08-06 | 12 | 8537 | 114.1272 | 1.337% | 18.5216 | 0.217% | 132.6489 | 1.554% | 1121 | 8518.4784 | 8404.3511 | 1.358% | 0.2204%
2017-06-03 | 22 | 8540 | 114.14 | 1.337% | 18.5245 | 0.2169% | 132.6645 | 1.553% | 1122 | 8521.4755 | 8407.3355 | 1.358% | 0.2203%
2017-07-25 | 9 | 8540 | 114.14 | 1.337% | 18.5245 | 0.2169% | 132.6645 | 1.553% | 1123 | 8521.4755 | 8407.3355 | 1.358% | 0.2203%
2017-06-25 | 22 | 8545 | 114.1613 | 1.336% | 18.5294 | 0.2168% | 132.6907 | 1.553% | 1124 | 8526.4706 | 8412.3093 | 1.357% | 0.2203%
2017-07-13 | 1 | 8545 | 114.1613 | 1.336% | 18.5294 | 0.2168% | 132.6907 | 1.553% | 1125 | 8526.4706 | 8412.3093 | 1.357% | 0.2203%
2017-08-01 | 12 | 8551 | 114.1868 | 1.335% | 18.5352 | 0.2168% | 132.7221 | 1.552% | 1126 | 8532.4648 | 8418.2779 | 1.356% | 0.2202%
2017-07-27 | 24 | 8553 | 114.1953 | 1.335% | 18.5372 | 0.2167% | 132.7325 | 1.552% | 1127 | 8534.4628 | 8420.2675 | 1.356% | 0.2201%
2017-08-16 | 24 | 8554 | 114.1996 | 1.335% | 18.5382 | 0.2167% | 132.7378 | 1.552% | 1128 | 8535.4618 | 8421.2622 | 1.356% | 0.2201%
2017-07-30 | 14 | 8556 | 114.2081 | 1.335% | 18.5401 | 0.2167% | 132.7482 | 1.552% | 1129 | 8537.4599 | 8423.2518 | 1.356% | 0.2201%
2017-06-28 | 22 | 8557 | 114.2124 | 1.335% | 18.5411 | 0.2167% | 132.7535 | 1.551% | 1130 | 8538.4589 | 8424.2465 | 1.356% | 0.2201%
2017-06-20 | 19 | 8561 | 114.2294 | 1.334% | 18.545 | 0.2166% | 132.7744 | 1.551% | 1131 | 8542.455 | 8428.2256 | 1.355% | 0.22%
2017-08-28 | 16 | 8564 | 114.2422 | 1.334% | 18.5479 | 0.2166% | 132.7901 | 1.551% | 1132 | 8545.4521 | 8431.2099 | 1.355% | 0.22%
2017-08-28 | 15 | 8566 | 114.2507 | 1.334% | 18.5498 | 0.2166% | 132.8005 | 1.55% | 1133 | 8547.4502 | 8433.1995 | 1.355% | 0.22%
2017-06-10 | 22 | 8570 | 114.2677 | 1.333% | 18.5537 | 0.2165% | 132.8215 | 1.55% | 1134 | 8551.4463 | 8437.1785 | 1.354% | 0.2199%
2017-07-05 | 10 | 8571 | 114.272 | 1.333% | 18.5547 | 0.2165% | 132.8267 | 1.55% | 1135 | 8552.4453 | 8438.1733 | 1.354% | 0.2199%
2017-08-03 | 23 | 8574 | 114.2847 | 1.333% | 18.5576 | 0.2164% | 132.8424 | 1.549% | 1136 | 8555.4424 | 8441.1576 | 1.354% | 0.2198%
2017-07-04 | 11 | 8580 | 114.3103 | 1.332% | 18.5635 | 0.2164% | 132.8738 | 1.549% | 1137 | 8561.4365 | 8447.1262 | 1.353% | 0.2198%
2017-08-10 | 12 | 8582 | 114.3188 | 1.332% | 18.5654 | 0.2163% | 132.8842 | 1.548% | 1138 | 8563.4346 | 8449.1158 | 1.353% | 0.2197%
2017-08-08 | 10 | 8584 | 114.3273 | 1.332% | 18.5674 | 0.2163% | 132.8947 | 1.548% | 1139 | 8565.4326 | 8451.1053 | 1.353% | 0.2197%
2017-06-13 | 11 | 8586 | 114.3358 | 1.332% | 18.5693 | 0.2163% | 132.9051 | 1.548% | 1140 | 8567.4307 | 8453.0949 | 1.353% | 0.2197%
2017-07-01 | 23 | 8586 | 114.3358 | 1.332% | 18.5693 | 0.2163% | 132.9051 | 1.548% | 1141 | 8567.4307 | 8453.0949 | 1.353% | 0.2197%
2017-08-08 | 19 | 8587 | 114.3401 | 1.332% | 18.5703 | 0.2163% | 132.9104 | 1.548% | 1142 | 8568.4297 | 8454.0896 | 1.352% | 0.2197%
2017-06-27 | 12 | 8593 | 114.3656 | 1.331% | 18.5761 | 0.2162% | 132.9417 | 1.547% | 1143 | 8574.4239 | 8460.0583 | 1.352% | 0.2196%
2017-06-17 | 11 | 8596 | 114.3784 | 1.331% | 18.579 | 0.2161% | 132.9574 | 1.547% | 1144 | 8577.421 | 8463.0426 | 1.352% | 0.2195%
2017-07-25 | 24 | 8597 | 114.3827 | 1.33% | 18.58 | 0.2161% | 132.9627 | 1.547% | 1145 | 8578.42 | 8464.0373 | 1.351% | 0.2195%
2017-07-21 | 9 | 8599 | 114.3912 | 1.33% | 18.582 | 0.2161% | 132.9731 | 1.546% | 1146 | 8580.418 | 8466.0269 | 1.351% | 0.2195%
2017-07-07 | 24 | 8609 | 114.4337 | 1.329% | 18.5917 | 0.216% | 133.0254 | 1.545% | 1147 | 8590.4083 | 8475.9746 | 1.35% | 0.2193%
2017-08-27 | 20 | 8632 | 114.5316 | 1.327% | 18.6141 | 0.2156% | 133.1457 | 1.542% | 1148 | 8613.3859 | 8498.8543 | 1.348% | 0.219%
2017-08-15 | 9 | 8633 | 114.5359 | 1.327% | 18.615 | 0.2156% | 133.1509 | 1.542% | 1149 | 8614.385 | 8499.8491 | 1.348% | 0.219%
2017-06-28 | 13 | 8634 | 114.5402 | 1.327% | 18.616 | 0.2156% | 133.1562 | 1.542% | 1150 | 8615.384 | 8500.8438 | 1.347% | 0.219%
2017-06-06 | 22 | 8642 | 114.5742 | 1.326% | 18.6238 | 0.2155% | 133.198 | 1.541% | 1151 | 8623.3762 | 8508.802 | 1.347% | 0.2189%
2017-07-29 | 12 | 8642 | 114.5742 | 1.326% | 18.6238 | 0.2155% | 133.198 | 1.541% | 1152 | 8623.3762 | 8508.802 | 1.347% | 0.2189%
2017-06-30 | 22 | 8643 | 114.5785 | 1.326% | 18.6248 | 0.2155% | 133.2032 | 1.541% | 1153 | 8624.3752 | 8509.7968 | 1.346% | 0.2189%
2017-06-04 | 12 | 8644 | 114.5827 | 1.326% | 18.6257 | 0.2155% | 133.2085 | 1.541% | 1154 | 8625.3743 | 8510.7915 | 1.346% | 0.2188%
2017-08-12 | 11 | 8660 | 114.6508 | 1.324% | 18.6413 | 0.2153% | 133.2922 | 1.539% | 1155 | 8641.3587 | 8526.7078 | 1.345% | 0.2186%
2017-06-04 | 22 | 8663 | 114.6636 | 1.324% | 18.6442 | 0.2152% | 133.3079 | 1.539% | 1156 | 8644.3558 | 8529.6921 | 1.344% | 0.2186%
2017-07-17 | 23 | 8663 | 114.6636 | 1.324% | 18.6442 | 0.2152% | 133.3079 | 1.539% | 1157 | 8644.3558 | 8529.6921 | 1.344% | 0.2186%
2017-08-09 | 13 | 8664 | 114.6679 | 1.323% | 18.6452 | 0.2152% | 133.3131 | 1.539% | 1158 | 8645.3548 | 8530.6869 | 1.344% | 0.2186%
2017-06-20 | 13 | 8665 | 114.6721 | 1.323% | 18.6462 | 0.2152% | 133.3183 | 1.539% | 1159 | 8646.3538 | 8531.6817 | 1.344% | 0.2186%
2017-07-31 | 22 | 8667 | 114.6806 | 1.323% | 18.6481 | 0.2152% | 133.3288 | 1.538% | 1160 | 8648.3519 | 8533.6712 | 1.344% | 0.2185%
2017-06-26 | 12 | 8668 | 114.6849 | 1.323% | 18.6491 | 0.2151% | 133.334 | 1.538% | 1161 | 8649.3509 | 8534.666 | 1.344% | 0.2185%
2017-06-18 | 11 | 8674 | 114.7104 | 1.322% | 18.6549 | 0.2151% | 133.3654 | 1.538% | 1162 | 8655.3451 | 8540.6346 | 1.343% | 0.2184%
2017-08-30 | 22 | 8679 | 114.7317 | 1.322% | 18.6598 | 0.215% | 133.3915 | 1.537% | 1163 | 8660.3402 | 8545.6085 | 1.343% | 0.2184%
2017-08-15 | 24 | 8681 | 114.7402 | 1.322% | 18.6618 | 0.215% | 133.402 | 1.537% | 1164 | 8662.3382 | 8547.598 | 1.342% | 0.2183%
2017-07-31 | 13 | 8682 | 114.7445 | 1.322% | 18.6627 | 0.215% | 133.4072 | 1.537% | 1165 | 8663.3373 | 8548.5928 | 1.342% | 0.2183%
2017-06-09 | 16 | 8683 | 114.7488 | 1.322% | 18.6637 | 0.2149% | 133.4125 | 1.536% | 1166 | 8664.3363 | 8549.5875 | 1.342% | 0.2183%
2017-08-13 | 11 | 8683 | 114.7488 | 1.322% | 18.6637 | 0.2149% | 133.4125 | 1.536% | 1167 | 8664.3363 | 8549.5875 | 1.342% | 0.2183%
2017-08-27 | 14 | 8689 | 114.7743 | 1.321% | 18.6695 | 0.2149% | 133.4438 | 1.536% | 1168 | 8670.3305 | 8555.5562 | 1.342% | 0.2182%
2017-06-20 | 18 | 8690 | 114.7786 | 1.321% | 18.6705 | 0.2149% | 133.4491 | 1.536% | 1169 | 8671.3295 | 8556.5509 | 1.341% | 0.2182%
2017-07-07 | 9 | 8691 | 114.7828 | 1.321% | 18.6715 | 0.2148% | 133.4543 | 1.536% | 1170 | 8672.3285 | 8557.5457 | 1.341% | 0.2182%
2017-07-23 | 1 | 8695 | 114.7998 | 1.32% | 18.6754 | 0.2148% | 133.4752 | 1.535% | 1171 | 8676.3246 | 8561.5248 | 1.341% | 0.2181%
2017-08-31 | 22 | 8696 | 114.8041 | 1.32% | 18.6764 | 0.2148% | 133.4804 | 1.535% | 1172 | 8677.3236 | 8562.5196 | 1.341% | 0.2181%
2017-07-23 | 23 | 8698 | 114.8126 | 1.32% | 18.6783 | 0.2147% | 133.4909 | 1.535% | 1173 | 8679.3217 | 8564.5091 | 1.341% | 0.2181%
2017-06-24 | 22 | 8702 | 114.8296 | 1.32% | 18.6822 | 0.2147% | 133.5118 | 1.534% | 1174 | 8683.3178 | 8568.4882 | 1.34% | 0.218%
2017-08-08 | 18 | 8702 | 114.8296 | 1.32% | 18.6822 | 0.2147% | 133.5118 | 1.534% | 1175 | 8683.3178 | 8568.4882 | 1.34% | 0.218%
2017-08-17 | 9 | 8702 | 114.8296 | 1.32% | 18.6822 | 0.2147% | 133.5118 | 1.534% | 1176 | 8683.3178 | 8568.4882 | 1.34% | 0.218%
2017-06-11 | 12 | 8705 | 114.8424 | 1.319% | 18.6851 | 0.2146% | 133.5275 | 1.534% | 1177 | 8686.3149 | 8571.4725 | 1.34% | 0.218%
2017-06-29 | 12 | 8705 | 114.8424 | 1.319% | 18.6851 | 0.2146% | 133.5275 | 1.534% | 1178 | 8686.3149 | 8571.4725 | 1.34% | 0.218%
2017-06-15 | 23 | 8706 | 114.8467 | 1.319% | 18.6861 | 0.2146% | 133.5327 | 1.534% | 1179 | 8687.3139 | 8572.4673 | 1.34% | 0.218%
2017-07-17 | 11 | 8706 | 114.8467 | 1.319% | 18.6861 | 0.2146% | 133.5327 | 1.534% | 1180 | 8687.3139 | 8572.4673 | 1.34% | 0.218%
2017-07-04 | 23 | 8711 | 114.8679 | 1.319% | 18.6909 | 0.2146% | 133.5589 | 1.533% | 1181 | 8692.3091 | 8577.4411 | 1.339% | 0.2179%
2017-08-23 | 9 | 8715 | 114.885 | 1.318% | 18.6948 | 0.2145% | 133.5798 | 1.533% | 1182 | 8696.3052 | 8581.4202 | 1.339% | 0.2179%
2017-08-06 | 23 | 8718 | 114.8977 | 1.318% | 18.6978 | 0.2145% | 133.5955 | 1.532% | 1183 | 8699.3022 | 8584.4045 | 1.338% | 0.2178%
2017-06-26 | 22 | 8721 | 114.9105 | 1.318% | 18.7007 | 0.2144% | 133.6112 | 1.532% | 1184 | 8702.2993 | 8587.3888 | 1.338% | 0.2178%
2017-06-05 | 22 | 8724 | 114.9233 | 1.317% | 18.7036 | 0.2144% | 133.6269 | 1.532% | 1185 | 8705.2964 | 8590.3731 | 1.338% | 0.2177%
2017-06-05 | 11 | 8725 | 114.9275 | 1.317% | 18.7046 | 0.2144% | 133.6321 | 1.532% | 1186 | 8706.2954 | 8591.3679 | 1.338% | 0.2177%
2017-06-30 | 21 | 8734 | 114.9659 | 1.316% | 18.7133 | 0.2143% | 133.6792 | 1.531% | 1187 | 8715.2867 | 8600.3208 | 1.337% | 0.2176%
2017-06-12 | 11 | 8747 | 115.0212 | 1.315% | 18.726 | 0.2141% | 133.7472 | 1.529% | 1188 | 8728.274 | 8613.2528 | 1.335% | 0.2174%
2017-06-01 | 22 | 8754 | 115.051 | 1.314% | 18.7328 | 0.214% | 133.7838 | 1.528% | 1189 | 8735.2672 | 8620.2162 | 1.335% | 0.2173%
2017-07-08 | 23 | 8756 | 115.0595 | 1.314% | 18.7347 | 0.214% | 133.7943 | 1.528% | 1190 | 8737.2653 | 8622.2057 | 1.334% | 0.2173%
2017-08-11 | 23 | 8762 | 115.0851 | 1.313% | 18.7406 | 0.2139% | 133.8256 | 1.527% | 1191 | 8743.2594 | 8628.1744 | 1.334% | 0.2172%
2017-08-19 | 1 | 8763 | 115.0893 | 1.313% | 18.7416 | 0.2139% | 133.8309 | 1.527% | 1192 | 8744.2584 | 8629.1691 | 1.334% | 0.2172%
2017-08-30 | 14 | 8764 | 115.0936 | 1.313% | 18.7425 | 0.2139% | 133.8361 | 1.527% | 1193 | 8745.2575 | 8630.1639 | 1.334% | 0.2172%
2017-08-25 | 11 | 8768 | 115.1106 | 1.313% | 18.7464 | 0.2138% | 133.857 | 1.527% | 1194 | 8749.2536 | 8634.143 | 1.333% | 0.2171%
2017-08-24 | 11 | 8772 | 115.1276 | 1.312% | 18.7503 | 0.2138% | 133.8779 | 1.526% | 1195 | 8753.2497 | 8638.1221 | 1.333% | 0.2171%
2017-06-19 | 23 | 8774 | 115.1361 | 1.312% | 18.7523 | 0.2137% | 133.8884 | 1.526% | 1196 | 8755.2477 | 8640.1116 | 1.333% | 0.217%
2017-07-16 | 12 | 8776 | 115.1447 | 1.312% | 18.7542 | 0.2137% | 133.8989 | 1.526% | 1197 | 8757.2458 | 8642.1011 | 1.332% | 0.217%
2017-07-24 | 24 | 8777 | 115.1489 | 1.312% | 18.7552 | 0.2137% | 133.9041 | 1.526% | 1198 | 8758.2448 | 8643.0959 | 1.332% | 0.217%
2017-06-14 | 23 | 8778 | 115.1532 | 1.312% | 18.7561 | 0.2137% | 133.9093 | 1.526% | 1199 | 8759.2439 | 8644.0907 | 1.332% | 0.217%
2017-06-20 | 17 | 8787 | 115.1915 | 1.311% | 18.7649 | 0.2136% | 133.9564 | 1.524% | 1200 | 8768.2351 | 8653.0436 | 1.331% | 0.2169% | 8791.5517
2017-07-24 | 10 | 8794 | 115.2666 | 1.311% | 18.7776 | 0.2135% | 134.0441 | 1.524% | 1201 | 8775.2224 | 8659.9559 | 1.331% | 0.2168%
2017-08-04 | 11 | 8794 | 115.2666 | 1.311% | 18.7776 | 0.2135% | 134.0441 | 1.524% | 1202 | 8775.2224 | 8659.9559 | 1.331% | 0.2168%
2017-06-17 | 22 | 8795 | 115.286 | 1.311% | 18.7805 | 0.2135% | 134.0665 | 1.524% | 1203 | 8776.2195 | 8660.9335 | 1.331% | 0.2168%
2017-07-11 | 24 | 8796 | 115.3054 | 1.311% | 18.7835 | 0.2135% | 134.0889 | 1.524% | 1204 | 8777.2165 | 8661.9111 | 1.331% | 0.2169%
2017-06-02 | 12 | 8797 | 115.3248 | 1.311% | 18.7864 | 0.2136% | 134.1112 | 1.525% | 1205 | 8778.2136 | 8662.8888 | 1.331% | 0.2169%
2017-06-20 | 14 | 8798 | 115.3442 | 1.311% | 18.7893 | 0.2136% | 134.1336 | 1.525% | 1206 | 8779.2107 | 8663.8664 | 1.331% | 0.2169%
2017-07-02 | 11 | 8801 | 115.4025 | 1.311% | 18.7982 | 0.2136% | 134.2006 | 1.525% | 1207 | 8782.2018 | 8666.7994 | 1.332% | 0.2169%
2017-07-11 | 10 | 8802 | 115.4219 | 1.311% | 18.8011 | 0.2136% | 134.223 | 1.525% | 1208 | 8783.1989 | 8667.777 | 1.332% | 0.2169%
2017-08-13 | 22 | 8804 | 115.4607 | 1.311% | 18.807 | 0.2136% | 134.2677 | 1.525% | 1209 | 8785.193 | 8669.7323 | 1.332% | 0.2169%
2017-07-15 | 1 | 8806 | 115.4996 | 1.312% | 18.8129 | 0.2136% | 134.3124 | 1.525% | 1210 | 8787.1871 | 8671.6876 | 1.332% | 0.2169%
2017-07-16 | 22 | 8806 | 115.4996 | 1.312% | 18.8129 | 0.2136% | 134.3124 | 1.525% | 1211 | 8787.1871 | 8671.6876 | 1.332% | 0.2169%
2017-08-18 | 9 | 8806 | 115.4996 | 1.312% | 18.8129 | 0.2136% | 134.3124 | 1.525% | 1212 | 8787.1871 | 8671.6876 | 1.332% | 0.2169%
2017-08-08 | 11 | 8807 | 115.519 | 1.312% | 18.8158 | 0.2136% | 134.3348 | 1.525% | 1213 | 8788.1842 | 8672.6652 | 1.332% | 0.217%
2017-08-12 | 23 | 8813 | 115.6355 | 1.312% | 18.8334 | 0.2137% | 134.4689 | 1.526% | 1214 | 8794.1666 | 8678.5311 | 1.332% | 0.217%
2017-06-10 | 13 | 8817 | 115.7131 | 1.312% | 18.8452 | 0.2137% | 134.5583 | 1.526% | 1215 | 8798.1548 | 8682.4417 | 1.333% | 0.217%
2017-07-12 | 9 | 8817 | 115.7131 | 1.312% | 18.8452 | 0.2137% | 134.5583 | 1.526% | 1216 | 8798.1548 | 8682.4417 | 1.333% | 0.217%
2017-06-09 | 17 | 8820 | 115.7714 | 1.313% | 18.854 | 0.2138% | 134.6254 | 1.526% | 1217 | 8801.146 | 8685.3746 | 1.333% | 0.2171%
2017-07-29 | 20 | 8822 | 115.8102 | 1.313% | 18.8599 | 0.2138% | 134.6701 | 1.527% | 1218 | 8803.1401 | 8687.3299 | 1.333% | 0.2171%
2017-08-02 | 12 | 8822 | 115.8102 | 1.313% | 18.8599 | 0.2138% | 134.6701 | 1.527% | 1219 | 8803.1401 | 8687.3299 | 1.333% | 0.2171%
2017-07-06 | 10 | 8823 | 115.8296 | 1.313% | 18.8628 | 0.2138% | 134.6925 | 1.527% | 1220 | 8804.1372 | 8688.3075 | 1.333% | 0.2171%
2017-08-22 | 24 | 8823 | 115.8296 | 1.313% | 18.8628 | 0.2138% | 134.6925 | 1.527% | 1221 | 8804.1372 | 8688.3075 | 1.333% | 0.2171%
2017-07-27 | 10 | 8824 | 115.8491 | 1.313% | 18.8657 | 0.2138% | 134.7148 | 1.527% | 1222 | 8805.1343 | 8689.2852 | 1.333% | 0.2171%
2017-08-08 | 17 | 8837 | 116.1015 | 1.314% | 18.904 | 0.2139% | 135.0054 | 1.528% | 1223 | 8818.096 | 8701.9946 | 1.334% | 0.2172%
2017-08-25 | 22 | 8839 | 116.1403 | 1.314% | 18.9098 | 0.2139% | 135.0501 | 1.528% | 1224 | 8820.0902 | 8703.9499 | 1.334% | 0.2173%
2017-06-25 | 21 | 8840 | 116.1597 | 1.314% | 18.9128 | 0.2139% | 135.0725 | 1.528% | 1225 | 8821.0872 | 8704.9275 | 1.334% | 0.2173%
2017-08-09 | 21 | 8840 | 116.1597 | 1.314% | 18.9128 | 0.2139% | 135.0725 | 1.528% | 1226 | 8821.0872 | 8704.9275 | 1.334% | 0.2173%
2017-08-07 | 23 | 8844 | 116.2374 | 1.314% | 18.9245 | 0.214% | 135.1619 | 1.528% | 1227 | 8825.0755 | 8708.8381 | 1.335% | 0.2173%
2017-07-30 | 15 | 8848 | 116.3151 | 1.315% | 18.9363 | 0.214% | 135.2513 | 1.529% | 1228 | 8829.0637 | 8712.7487 | 1.335% | 0.2173%
2017-06-09 | 19 | 8850 | 116.3539 | 1.315% | 18.9422 | 0.214% | 135.2961 | 1.529% | 1229 | 8831.0578 | 8714.7039 | 1.335% | 0.2174%
2017-08-26 | 12 | 8851 | 116.3733 | 1.315% | 18.9451 | 0.214% | 135.3184 | 1.529% | 1230 | 8832.0549 | 8715.6816 | 1.335% | 0.2174%
2017-06-23 | 24 | 8854 | 116.4316 | 1.315% | 18.9539 | 0.2141% | 135.3855 | 1.529% | 1231 | 8835.0461 | 8718.6145 | 1.335% | 0.2174%
2017-06-27 | 21 | 8858 | 116.5092 | 1.315% | 18.9657 | 0.2141% | 135.4749 | 1.529% | 1232 | 8839.0343 | 8722.5251 | 1.336% | 0.2174%
2017-06-20 | 15 | 8860 | 116.5481 | 1.315% | 18.9715 | 0.2141% | 135.5196 | 1.53% | 1233 | 8841.0285 | 8724.4804 | 1.336% | 0.2175%
2017-06-20 | 16 | 8867 | 116.684 | 1.316% | 18.9921 | 0.2142% | 135.6761 | 1.53% | 1234 | 8848.0079 | 8731.3239 | 1.336% | 0.2175%
2017-07-29 | 13 | 8868 | 116.7034 | 1.316% | 18.995 | 0.2142% | 135.6985 | 1.53% | 1235 | 8849.005 | 8732.3015 | 1.336% | 0.2175%
2017-06-03 | 13 | 8872 | 116.7811 | 1.316% | 19.0068 | 0.2142% | 135.7879 | 1.531% | 1236 | 8852.9932 | 8736.2121 | 1.337% | 0.2176%
2017-07-30 | 20 | 8881 | 116.9558 | 1.317% | 19.0332 | 0.2143% | 135.9891 | 1.531% | 1237 | 8861.9668 | 8745.0109 | 1.337% | 0.2176%
2017-08-08 | 12 | 8882 | 116.9752 | 1.317% | 19.0362 | 0.2143% | 136.0114 | 1.531% | 1238 | 8862.9638 | 8745.9886 | 1.337% | 0.2177%
2017-07-15 | 23 | 8888 | 117.0917 | 1.317% | 19.0538 | 0.2144% | 136.1456 | 1.532% | 1239 | 8868.9462 | 8751.8544 | 1.338% | 0.2177%
2017-07-03 | 22 | 8889 | 117.1112 | 1.317% | 19.0568 | 0.2144% | 136.1679 | 1.532% | 1240 | 8869.9432 | 8752.8321 | 1.338% | 0.2177%
2017-08-26 | 21 | 8890 | 117.1306 | 1.318% | 19.0597 | 0.2144% | 136.1903 | 1.532% | 1241 | 8870.9403 | 8753.8097 | 1.338% | 0.2177%
2017-06-24 | 10 | 8891 | 117.15 | 1.318% | 19.0626 | 0.2144% | 136.2126 | 1.532% | 1242 | 8871.9374 | 8754.7874 | 1.338% | 0.2177%
2017-08-01 | 22 | 8892 | 117.1694 | 1.318% | 19.0656 | 0.2144% | 136.235 | 1.532% | 1243 | 8872.9344 | 8755.765 | 1.338% | 0.2177%
2017-08-19 | 23 | 8893 | 117.1888 | 1.318% | 19.0685 | 0.2144% | 136.2573 | 1.532% | 1244 | 8873.9315 | 8756.7427 | 1.338% | 0.2178%
2017-06-03 | 21 | 8894 | 117.2082 | 1.318% | 19.0715 | 0.2144% | 136.2797 | 1.532% | 1245 | 8874.9285 | 8757.7203 | 1.338% | 0.2178%
2017-06-22 | 22 | 8895 | 117.2277 | 1.318% | 19.0744 | 0.2144% | 136.3021 | 1.532% | 1246 | 8875.9256 | 8758.6979 | 1.338% | 0.2178%
2017-06-02 | 21 | 8899 | 117.3053 | 1.318% | 19.0861 | 0.2145% | 136.3915 | 1.533% | 1247 | 8879.9139 | 8762.6085 | 1.339% | 0.2178%
2017-06-10 | 21 | 8917 | 117.6548 | 1.319% | 19.139 | 0.2146% | 136.7939 | 1.534% | 1248 | 8897.861 | 8780.2061 | 1.34% | 0.218%
2017-08-24 | 22 | 8919 | 117.6937 | 1.32% | 19.1449 | 0.2147% | 136.8386 | 1.534% | 1249 | 8899.8551 | 8782.1614 | 1.34% | 0.218%
2017-06-06 | 13 | 8927 | 117.849 | 1.32% | 19.1684 | 0.2147% | 137.0174 | 1.535% | 1250 | 8907.8316 | 8789.9826 | 1.341% | 0.2181%
2017-07-06 | 24 | 8930 | 117.9073 | 1.32% | 19.1772 | 0.2148% | 137.0845 | 1.535% | 1251 | 8910.8228 | 8792.9155 | 1.341% | 0.2181%
2017-06-28 | 21 | 8934 | 117.9849 | 1.321% | 19.189 | 0.2148% | 137.1739 | 1.535% | 1252 | 8914.811 | 8796.8261 | 1.341% | 0.2181%
2017-07-08 | 10 | 8937 | 118.0432 | 1.321% | 19.1978 | 0.2148% | 137.241 | 1.536% | 1253 | 8917.8022 | 8799.759 | 1.341% | 0.2182%
2017-07-28 | 10 | 8938 | 118.0626 | 1.321% | 19.2008 | 0.2148% | 137.2633 | 1.536% | 1254 | 8918.7992 | 8800.7367 | 1.342% | 0.2182%
2017-07-01 | 13 | 8942 | 118.1403 | 1.321% | 19.2125 | 0.2149% | 137.3528 | 1.536% | 1255 | 8922.7875 | 8804.6472 | 1.342% | 0.2182%
2017-08-31 | 12 | 8950 | 118.2956 | 1.322% | 19.236 | 0.2149% | 137.5316 | 1.537% | 1256 | 8930.764 | 8812.4684 | 1.342% | 0.2183%
2017-06-30 | 11 | 8952 | 118.3344 | 1.322% | 19.2419 | 0.2149% | 137.5763 | 1.537% | 1257 | 8932.7581 | 8814.4237 | 1.343% | 0.2183%
2017-08-05 | 12 | 8955 | 118.3927 | 1.322% | 19.2507 | 0.215% | 137.6434 | 1.537% | 1258 | 8935.7493 | 8817.3566 | 1.343% | 0.2183%
2017-08-23 | 23 | 8957 | 118.4315 | 1.322% | 19.2566 | 0.215% | 137.6881 | 1.537% | 1259 | 8937.7434 | 8819.3119 | 1.343% | 0.2183%
2017-08-27 | 15 | 8963 | 118.548 | 1.323% | 19.2742 | 0.215% | 137.8222 | 1.538% | 1260 | 8943.7258 | 8825.1778 | 1.343% | 0.2184%
2017-07-21 | 24 | 8967 | 118.6257 | 1.323% | 19.286 | 0.2151% | 137.9116 | 1.538% | 1261 | 8947.714 | 8829.0884 | 1.344% | 0.2184%
2017-08-20 | 11 | 8968 | 118.6451 | 1.323% | 19.2889 | 0.2151% | 137.934 | 1.538% | 1262 | 8948.7111 | 8830.066 | 1.344% | 0.2184%
2017-08-21 | 10 | 8972 | 118.7228 | 1.323% | 19.3007 | 0.2151% | 138.0234 | 1.538% | 1263 | 8952.6993 | 8833.9766 | 1.344% | 0.2185%
2017-06-25 | 13 | 8975 | 118.781 | 1.323% | 19.3095 | 0.2151% | 138.0905 | 1.539% | 1264 | 8955.6905 | 8836.9095 | 1.344% | 0.2185%
2017-06-24 | 21 | 8978 | 118.8393 | 1.324% | 19.3183 | 0.2152% | 138.1576 | 1.539% | 1265 | 8958.6817 | 8839.8424 | 1.344% | 0.2185%
2017-07-20 | 24 | 8978 | 118.8393 | 1.324% | 19.3183 | 0.2152% | 138.1576 | 1.539% | 1266 | 8958.6817 | 8839.8424 | 1.344% | 0.2185%
2017-06-18 | 23 | 8979 | 118.8587 | 1.324% | 19.3212 | 0.2152% | 138.1799 | 1.539% | 1267 | 8959.6788 | 8840.8201 | 1.344% | 0.2185%
2017-08-08 | 16 | 8982 | 118.9169 | 1.324% | 19.33 | 0.2152% | 138.247 | 1.539% | 1268 | 8962.67 | 8843.753 | 1.345% | 0.2186%
2017-06-16 | 22 | 8983 | 118.9363 | 1.324% | 19.333 | 0.2152% | 138.2693 | 1.539% | 1269 | 8963.667 | 8844.7307 | 1.345% | 0.2186%
2017-08-04 | 23 | 8983 | 118.9363 | 1.324% | 19.333 | 0.2152% | 138.2693 | 1.539% | 1270 | 8963.667 | 8844.7307 | 1.345% | 0.2186%
2017-06-30 | 20 | 8985 | 118.9752 | 1.324% | 19.3389 | 0.2152% | 138.314 | 1.539% | 1271 | 8965.6611 | 8846.686 | 1.345% | 0.2186%
2017-08-19 | 10 | 8987 | 119.014 | 1.324% | 19.3447 | 0.2153% | 138.3588 | 1.54% | 1272 | 8967.6553 | 8848.6412 | 1.345% | 0.2186%
2017-06-09 | 18 | 8988 | 119.0334 | 1.324% | 19.3477 | 0.2153% | 138.3811 | 1.54% | 1273 | 8968.6523 | 8849.6189 | 1.345% | 0.2186%
2017-06-01 | 12 | 8990 | 119.0723 | 1.324% | 19.3536 | 0.2153% | 138.4258 | 1.54% | 1274 | 8970.6464 | 8851.5742 | 1.345% | 0.2186%
2017-08-07 | 11 | 8997 | 119.2082 | 1.325% | 19.3741 | 0.2153% | 138.5823 | 1.54% | 1275 | 8977.6259 | 8858.4177 | 1.346% | 0.2187%
2017-08-09 | 14 | 8998 | 119.2276 | 1.325% | 19.3771 | 0.2153% | 138.6047 | 1.54% | 1276 | 8978.6229 | 8859.3953 | 1.346% | 0.2187%
2017-08-22 | 10 | 9002 | 119.3053 | 1.325% | 19.3888 | 0.2154% | 138.6941 | 1.541% | 1277 | 8982.6112 | 8863.3059 | 1.346% | 0.2188%
2017-06-04 | 21 | 9003 | 119.3247 | 1.325% | 19.3918 | 0.2154% | 138.7164 | 1.541% | 1278 | 8983.6082 | 8864.2836 | 1.346% | 0.2188%
2017-07-20 | 10 | 9006 | 119.3829 | 1.326% | 19.4006 | 0.2154% | 138.7835 | 1.541% | 1279 | 8986.5994 | 8867.2165 | 1.346% | 0.2188%
2017-06-11 | 22 | 9009 | 119.4412 | 1.326% | 19.4094 | 0.2154% | 138.8506 | 1.541% | 1280 | 8989.5906 | 8870.1494 | 1.347% | 0.2188%
2017-08-11 | 11 | 9009 | 119.4412 | 1.326% | 19.4094 | 0.2154% | 138.8506 | 1.541% | 1281 | 8989.5906 | 8870.1494 | 1.347% | 0.2188%
2017-06-23 | 11 | 9012 | 119.4994 | 1.326% | 19.4182 | 0.2155% | 138.9176 | 1.541% | 1282 | 8992.5818 | 8873.0824 | 1.347% | 0.2188%
2017-07-18 | 12 | 9023 | 119.713 | 1.327% | 19.4505 | 0.2156% | 139.1636 | 1.542% | 1283 | 9003.5495 | 8883.8364 | 1.348% | 0.2189%
2017-08-09 | 20 | 9023 | 119.713 | 1.327% | 19.4505 | 0.2156% | 139.1636 | 1.542% | 1284 | 9003.5495 | 8883.8364 | 1.348% | 0.2189%
2017-08-03 | 12 | 9025 | 119.7519 | 1.327% | 19.4564 | 0.2156% | 139.2083 | 1.542% | 1285 | 9005.5436 | 8885.7917 | 1.348% | 0.219%
2017-06-22 | 11 | 9031 | 119.8684 | 1.327% | 19.474 | 0.2156% | 139.3424 | 1.543% | 1286 | 9011.526 | 8891.6576 | 1.348% | 0.219%
2017-08-27 | 19 | 9035 | 119.946 | 1.328% | 19.4858 | 0.2157% | 139.4318 | 1.543% | 1287 | 9015.5142 | 8895.5682 | 1.348% | 0.2191%
2017-07-28 | 23 | 9036 | 119.9654 | 1.328% | 19.4887 | 0.2157% | 139.4542 | 1.543% | 1288 | 9016.5113 | 8896.5458 | 1.348% | 0.2191%
2017-06-27 | 13 | 9039 | 120.0237 | 1.328% | 19.4975 | 0.2157% | 139.5212 | 1.544% | 1289 | 9019.5025 | 8899.4788 | 1.349% | 0.2191%
2017-06-21 | 14 | 9041 | 120.0625 | 1.328% | 19.5034 | 0.2157% | 139.566 | 1.544% | 1290 | 9021.4966 | 8901.434 | 1.349% | 0.2191%
2017-08-08 | 13 | 9046 | 120.1596 | 1.328% | 19.5181 | 0.2158% | 139.6777 | 1.544% | 1291 | 9026.4819 | 8906.3223 | 1.349% | 0.2191%
2017-07-09 | 12 | 9047 | 120.179 | 1.328% | 19.5211 | 0.2158% | 139.7001 | 1.544% | 1292 | 9027.4789 | 8907.2999 | 1.349% | 0.2192%
2017-06-26 | 13 | 9049 | 120.2179 | 1.329% | 19.5269 | 0.2158% | 139.7448 | 1.544% | 1293 | 9029.4731 | 8909.2552 | 1.349% | 0.2192%
2017-08-14 | 11 | 9049 | 120.2179 | 1.329% | 19.5269 | 0.2158% | 139.7448 | 1.544% | 1294 | 9029.4731 | 8909.2552 | 1.349% | 0.2192%
2017-07-13 | 9 | 9063 | 120.4897 | 1.329% | 19.5681 | 0.2159% | 140.0578 | 1.545% | 1295 | 9043.4319 | 8922.9422 | 1.35% | 0.2193%
2017-06-17 | 21 | 9069 | 120.6062 | 1.33% | 19.5857 | 0.216% | 140.1919 | 1.546% | 1296 | 9049.4143 | 8928.8081 | 1.351% | 0.2194%
2017-08-10 | 13 | 9077 | 120.7615 | 1.33% | 19.6092 | 0.216% | 140.3708 | 1.546% | 1297 | 9057.3908 | 8936.6292 | 1.351% | 0.2194%
2017-08-08 | 15 | 9078 | 120.781 | 1.33% | 19.6122 | 0.216% | 140.3931 | 1.547% | 1298 | 9058.3878 | 8937.6069 | 1.351% | 0.2194%
2017-07-16 | 21 | 9082 | 120.8586 | 1.331% | 19.6239 | 0.2161% | 140.4825 | 1.547% | 1299 | 9062.3761 | 8941.5175 | 1.352% | 0.2195%
2017-08-08 | 14 | 9083 | 120.878 | 1.331% | 19.6268 | 0.2161% | 140.5049 | 1.547% | 1300 | 9063.3732 | 8942.4951 | 1.352% | 0.2195%
2017-06-05 | 12 | 9091 | 121.0334 | 1.331% | 19.6504 | 0.2162% | 140.6837 | 1.548% | 1301 | 9071.3496 | 8950.3163 | 1.352% | 0.2195%
2017-06-19 | 10 | 9093 | 121.0722 | 1.331% | 19.6562 | 0.2162% | 140.7284 | 1.548% | 1302 | 9073.3438 | 8952.2716 | 1.352% | 0.2196%
2017-06-28 | 14 | 9095 | 121.111 | 1.332% | 19.6621 | 0.2162% | 140.7732 | 1.548% | 1303 | 9075.3379 | 8954.2268 | 1.353% | 0.2196%
2017-06-14 | 11 | 9097 | 121.1499 | 1.332% | 19.668 | 0.2162% | 140.8179 | 1.548% | 1304 | 9077.332 | 8956.1821 | 1.353% | 0.2196%
2017-07-22 | 10 | 9097 | 121.1499 | 1.332% | 19.668 | 0.2162% | 140.8179 | 1.548% | 1305 | 9077.332 | 8956.1821 | 1.353% | 0.2196%
2017-07-29 | 14 | 9098 | 121.1693 | 1.332% | 19.6709 | 0.2162% | 140.8402 | 1.548% | 1306 | 9078.3291 | 8957.1598 | 1.353% | 0.2196%
2017-06-06 | 21 | 9100 | 121.2081 | 1.332% | 19.6768 | 0.2162% | 140.8849 | 1.548% | 1307 | 9080.3232 | 8959.1151 | 1.353% | 0.2196%
2017-06-16 | 11 | 9100 | 121.2081 | 1.332% | 19.6768 | 0.2162% | 140.8849 | 1.548% | 1308 | 9080.3232 | 8959.1151 | 1.353% | 0.2196%
2017-06-21 | 22 | 9106 | 121.3246 | 1.332% | 19.6944 | 0.2163% | 141.0191 | 1.549% | 1309 | 9086.3056 | 8964.9809 | 1.353% | 0.2197%
2017-06-26 | 21 | 9110 | 121.4023 | 1.333% | 19.7062 | 0.2163% | 141.1085 | 1.549% | 1310 | 9090.2938 | 8968.8915 | 1.354% | 0.2197%
2017-08-16 | 10 | 9115 | 121.4994 | 1.333% | 19.7209 | 0.2164% | 141.2203 | 1.549% | 1311 | 9095.2791 | 8973.7797 | 1.354% | 0.2198%
2017-08-10 | 22 | 9120 | 121.5965 | 1.333% | 19.7356 | 0.2164% | 141.332 | 1.55% | 1312 | 9100.2644 | 8978.668 | 1.354% | 0.2198%
2017-08-26 | 20 | 9124 | 121.6741 | 1.334% | 19.7473 | 0.2164% | 141.4215 | 1.55% | 1313 | 9104.2527 | 8982.5785 | 1.355% | 0.2198%
2017-07-26 | 23 | 9129 | 121.7712 | 1.334% | 19.762 | 0.2165% | 141.5332 | 1.55% | 1314 | 9109.238 | 8987.4668 | 1.355% | 0.2199%
2017-08-13 | 12 | 9132 | 121.8295 | 1.334% | 19.7708 | 0.2165% | 141.6003 | 1.551% | 1315 | 9112.2292 | 8990.3997 | 1.355% | 0.2199%
2017-06-22 | 21 | 9134 | 121.8683 | 1.334% | 19.7767 | 0.2165% | 141.645 | 1.551% | 1316 | 9114.2233 | 8992.355 | 1.355% | 0.2199%
2017-08-05 | 22 | 9134 | 121.8683 | 1.334% | 19.7767 | 0.2165% | 141.645 | 1.551% | 1317 | 9114.2233 | 8992.355 | 1.355% | 0.2199%
2017-08-17 | 23 | 9135 | 121.8877 | 1.334% | 19.7797 | 0.2165% | 141.6674 | 1.551% | 1318 | 9115.2203 | 8993.3326 | 1.355% | 0.2199%
2017-07-14 | 9 | 9137 | 121.9265 | 1.334% | 19.7855 | 0.2165% | 141.7121 | 1.551% | 1319 | 9117.2145 | 8995.2879 | 1.355% | 0.22%
2017-06-17 | 12 | 9142 | 122.0236 | 1.335% | 19.8002 | 0.2166% | 141.8239 | 1.551% | 1320 | 9122.1998 | 9000.1761 | 1.356% | 0.22%
2017-06-25 | 20 | 9145 | 122.0819 | 1.335% | 19.809 | 0.2166% | 141.8909 | 1.552% | 1321 | 9125.191 | 9003.1091 | 1.356% | 0.22%
2017-07-19 | 11 | 9147 | 122.1207 | 1.335% | 19.8149 | 0.2166% | 141.9356 | 1.552% | 1322 | 9127.1851 | 9005.0644 | 1.356% | 0.22%
2017-07-30 | 16 | 9147 | 122.1207 | 1.335% | 19.8149 | 0.2166% | 141.9356 | 1.552% | 1323 | 9127.1851 | 9005.0644 | 1.356% | 0.22%
2017-07-18 | 22 | 9153 | 122.2372 | 1.335% | 19.8326 | 0.2167% | 142.0698 | 1.552% | 1324 | 9133.1674 | 9010.9302 | 1.357% | 0.2201%
2017-07-04 | 22 | 9154 | 122.2566 | 1.336% | 19.8355 | 0.2167% | 142.0921 | 1.552% | 1325 | 9134.1645 | 9011.9079 | 1.357% | 0.2201%
2017-08-24 | 12 | 9156 | 122.2955 | 1.336% | 19.8414 | 0.2167% | 142.1368 | 1.552% | 1326 | 9136.1586 | 9013.8632 | 1.357% | 0.2201%
2017-07-02 | 23 | 9160 | 122.3731 | 1.336% | 19.8531 | 0.2167% | 142.2263 | 1.553% | 1327 | 9140.1469 | 9017.7737 | 1.357% | 0.2202%
2017-08-01 | 13 | 9161 | 122.3926 | 1.336% | 19.8561 | 0.2167% | 142.2486 | 1.553% | 1328 | 9141.1439 | 9018.7514 | 1.357% | 0.2202%
2017-07-31 | 14 | 9169 | 122.5479 | 1.337% | 19.8796 | 0.2168% | 142.4275 | 1.553% | 1329 | 9149.1204 | 9026.5725 | 1.358% | 0.2202%
2017-07-10 | 22 | 9171 | 122.5867 | 1.337% | 19.8854 | 0.2168% | 142.4722 | 1.554% | 1330 | 9151.1146 | 9028.5278 | 1.358% | 0.2203%
2017-07-19 | 23 | 9175 | 122.6644 | 1.337% | 19.8972 | 0.2169% | 142.5616 | 1.554% | 1331 | 9155.1028 | 9032.4384 | 1.358% | 0.2203%
2017-06-15 | 11 | 9177 | 122.7032 | 1.337% | 19.9031 | 0.2169% | 142.6063 | 1.554% | 1332 | 9157.0969 | 9034.3937 | 1.358% | 0.2203%
2017-06-01 | 21 | 9178 | 122.7226 | 1.337% | 19.906 | 0.2169% | 142.6287 | 1.554% | 1333 | 9158.094 | 9035.3713 | 1.358% | 0.2203%
2017-06-22 | 20 | 9182 | 122.8003 | 1.337% | 19.9178 | 0.2169% | 142.7181 | 1.554% | 1334 | 9162.0822 | 9039.2819 | 1.359% | 0.2203%
2017-06-29 | 22 | 9182 | 122.8003 | 1.337% | 19.9178 | 0.2169% | 142.7181 | 1.554% | 1335 | 9162.0822 | 9039.2819 | 1.359% | 0.2203%
2017-07-10 | 11 | 9186 | 122.878 | 1.338% | 19.9295 | 0.217% | 142.8075 | 1.555% | 1336 | 9166.0705 | 9043.1925 | 1.359% | 0.2204%
2017-06-04 | 20 | 9198 | 123.111 | 1.338% | 19.9648 | 0.2171% | 143.0758 | 1.556% | 1337 | 9178.0352 | 9054.9242 | 1.36% | 0.2205%
2017-06-05 | 21 | 9203 | 123.2081 | 1.339% | 19.9795 | 0.2171% | 143.1875 | 1.556% | 1338 | 9183.0205 | 9059.8125 | 1.36% | 0.2205%
2017-08-27 | 16 | 9204 | 123.2275 | 1.339% | 19.9824 | 0.2171% | 143.2099 | 1.556% | 1339 | 9184.0176 | 9060.7901 | 1.36% | 0.2205%
2017-06-13 | 12 | 9205 | 123.2469 | 1.339% | 19.9854 | 0.2171% | 143.2323 | 1.556% | 1340 | 9185.0146 | 9061.7677 | 1.36% | 0.2205%
2017-07-05 | 23 | 9207 | 123.2857 | 1.339% | 19.9912 | 0.2171% | 143.277 | 1.556% | 1341 | 9187.0088 | 9063.723 | 1.36% | 0.2206%
2017-07-17 | 12 | 9208 | 123.3051 | 1.339% | 19.9942 | 0.2171% | 143.2993 | 1.556% | 1342 | 9188.0058 | 9064.7007 | 1.36% | 0.2206%
2017-07-31 | 21 | 9208 | 123.3051 | 1.339% | 19.9942 | 0.2171% | 143.2993 | 1.556% | 1343 | 9188.0058 | 9064.7007 | 1.36% | 0.2206%
2017-08-09 | 15 | 9209 | 123.3246 | 1.339% | 19.9971 | 0.2171% | 143.3217 | 1.556% | 1344 | 9189.0029 | 9065.6783 | 1.36% | 0.2206%
2017-08-30 | 15 | 9211 | 123.3634 | 1.339% | 20.003 | 0.2172% | 143.3664 | 1.556% | 1345 | 9190.997 | 9067.6336 | 1.36% | 0.2206%
2017-08-13 | 21 | 9217 | 123.4799 | 1.34% | 20.0206 | 0.2172% | 143.5005 | 1.557% | 1346 | 9196.9794 | 9073.4995 | 1.361% | 0.2206%
2017-06-04 | 13 | 9218 | 123.4993 | 1.34% | 20.0236 | 0.2172% | 143.5229 | 1.557% | 1347 | 9197.9764 | 9074.4771 | 1.361% | 0.2207%
2017-06-10 | 14 | 9224 | 123.6158 | 1.34% | 20.0412 | 0.2173% | 143.657 | 1.557% | 1348 | 9203.9588 | 9080.343 | 1.361% | 0.2207%
2017-06-02 | 13 | 9230 | 123.7323 | 1.341% | 20.0588 | 0.2173% | 143.7911 | 1.558% | 1349 | 9209.9412 | 9086.2089 | 1.362% | 0.2208%
2017-06-30 | 19 | 9238 | 123.8877 | 1.341% | 20.0823 | 0.2174% | 143.97 | 1.558% | 1350 | 9217.9177 | 9094.03 | 1.362% | 0.2208%
2017-07-13 | 24 | 9238 | 123.8877 | 1.341% | 20.0823 | 0.2174% | 143.97 | 1.558% | 1351 | 9217.9177 | 9094.03 | 1.362% | 0.2208%
2017-08-12 | 12 | 9238 | 123.8877 | 1.341% | 20.0823 | 0.2174% | 143.97 | 1.558% | 1352 | 9217.9177 | 9094.03 | 1.362% | 0.2208%
2017-08-15 | 10 | 9239 | 123.9071 | 1.341% | 20.0853 | 0.2174% | 143.9923 | 1.559% | 1353 | 9218.9147 | 9095.0077 | 1.362% | 0.2208%
2017-08-21 | 23 | 9240 | 123.9265 | 1.341% | 20.0882 | 0.2174% | 144.0147 | 1.559% | 1354 | 9219.9118 | 9095.9853 | 1.362% | 0.2208%
2017-07-03 | 21 | 9256 | 124.2372 | 1.342% | 20.1352 | 0.2175% | 144.3724 | 1.56% | 1355 | 9235.8648 | 9111.6276 | 1.364% | 0.221%
2017-08-31 | 21 | 9256 | 124.2372 | 1.342% | 20.1352 | 0.2175% | 144.3724 | 1.56% | 1356 | 9235.8648 | 9111.6276 | 1.364% | 0.221%
2017-06-17 | 20 | 9259 | 124.2954 | 1.342% | 20.144 | 0.2176% | 144.4395 | 1.56% | 1357 | 9238.856 | 9114.5605 | 1.364% | 0.221%
2017-07-01 | 22 | 9260 | 124.3148 | 1.342% | 20.147 | 0.2176% | 144.4618 | 1.56% | 1358 | 9239.853 | 9115.5382 | 1.364% | 0.221%
2017-08-06 | 13 | 9274 | 124.5867 | 1.343% | 20.1881 | 0.2177% | 144.7748 | 1.561% | 1359 | 9253.8119 | 9129.2252 | 1.365% | 0.2211%
2017-07-12 | 24 | 9276 | 124.6255 | 1.344% | 20.194 | 0.2177% | 144.8195 | 1.561% | 1360 | 9255.806 | 9131.1805 | 1.365% | 0.2212%
2017-06-18 | 12 | 9278 | 124.6643 | 1.344% | 20.1999 | 0.2177% | 144.8642 | 1.561% | 1361 | 9257.8001 | 9133.1358 | 1.365% | 0.2212%
2017-06-06 | 20 | 9279 | 124.6837 | 1.344% | 20.2028 | 0.2177% | 144.8866 | 1.561% | 1362 | 9258.7972 | 9134.1134 | 1.365% | 0.2212%
2017-08-20 | 23 | 9280 | 124.7032 | 1.344% | 20.2058 | 0.2177% | 144.9089 | 1.562% | 1363 | 9259.7942 | 9135.0911 | 1.365% | 0.2212%
2017-07-04 | 12 | 9286 | 124.8197 | 1.344% | 20.2234 | 0.2178% | 145.0431 | 1.562% | 1364 | 9265.7766 | 9140.9569 | 1.365% | 0.2212%
2017-06-29 | 13 | 9290 | 124.8973 | 1.344% | 20.2351 | 0.2178% | 145.1325 | 1.562% | 1365 | 9269.7649 | 9144.8675 | 1.366% | 0.2213%
2017-07-29 | 15 | 9293 | 124.9556 | 1.345% | 20.244 | 0.2178% | 145.1995 | 1.562% | 1366 | 9272.756 | 9147.8005 | 1.366% | 0.2213%
2017-08-30 | 21 | 9294 | 124.975 | 1.345% | 20.2469 | 0.2178% | 145.2219 | 1.563% | 1367 | 9273.7531 | 9148.7781 | 1.366% | 0.2213%
2017-08-26 | 13 | 9306 | 125.208 | 1.345% | 20.2822 | 0.2179% | 145.4902 | 1.563% | 1368 | 9285.7178 | 9160.5098 | 1.367% | 0.2214%
2017-08-09 | 19 | 9312 | 125.3245 | 1.346% | 20.2998 | 0.218% | 145.6243 | 1.564% | 1369 | 9291.7002 | 9166.3757 | 1.367% | 0.2215%
2017-07-23 | 10 | 9314 | 125.3633 | 1.346% | 20.3057 | 0.218% | 145.669 | 1.564% | 1370 | 9293.6943 | 9168.331 | 1.367% | 0.2215%
2017-07-15 | 10 | 9320 | 125.4798 | 1.346% | 20.3233 | 0.2181% | 145.8031 | 1.564% | 1371 | 9299.6767 | 9174.1969 | 1.368% | 0.2215%
2017-06-03 | 20 | 9326 | 125.5963 | 1.347% | 20.3409 | 0.2181% | 145.9373 | 1.565% | 1372 | 9305.6591 | 9180.0627 | 1.368% | 0.2216%
2017-08-25 | 21 | 9328 | 125.6352 | 1.347% | 20.3468 | 0.2181% | 145.982 | 1.565% | 1373 | 9307.6532 | 9182.018 | 1.368% | 0.2216%
2017-07-29 | 19 | 9330 | 125.674 | 1.347% | 20.3527 | 0.2181% | 146.0267 | 1.565% | 1374 | 9309.6473 | 9183.9733 | 1.368% | 0.2216%
2017-06-13 | 22 | 9334 | 125.7517 | 1.347% | 20.3644 | 0.2182% | 146.1161 | 1.565% | 1375 | 9313.6356 | 9187.8839 | 1.369% | 0.2216%
2017-06-11 | 13 | 9337 | 125.8099 | 1.347% | 20.3733 | 0.2182% | 146.1832 | 1.566% | 1376 | 9316.6267 | 9190.8168 | 1.369% | 0.2217%
2017-06-11 | 21 | 9343 | 125.9264 | 1.348% | 20.3909 | 0.2182% | 146.3173 | 1.566% | 1377 | 9322.6091 | 9196.6827 | 1.369% | 0.2217%
2017-08-11 | 22 | 9344 | 125.9458 | 1.348% | 20.3938 | 0.2183% | 146.3397 | 1.566% | 1378 | 9323.6062 | 9197.6603 | 1.369% | 0.2217%
2017-08-27 | 18 | 9345 | 125.9653 | 1.348% | 20.3968 | 0.2183% | 146.362 | 1.566% | 1379 | 9324.6032 | 9198.638 | 1.369% | 0.2217%
2017-07-25 | 10 | 9348 | 126.0235 | 1.348% | 20.4056 | 0.2183% | 146.4291 | 1.566% | 1380 | 9327.5944 | 9201.5709 | 1.37% | 0.2218%
2017-08-03 | 22 | 9350 | 126.0623 | 1.348% | 20.4115 | 0.2183% | 146.4738 | 1.567% | 1381 | 9329.5885 | 9203.5262 | 1.37% | 0.2218%
2017-07-16 | 20 | 9353 | 126.1206 | 1.348% | 20.4203 | 0.2183% | 146.5409 | 1.567% | 1382 | 9332.5797 | 9206.4591 | 1.37% | 0.2218%
2017-06-25 | 14 | 9356 | 126.1788 | 1.349% | 20.4291 | 0.2184% | 146.6079 | 1.567% | 1383 | 9335.5709 | 9209.3921 | 1.37% | 0.2218%
2017-08-25 | 12 | 9357 | 126.1983 | 1.349% | 20.432 | 0.2184% | 146.6303 | 1.567% | 1384 | 9336.568 | 9210.3697 | 1.37% | 0.2218%
2017-08-02 | 22 | 9360 | 126.2565 | 1.349% | 20.4408 | 0.2184% | 146.6974 | 1.567% | 1385 | 9339.5592 | 9213.3026 | 1.37% | 0.2219%
2017-08-14 | 23 | 9360 | 126.2565 | 1.349% | 20.4408 | 0.2184% | 146.6974 | 1.567% | 1386 | 9339.5592 | 9213.3026 | 1.37% | 0.2219%
2017-07-03 | 11 | 9361 | 126.2759 | 1.349% | 20.4438 | 0.2184% | 146.7197 | 1.567% | 1387 | 9340.5562 | 9214.2803 | 1.37% | 0.2219%
2017-06-24 | 20 | 9363 | 126.3148 | 1.349% | 20.4497 | 0.2184% | 146.7644 | 1.567% | 1388 | 9342.5503 | 9216.2356 | 1.371% | 0.2219%
2017-07-26 | 11 | 9365 | 126.3536 | 1.349% | 20.4555 | 0.2184% | 146.8091 | 1.568% | 1389 | 9344.5445 | 9218.1909 | 1.371% | 0.2219%
2017-08-06 | 22 | 9365 | 126.3536 | 1.349% | 20.4555 | 0.2184% | 146.8091 | 1.568% | 1390 | 9344.5445 | 9218.1909 | 1.371% | 0.2219%
2017-07-09 | 22 | 9368 | 126.4119 | 1.349% | 20.4644 | 0.2184% | 146.8762 | 1.568% | 1391 | 9347.5356 | 9221.1238 | 1.371% | 0.2219%
2017-07-30 | 19 | 9373 | 126.5089 | 1.35% | 20.479 | 0.2185% | 146.988 | 1.568% | 1392 | 9352.521 | 9226.012 | 1.371% | 0.222%
2017-08-09 | 16 | 9374 | 126.5284 | 1.35% | 20.482 | 0.2185% | 147.0103 | 1.568% | 1393 | 9353.518 | 9226.9897 | 1.371% | 0.222%
2017-06-02 | 20 | 9376 | 126.5672 | 1.35% | 20.4879 | 0.2185% | 147.055 | 1.568% | 1394 | 9355.5121 | 9228.945 | 1.371% | 0.222%
2017-07-05 | 11 | 9377 | 126.5866 | 1.35% | 20.4908 | 0.2185% | 147.0774 | 1.568% | 1395 | 9356.5092 | 9229.9226 | 1.371% | 0.222%
2017-08-13 | 20 | 9378 | 126.606 | 1.35% | 20.4937 | 0.2185% | 147.0998 | 1.569% | 1396 | 9357.5063 | 9230.9002 | 1.372% | 0.222%
2017-07-27 | 23 | 9380 | 126.6449 | 1.35% | 20.4996 | 0.2185% | 147.1445 | 1.569% | 1397 | 9359.5004 | 9232.8555 | 1.372% | 0.222%
2017-08-09 | 18 | 9380 | 126.6449 | 1.35% | 20.4996 | 0.2185% | 147.1445 | 1.569% | 1398 | 9359.5004 | 9232.8555 | 1.372% | 0.222%
2017-06-27 | 20 | 9385 | 126.7419 | 1.35% | 20.5143 | 0.2186% | 147.2562 | 1.569% | 1399 | 9364.4857 | 9237.7438 | 1.372% | 0.2221%
2017-06-30 | 18 | 9390 | 126.839 | 1.351% | 20.529 | 0.2186% | 147.368 | 1.569% | 1400 | 9369.471 | 9242.632 | 1.372% | 0.2221%
2017-08-27 | 17 | 9390 | 126.839 | 1.351% | 20.529 | 0.2186% | 147.368 | 1.569% | 1401 | 9369.471 | 9242.632 | 1.372% | 0.2221%
2017-06-03 | 14 | 9391 | 126.8584 | 1.351% | 20.5319 | 0.2186% | 147.3904 | 1.569% | 1402 | 9370.4681 | 9243.6096 | 1.372% | 0.2221%
2017-06-05 | 13 | 9392 | 126.8779 | 1.351% | 20.5349 | 0.2186% | 147.4127 | 1.57% | 1403 | 9371.4651 | 9244.5873 | 1.372% | 0.2221%
2017-07-30 | 17 | 9397 | 126.9749 | 1.351% | 20.5496 | 0.2187% | 147.5245 | 1.57% | 1404 | 9376.4504 | 9249.4755 | 1.373% | 0.2222%
2017-06-06 | 14 | 9401 | 127.0526 | 1.351% | 20.5613 | 0.2187% | 147.6139 | 1.57% | 1405 | 9380.4387 | 9253.3861 | 1.373% | 0.2222%
2017-07-01 | 14 | 9404 | 127.1109 | 1.352% | 20.5701 | 0.2187% | 147.681 | 1.57% | 1406 | 9383.4299 | 9256.319 | 1.373% | 0.2222%
2017-08-04 | 12 | 9404 | 127.1109 | 1.352% | 20.5701 | 0.2187% | 147.681 | 1.57% | 1407 | 9383.4299 | 9256.319 | 1.373% | 0.2222%
2017-06-22 | 19 | 9405 | 127.1303 | 1.352% | 20.5731 | 0.2187% | 147.7034 | 1.57% | 1408 | 9384.4269 | 9257.2966 | 1.373% | 0.2222%
2017-08-01 | 21 | 9407 | 127.1691 | 1.352% | 20.579 | 0.2188% | 147.7481 | 1.571% | 1409 | 9386.421 | 9259.2519 | 1.373% | 0.2223%
2017-06-26 | 14 | 9408 | 127.1885 | 1.352% | 20.5819 | 0.2188% | 147.7704 | 1.571% | 1410 | 9387.4181 | 9260.2296 | 1.373% | 0.2223%
2017-08-12 | 22 | 9408 | 127.1885 | 1.352% | 20.5819 | 0.2188% | 147.7704 | 1.571% | 1411 | 9387.4181 | 9260.2296 | 1.373% | 0.2223%
2017-08-30 | 20 | 9409 | 127.2079 | 1.352% | 20.5848 | 0.2188% | 147.7928 | 1.571% | 1412 | 9388.4152 | 9261.2072 | 1.374% | 0.2223%
2017-07-24 | 11 | 9411 | 127.2468 | 1.352% | 20.5907 | 0.2188% | 147.8375 | 1.571% | 1413 | 9390.4093 | 9263.1625 | 1.374% | 0.2223%
2017-06-10 | 20 | 9415 | 127.3244 | 1.352% | 20.6025 | 0.2188% | 147.9269 | 1.571% | 1414 | 9394.3975 | 9267.0731 | 1.374% | 0.2223%
2017-07-21 | 10 | 9419 | 127.4021 | 1.353% | 20.6142 | 0.2189% | 148.0163 | 1.571% | 1415 | 9398.3858 | 9270.9837 | 1.374% | 0.2224%
2017-07-16 | 13 | 9423 | 127.4798 | 1.353% | 20.626 | 0.2189% | 148.1058 | 1.572% | 1416 | 9402.374 | 9274.8942 | 1.374% | 0.2224%
2017-07-23 | 22 | 9425 | 127.5186 | 1.353% | 20.6319 | 0.2189% | 148.1505 | 1.572% | 1417 | 9404.3681 | 9276.8495 | 1.375% | 0.2224%
2017-06-21 | 21 | 9428 | 127.5769 | 1.353% | 20.6407 | 0.2189% | 148.2175 | 1.572% | 1418 | 9407.3593 | 9279.7825 | 1.375% | 0.2224%
2017-06-16 | 21 | 9437 | 127.7516 | 1.354% | 20.6671 | 0.219% | 148.4187 | 1.573% | 1419 | 9416.3329 | 9288.5813 | 1.375% | 0.2225%
2017-06-12 | 12 | 9439 | 127.7905 | 1.354% | 20.673 | 0.219% | 148.4634 | 1.573% | 1420 | 9418.327 | 9290.5366 | 1.375% | 0.2225%
2017-08-23 | 10 | 9442 | 127.8487 | 1.354% | 20.6818 | 0.219% | 148.5305 | 1.573% | 1421 | 9421.3182 | 9293.4695 | 1.376% | 0.2225%
2017-06-30 | 12 | 9443 | 127.8681 | 1.354% | 20.6847 | 0.219% | 148.5529 | 1.573% | 1422 | 9422.3153 | 9294.4471 | 1.376% | 0.2225%
2017-06-27 | 14 | 9448 | 127.9652 | 1.354% | 20.6994 | 0.2191% | 148.6646 | 1.574% | 1423 | 9427.3006 | 9299.3354 | 1.376% | 0.2226%
2017-08-18 | 24 | 9448 | 127.9652 | 1.354% | 20.6994 | 0.2191% | 148.6646 | 1.574% | 1424 | 9427.3006 | 9299.3354 | 1.376% | 0.2226%
2017-08-09 | 17 | 9449 | 127.9846 | 1.354% | 20.7024 | 0.2191% | 148.687 | 1.574% | 1425 | 9428.2976 | 9300.313 | 1.376% | 0.2226%
2017-06-01 | 20 | 9451 | 128.0235 | 1.355% | 20.7083 | 0.2191% | 148.7317 | 1.574% | 1426 | 9430.2917 | 9302.2683 | 1.376% | 0.2226%
2017-06-12 | 22 | 9457 | 128.14 | 1.355% | 20.7259 | 0.2192% | 148.8658 | 1.574% | 1427 | 9436.2741 | 9308.1342 | 1.377% | 0.2227%
2017-08-24 | 21 | 9466 | 128.3147 | 1.356% | 20.7523 | 0.2192% | 149.067 | 1.575% | 1428 | 9445.2477 | 9316.933 | 1.377% | 0.2227%
2017-07-22 | 24 | 9467 | 128.3341 | 1.356% | 20.7553 | 0.2192% | 149.0894 | 1.575% | 1429 | 9446.2447 | 9317.9106 | 1.377% | 0.2227%
2017-06-30 | 17 | 9469 | 128.373 | 1.356% | 20.7612 | 0.2193% | 149.1341 | 1.575% | 1430 | 9448.2388 | 9319.8659 | 1.377% | 0.2228%
2017-06-05 | 20 | 9476 | 128.5089 | 1.356% | 20.7817 | 0.2193% | 149.2906 | 1.575% | 1431 | 9455.2183 | 9326.7094 | 1.378% | 0.2228%
2017-08-24 | 13 | 9487 | 128.7225 | 1.357% | 20.814 | 0.2194% | 149.5365 | 1.576% | 1432 | 9466.186 | 9337.4635 | 1.379% | 0.2229%
2017-08-31 | 13 | 9491 | 128.8001 | 1.357% | 20.8258 | 0.2194% | 149.6259 | 1.577% | 1433 | 9470.1742 | 9341.3741 | 1.379% | 0.2229%
2017-06-28 | 20 | 9493 | 128.839 | 1.357% | 20.8317 | 0.2194% | 149.6706 | 1.577% | 1434 | 9472.1683 | 9343.3294 | 1.379% | 0.223%
2017-07-02 | 12 | 9495 | 128.8778 | 1.357% | 20.8376 | 0.2195% | 149.7154 | 1.577% | 1435 | 9474.1624 | 9345.2846 | 1.379% | 0.223%
2017-07-08 | 22 | 9495 | 128.8778 | 1.357% | 20.8376 | 0.2195% | 149.7154 | 1.577% | 1436 | 9474.1624 | 9345.2846 | 1.379% | 0.223%
2017-07-17 | 22 | 9495 | 128.8778 | 1.357% | 20.8376 | 0.2195% | 149.7154 | 1.577% | 1437 | 9474.1624 | 9345.2846 | 1.379% | 0.223%
2017-07-07 | 10 | 9496 | 128.8972 | 1.357% | 20.8405 | 0.2195% | 149.7377 | 1.577% | 1438 | 9475.1595 | 9346.2623 | 1.379% | 0.223%
2017-06-15 | 22 | 9499 | 128.9555 | 1.358% | 20.8493 | 0.2195% | 149.8048 | 1.577% | 1439 | 9478.1507 | 9349.1952 | 1.379% | 0.223%
2017-06-28 | 15 | 9501 | 128.9943 | 1.358% | 20.8552 | 0.2195% | 149.8495 | 1.577% | 1440 | 9480.1448 | 9351.1505 | 1.379% | 0.223%
2017-06-29 | 21 | 9501 | 128.9943 | 1.358% | 20.8552 | 0.2195% | 149.8495 | 1.577% | 1441 | 9480.1448 | 9351.1505 | 1.379% | 0.223%
2017-06-01 | 13 | 9505 | 129.072 | 1.358% | 20.8669 | 0.2195% | 149.9389 | 1.577% | 1442 | 9484.1331 | 9355.0611 | 1.38% | 0.2231%
2017-08-17 | 10 | 9509 | 129.1496 | 1.358% | 20.8787 | 0.2196% | 150.0283 | 1.578% | 1443 | 9488.1213 | 9358.9717 | 1.38% | 0.2231%
2017-07-29 | 16 | 9510 | 129.1691 | 1.358% | 20.8816 | 0.2196% | 150.0507 | 1.578% | 1444 | 9489.1184 | 9359.9493 | 1.38% | 0.2231%
2017-07-30 | 18 | 9522 | 129.4021 | 1.359% | 20.9169 | 0.2197% | 150.319 | 1.579% | 1445 | 9501.0831 | 9371.681 | 1.381% | 0.2232%
2017-06-22 | 12 | 9523 | 129.4215 | 1.359% | 20.9198 | 0.2197% | 150.3413 | 1.579% | 1446 | 9502.0802 | 9372.6587 | 1.381% | 0.2232%
2017-08-10 | 21 | 9530 | 129.5574 | 1.359% | 20.9404 | 0.2197% | 150.4978 | 1.579% | 1447 | 9509.0596 | 9379.5022 | 1.381% | 0.2233%
2017-08-16 | 23 | 9535 | 129.6545 | 1.36% | 20.9551 | 0.2198% | 150.6096 | 1.58% | 1448 | 9514.0449 | 9384.3904 | 1.382% | 0.2233%
2017-06-21 | 15 | 9536 | 129.6739 | 1.36% | 20.958 | 0.2198% | 150.6319 | 1.58% | 1449 | 9515.042 | 9385.3681 | 1.382% | 0.2233%
2017-08-25 | 20 | 9538 | 129.7127 | 1.36% | 20.9639 | 0.2198% | 150.6766 | 1.58% | 1450 | 9517.0361 | 9387.3234 | 1.382% | 0.2233%
2017-08-13 | 13 | 9539 | 129.7321 | 1.36% | 20.9669 | 0.2198% | 150.699 | 1.58% | 1451 | 9518.0331 | 9388.301 | 1.382% | 0.2233%
2017-08-02 | 13 | 9541 | 129.771 | 1.36% | 20.9727 | 0.2198% | 150.7437 | 1.58% | 1452 | 9520.0273 | 9390.2563 | 1.382% | 0.2233%
2017-08-31 | 20 | 9544 | 129.8292 | 1.36% | 20.9815 | 0.2198% | 150.8108 | 1.58% | 1453 | 9523.0185 | 9393.1892 | 1.382% | 0.2234%
2017-07-07 | 23 | 9549 | 129.9263 | 1.361% | 20.9962 | 0.2199% | 150.9225 | 1.581% | 1454 | 9528.0038 | 9398.0775 | 1.382% | 0.2234%
2017-06-05 | 14 | 9551 | 129.9651 | 1.361% | 21.0021 | 0.2199% | 150.9673 | 1.581% | 1455 | 9529.9979 | 9400.0327 | 1.383% | 0.2234%
2017-08-24 | 20 | 9552 | 129.9846 | 1.361% | 21.0051 | 0.2199% | 150.9896 | 1.581% | 1456 | 9530.9949 | 9401.0104 | 1.383% | 0.2234%
2017-07-10 | 21 | 9554 | 130.0234 | 1.361% | 21.0109 | 0.2199% | 151.0343 | 1.581% | 1457 | 9532.9891 | 9402.9657 | 1.383% | 0.2235%
2017-08-05 | 13 | 9555 | 130.0428 | 1.361% | 21.0139 | 0.2199% | 151.0567 | 1.581% | 1458 | 9533.9861 | 9403.9433 | 1.383% | 0.2235%
2017-07-25 | 23 | 9557 | 130.0816 | 1.361% | 21.0197 | 0.2199% | 151.1014 | 1.581% | 1459 | 9535.9803 | 9405.8986 | 1.383% | 0.2235%
2017-06-10 | 15 | 9558 | 130.1011 | 1.361% | 21.0227 | 0.2199% | 151.1237 | 1.581% | 1460 | 9536.9773 | 9406.8763 | 1.383% | 0.2235%
2017-06-25 | 19 | 9559 | 130.1205 | 1.361% | 21.0256 | 0.22% | 151.1461 | 1.581% | 1461 | 9537.9744 | 9407.8539 | 1.383% | 0.2235%
2017-08-07 | 22 | 9567 | 130.2758 | 1.362% | 21.0491 | 0.22% | 151.3249 | 1.582% | 1462 | 9545.9509 | 9415.6751 | 1.384% | 0.2236%
2017-08-05 | 21 | 9572 | 130.3729 | 1.362% | 21.0638 | 0.2201% | 151.4367 | 1.582% | 1463 | 9550.9362 | 9420.5633 | 1.384% | 0.2236%
2017-06-19 | 22 | 9574 | 130.4117 | 1.362% | 21.0697 | 0.2201% | 151.4814 | 1.582% | 1464 | 9552.9303 | 9422.5186 | 1.384% | 0.2236%
2017-06-17 | 19 | 9576 | 130.4506 | 1.362% | 21.0756 | 0.2201% | 151.5261 | 1.582% | 1465 | 9554.9244 | 9424.4739 | 1.384% | 0.2236%
2017-06-17 | 13 | 9577 | 130.47 | 1.362% | 21.0785 | 0.2201% | 151.5485 | 1.582% | 1466 | 9555.9215 | 9425.4515 | 1.384% | 0.2236%
2017-08-10 | 14 | 9579 | 130.5088 | 1.362% | 21.0844 | 0.2201% | 151.5932 | 1.583% | 1467 | 9557.9156 | 9427.4068 | 1.384% | 0.2237%
2017-07-03 | 20 | 9583 | 130.5865 | 1.363% | 21.0962 | 0.2201% | 151.6826 | 1.583% | 1468 | 9561.9038 | 9431.3174 | 1.385% | 0.2237%
2017-08-15 | 23 | 9586 | 130.6447 | 1.363% | 21.105 | 0.2202% | 151.7497 | 1.583% | 1469 | 9564.895 | 9434.2503 | 1.385% | 0.2237%
2017-07-29 | 18 | 9591 | 130.7418 | 1.363% | 21.1197 | 0.2202% | 151.8615 | 1.583% | 1470 | 9569.8803 | 9439.1385 | 1.385% | 0.2237%
2017-08-07 | 12 | 9591 | 130.7418 | 1.363% | 21.1197 | 0.2202% | 151.8615 | 1.583% | 1471 | 9569.8803 | 9439.1385 | 1.385% | 0.2237%
2017-06-18 | 22 | 9594 | 130.8001 | 1.363% | 21.1285 | 0.2202% | 151.9285 | 1.584% | 1472 | 9572.8715 | 9442.0715 | 1.385% | 0.2238%
2017-07-18 | 21 | 9594 | 130.8001 | 1.363% | 21.1285 | 0.2202% | 151.9285 | 1.584% | 1473 | 9572.8715 | 9442.0715 | 1.385% | 0.2238%
2017-07-14 | 24 | 9595 | 130.8195 | 1.363% | 21.1314 | 0.2202% | 151.9509 | 1.584% | 1474 | 9573.8686 | 9443.0491 | 1.385% | 0.2238%
2017-06-23 | 23 | 9597 | 130.8583 | 1.364% | 21.1373 | 0.2202% | 151.9956 | 1.584% | 1475 | 9575.8627 | 9445.0044 | 1.385% | 0.2238%
2017-08-26 | 19 | 9597 | 130.8583 | 1.364% | 21.1373 | 0.2202% | 151.9956 | 1.584% | 1476 | 9575.8627 | 9445.0044 | 1.385% | 0.2238%
2017-06-30 | 16 | 9598 | 130.8777 | 1.364% | 21.1402 | 0.2203% | 152.018 | 1.584% | 1477 | 9576.8598 | 9445.982 | 1.386% | 0.2238%
2017-08-30 | 16 | 9600 | 130.9166 | 1.364% | 21.1461 | 0.2203% | 152.0627 | 1.584% | 1478 | 9578.8539 | 9447.9373 | 1.386% | 0.2238%
2017-08-18 | 10 | 9605 | 131.0137 | 1.364% | 21.1608 | 0.2203% | 152.1745 | 1.584% | 1479 | 9583.8392 | 9452.8255 | 1.386% | 0.2239%
2017-06-04 | 19 | 9614 | 131.1884 | 1.365% | 21.1873 | 0.2204% | 152.3757 | 1.585% | 1480 | 9592.8127 | 9461.6243 | 1.387% | 0.2239%
2017-07-01 | 21 | 9615 | 131.2078 | 1.365% | 21.1902 | 0.2204% | 152.398 | 1.585% | 1481 | 9593.8098 | 9462.602 | 1.387% | 0.2239%
2017-07-29 | 17 | 9615 | 131.2078 | 1.365% | 21.1902 | 0.2204% | 152.398 | 1.585% | 1482 | 9593.8098 | 9462.602 | 1.387% | 0.2239%
2017-07-04 | 21 | 9617 | 131.2467 | 1.365% | 21.1961 | 0.2204% | 152.4427 | 1.585% | 1483 | 9595.8039 | 9464.5573 | 1.387% | 0.224%
2017-07-18 | 13 | 9617 | 131.2467 | 1.365% | 21.1961 | 0.2204% | 152.4427 | 1.585% | 1484 | 9595.8039 | 9464.5573 | 1.387% | 0.224%
2017-08-19 | 22 | 9617 | 131.2467 | 1.365% | 21.1961 | 0.2204% | 152.4427 | 1.585% | 1485 | 9595.8039 | 9464.5573 | 1.387% | 0.224%
2017-06-02 | 14 | 9623 | 131.3632 | 1.365% | 21.2137 | 0.2204% | 152.5769 | 1.586% | 1486 | 9601.7863 | 9470.4231 | 1.387% | 0.224%
2017-08-11 | 12 | 9623 | 131.3632 | 1.365% | 21.2137 | 0.2204% | 152.5769 | 1.586% | 1487 | 9601.7863 | 9470.4231 | 1.387% | 0.224%
2017-07-09 | 13 | 9628 | 131.4602 | 1.365% | 21.2284 | 0.2205% | 152.6886 | 1.586% | 1488 | 9606.7716 | 9475.3114 | 1.387% | 0.224%
2017-07-15 | 22 | 9631 | 131.5185 | 1.366% | 21.2372 | 0.2205% | 152.7557 | 1.586% | 1489 | 9609.7628 | 9478.2443 | 1.388% | 0.2241%
2017-06-22 | 18 | 9634 | 131.5767 | 1.366% | 21.246 | 0.2205% | 152.8228 | 1.586% | 1490 | 9612.754 | 9481.1772 | 1.388% | 0.2241%
2017-07-31 | 15 | 9635 | 131.5962 | 1.366% | 21.249 | 0.2205% | 152.8451 | 1.586% | 1491 | 9613.751 | 9482.1549 | 1.388% | 0.2241%
2017-06-23 | 12 | 9638 | 131.6544 | 1.366% | 21.2578 | 0.2206% | 152.9122 | 1.587% | 1492 | 9616.7422 | 9485.0878 | 1.388% | 0.2241%
2017-07-27 | 11 | 9642 | 131.7321 | 1.366% | 21.2695 | 0.2206% | 153.0016 | 1.587% | 1493 | 9620.7305 | 9488.9984 | 1.388% | 0.2241%
2017-06-06 | 19 | 9646 | 131.8097 | 1.366% | 21.2813 | 0.2206% | 153.091 | 1.587% | 1494 | 9624.7187 | 9492.909 | 1.389% | 0.2242%
2017-08-04 | 22 | 9650 | 131.8874 | 1.367% | 21.293 | 0.2207% | 153.1805 | 1.587% | 1495 | 9628.707 | 9496.8195 | 1.389% | 0.2242%
2017-08-14 | 12 | 9660 | 132.0816 | 1.367% | 21.3224 | 0.2207% | 153.404 | 1.588% | 1496 | 9638.6776 | 9506.596 | 1.389% | 0.2243%
2017-07-24 | 23 | 9662 | 132.1204 | 1.367% | 21.3283 | 0.2207% | 153.4487 | 1.588% | 1497 | 9640.6717 | 9508.5513 | 1.389% | 0.2243%
2017-07-12 | 10 | 9665 | 132.1787 | 1.368% | 21.3371 | 0.2208% | 153.5158 | 1.588% | 1498 | 9643.6629 | 9511.4842 | 1.39% | 0.2243%
2017-06-25 | 15 | 9668 | 132.2369 | 1.368% | 21.3459 | 0.2208% | 153.5829 | 1.589% | 1499 | 9646.6541 | 9514.4171 | 1.39% | 0.2244%
2017-07-11 | 11 | 9672 | 132.3146 | 1.368% | 21.3577 | 0.2208% | 153.6723 | 1.589% | 1500 | 9650.6423 | 9518.3277 | 1.39% | 0.2244%
2017-08-26 | 14 | 9674 | 132.3534 | 1.368% | 21.3636 | 0.2208% | 153.717 | 1.589% | 1501 | 9652.6364 | 9520.283 | 1.39% | 0.2244%
2017-06-24 | 11 | 9677 | 132.4117 | 1.368% | 21.3724 | 0.2209% | 153.7841 | 1.589% | 1502 | 9655.6276 | 9523.2159 | 1.39% | 0.2244%
2017-07-09 | 21 | 9681 | 132.4893 | 1.369% | 21.3841 | 0.2209% | 153.8735 | 1.589% | 1503 | 9659.6159 | 9527.1265 | 1.391% | 0.2245%
2017-08-30 | 19 | 9688 | 132.6253 | 1.369% | 21.4047 | 0.2209% | 154.03 | 1.59% | 1504 | 9666.5953 | 9533.97 | 1.391% | 0.2245%
2017-06-06 | 15 | 9696 | 132.7806 | 1.369% | 21.4282 | 0.221% | 154.2088 | 1.59% | 1505 | 9674.5718 | 9541.7912 | 1.392% | 0.2246%
2017-06-21 | 20 | 9705 | 132.9553 | 1.37% | 21.4547 | 0.2211% | 154.41 | 1.591% | 1506 | 9683.5453 | 9550.59 | 1.392% | 0.2246%
2017-06-26 | 20 | 9711 | 133.0718 | 1.37% | 21.4723 | 0.2211% | 154.5441 | 1.591% | 1507 | 9689.5277 | 9556.4559 | 1.392% | 0.2247%
2017-08-13 | 19 | 9711 | 133.0718 | 1.37% | 21.4723 | 0.2211% | 154.5441 | 1.591% | 1508 | 9689.5277 | 9556.4559 | 1.392% | 0.2247%
2017-06-03 | 15 | 9718 | 133.2078 | 1.371% | 21.4929 | 0.2212% | 154.7006 | 1.592% | 1509 | 9696.5071 | 9563.2994 | 1.393% | 0.2247%
2017-07-28 | 22 | 9718 | 133.2078 | 1.371% | 21.4929 | 0.2212% | 154.7006 | 1.592% | 1510 | 9696.5071 | 9563.2994 | 1.393% | 0.2247%
2017-07-06 | 11 | 9721 | 133.266 | 1.371% | 21.5017 | 0.2212% | 154.7677 | 1.592% | 1511 | 9699.4983 | 9566.2323 | 1.393% | 0.2248%
2017-07-17 | 13 | 9721 | 133.266 | 1.371% | 21.5017 | 0.2212% | 154.7677 | 1.592% | 1512 | 9699.4983 | 9566.2323 | 1.393% | 0.2248%
2017-07-28 | 11 | 9722 | 133.2854 | 1.371% | 21.5046 | 0.2212% | 154.7901 | 1.592% | 1513 | 9700.4954 | 9567.2099 | 1.393% | 0.2248%
2017-07-11 | 23 | 9723 | 133.3048 | 1.371% | 21.5076 | 0.2212% | 154.8124 | 1.592% | 1514 | 9701.4924 | 9568.1876 | 1.393% | 0.2248%
2017-07-16 | 19 | 9725 | 133.3437 | 1.371% | 21.5134 | 0.2212% | 154.8571 | 1.592% | 1515 | 9703.4866 | 9570.1429 | 1.393% | 0.2248%
2017-08-22 | 23 | 9725 | 133.3437 | 1.371% | 21.5134 | 0.2212% | 154.8571 | 1.592% | 1516 | 9703.4866 | 9570.1429 | 1.393% | 0.2248%
2017-06-05 | 15 | 9732 | 133.4796 | 1.372% | 21.534 | 0.2213% | 155.0136 | 1.593% | 1517 | 9710.466 | 9576.9864 | 1.394% | 0.2249%
2017-08-03 | 21 | 9734 | 133.5184 | 1.372% | 21.5399 | 0.2213% | 155.0583 | 1.593% | 1518 | 9712.4601 | 9578.9417 | 1.394% | 0.2249%
2017-07-31 | 20 | 9735 | 133.5379 | 1.372% | 21.5428 | 0.2213% | 155.0807 | 1.593% | 1519 | 9713.4572 | 9579.9193 | 1.394% | 0.2249%
2017-06-04 | 14 | 9737 | 133.5767 | 1.372% | 21.5487 | 0.2213% | 155.1254 | 1.593% | 1520 | 9715.4513 | 9581.8746 | 1.394% | 0.2249%
2017-06-30 | 13 | 9737 | 133.5767 | 1.372% | 21.5487 | 0.2213% | 155.1254 | 1.593% | 1521 | 9715.4513 | 9581.8746 | 1.394% | 0.2249%
2017-06-30 | 15 | 9738 | 133.5961 | 1.372% | 21.5516 | 0.2213% | 155.1477 | 1.593% | 1522 | 9716.4484 | 9582.8523 | 1.394% | 0.2249%
2017-06-13 | 21 | 9744 | 133.7126 | 1.372% | 21.5693 | 0.2214% | 155.2819 | 1.594% | 1523 | 9722.4307 | 9588.7181 | 1.394% | 0.2249%
2017-08-10 | 20 | 9746 | 133.7514 | 1.372% | 21.5751 | 0.2214% | 155.3266 | 1.594% | 1524 | 9724.4249 | 9590.6734 | 1.395% | 0.225%
2017-08-13 | 14 | 9747 | 133.7709 | 1.372% | 21.5781 | 0.2214% | 155.3489 | 1.594% | 1525 | 9725.4219 | 9591.6511 | 1.395% | 0.225%
2017-08-01 | 14 | 9754 | 133.9068 | 1.373% | 21.5987 | 0.2214% | 155.5054 | 1.594% | 1526 | 9732.4013 | 9598.4946 | 1.395% | 0.225%
2017-06-14 | 22 | 9755 | 133.9262 | 1.373% | 21.6016 | 0.2214% | 155.5278 | 1.594% | 1527 | 9733.3984 | 9599.4722 | 1.395% | 0.225%
2017-06-26 | 15 | 9762 | 134.0621 | 1.373% | 21.6222 | 0.2215% | 155.6843 | 1.595% | 1528 | 9740.3778 | 9606.3157 | 1.396% | 0.2251%
2017-08-11 | 21 | 9763 | 134.0815 | 1.373% | 21.6251 | 0.2215% | 155.7066 | 1.595% | 1529 | 9741.3749 | 9607.2934 | 1.396% | 0.2251%
2017-06-16 | 12 | 9772 | 134.2563 | 1.374% | 21.6516 | 0.2216% | 155.9078 | 1.595% | 1530 | 9750.3484 | 9616.0922 | 1.396% | 0.2252%
2017-06-30 | 14 | 9785 | 134.5087 | 1.375% | 21.6898 | 0.2217% | 156.1984 | 1.596% | 1531 | 9763.3102 | 9628.8016 | 1.397% | 0.2253%
2017-06-11 | 20 | 9791 | 134.6252 | 1.375% | 21.7074 | 0.2217% | 156.3326 | 1.597% | 1532 | 9769.2926 | 9634.6674 | 1.397% | 0.2253%
2017-06-18 | 21 | 9792 | 134.6446 | 1.375% | 21.7103 | 0.2217% | 156.3549 | 1.597% | 1533 | 9770.2897 | 9635.6451 | 1.397% | 0.2253%
2017-06-27 | 19 | 9794 | 134.6834 | 1.375% | 21.7162 | 0.2217% | 156.3996 | 1.597% | 1534 | 9772.2838 | 9637.6004 | 1.397% | 0.2253%
2017-06-27 | 15 | 9798 | 134.7611 | 1.375% | 21.728 | 0.2218% | 156.4891 | 1.597% | 1535 | 9776.272 | 9641.5109 | 1.398% | 0.2254%
2017-08-20 | 12 | 9798 | 134.7611 | 1.375% | 21.728 | 0.2218% | 156.4891 | 1.597% | 1536 | 9776.272 | 9641.5109 | 1.398% | 0.2254%
2017-06-10 | 16 | 9800 | 134.7999 | 1.376% | 21.7338 | 0.2218% | 156.5338 | 1.597% | 1537 | 9778.2662 | 9643.4662 | 1.398% | 0.2254%
2017-08-31 | 19 | 9802 | 134.8388 | 1.376% | 21.7397 | 0.2218% | 156.5785 | 1.597% | 1538 | 9780.2603 | 9645.4215 | 1.398% | 0.2254%
2017-08-03 | 13 | 9808 | 134.9553 | 1.376% | 21.7573 | 0.2218% | 156.7126 | 1.598% | 1539 | 9786.2427 | 9651.2874 | 1.398% | 0.2254%
2017-06-11 | 14 | 9822 | 135.2271 | 1.377% | 21.7985 | 0.2219% | 157.0256 | 1.599% | 1540 | 9800.2015 | 9664.9744 | 1.399% | 0.2255%
2017-06-17 | 16 | 9822 | 135.2271 | 1.377% | 21.7985 | 0.2219% | 157.0256 | 1.599% | 1541 | 9800.2015 | 9664.9744 | 1.399% | 0.2255%
2017-08-13 | 15 | 9825 | 135.2854 | 1.377% | 21.8073 | 0.222% | 157.0927 | 1.599% | 1542 | 9803.1927 | 9667.9073 | 1.399% | 0.2256%
2017-08-24 | 14 | 9828 | 135.3436 | 1.377% | 21.8161 | 0.222% | 157.1597 | 1.599% | 1543 | 9806.1839 | 9670.8403 | 1.4% | 0.2256%
2017-07-06 | 23 | 9830 | 135.3825 | 1.377% | 21.822 | 0.222% | 157.2044 | 1.599% | 1544 | 9808.178 | 9672.7956 | 1.4% | 0.2256%
2017-07-17 | 21 | 9830 | 135.3825 | 1.377% | 21.822 | 0.222% | 157.2044 | 1.599% | 1545 | 9808.178 | 9672.7956 | 1.4% | 0.2256%
2017-08-25 | 13 | 9834 | 135.4601 | 1.377% | 21.8337 | 0.222% | 157.2939 | 1.599% | 1546 | 9812.1663 | 9676.7061 | 1.4% | 0.2256%
2017-08-06 | 21 | 9835 | 135.4795 | 1.378% | 21.8367 | 0.222% | 157.3162 | 1.6% | 1547 | 9813.1633 | 9677.6838 | 1.4% | 0.2256%
2017-06-22 | 17 | 9836 | 135.499 | 1.378% | 21.8396 | 0.222% | 157.3386 | 1.6% | 1548 | 9814.1604 | 9678.6614 | 1.4% | 0.2256%
2017-08-21 | 11 | 9836 | 135.499 | 1.378% | 21.8396 | 0.222% | 157.3386 | 1.6% | 1549 | 9814.1604 | 9678.6614 | 1.4% | 0.2256%
2017-07-08 | 11 | 9837 | 135.5184 | 1.378% | 21.8426 | 0.222% | 157.3609 | 1.6% | 1550 | 9815.1574 | 9679.6391 | 1.4% | 0.2257%
2017-08-24 | 19 | 9842 | 135.6155 | 1.378% | 21.8573 | 0.2221% | 157.4727 | 1.6% | 1551 | 9820.1427 | 9684.5273 | 1.4% | 0.2257%
2017-06-17 | 18 | 9844 | 135.6543 | 1.378% | 21.8631 | 0.2221% | 157.5174 | 1.6% | 1552 | 9822.1369 | 9686.4826 | 1.4% | 0.2257%
2017-06-28 | 16 | 9849 | 135.7514 | 1.378% | 21.8778 | 0.2221% | 157.6292 | 1.6% | 1553 | 9827.1222 | 9691.3708 | 1.401% | 0.2257%
2017-06-03 | 19 | 9850 | 135.7708 | 1.378% | 21.8808 | 0.2221% | 157.6516 | 1.601% | 1554 | 9828.1192 | 9692.3484 | 1.401% | 0.2258%
2017-08-02 | 21 | 9850 | 135.7708 | 1.378% | 21.8808 | 0.2221% | 157.6516 | 1.601% | 1555 | 9828.1192 | 9692.3484 | 1.401% | 0.2258%
2017-07-21 | 23 | 9851 | 135.7902 | 1.378% | 21.8837 | 0.2221% | 157.6739 | 1.601% | 1556 | 9829.1163 | 9693.3261 | 1.401% | 0.2258%
2017-08-19 | 11 | 9851 | 135.7902 | 1.378% | 21.8837 | 0.2221% | 157.6739 | 1.601% | 1557 | 9829.1163 | 9693.3261 | 1.401% | 0.2258%
2017-06-13 | 13 | 9852 | 135.8096 | 1.378% | 21.8866 | 0.2222% | 157.6963 | 1.601% | 1558 | 9830.1134 | 9694.3037 | 1.401% | 0.2258%
2017-06-18 | 13 | 9852 | 135.8096 | 1.378% | 21.8866 | 0.2222% | 157.6963 | 1.601% | 1559 | 9830.1134 | 9694.3037 | 1.401% | 0.2258%
2017-08-30 | 17 | 9855 | 135.8679 | 1.379% | 21.8955 | 0.2222% | 157.7633 | 1.601% | 1560 | 9833.1045 | 9697.2367 | 1.401% | 0.2258%
2017-06-12 | 21 | 9856 | 135.8873 | 1.379% | 21.8984 | 0.2222% | 157.7857 | 1.601% | 1561 | 9834.1016 | 9698.2143 | 1.401% | 0.2258%
2017-06-29 | 14 | 9859 | 135.9455 | 1.379% | 21.9072 | 0.2222% | 157.8528 | 1.601% | 1562 | 9837.0928 | 9701.1472 | 1.401% | 0.2258%
2017-06-05 | 19 | 9860 | 135.965 | 1.379% | 21.9101 | 0.2222% | 157.8751 | 1.601% | 1563 | 9838.0899 | 9702.1249 | 1.401% | 0.2258%
2017-07-19 | 12 | 9861 | 135.9844 | 1.379% | 21.9131 | 0.2222% | 157.8975 | 1.601% | 1564 | 9839.0869 | 9703.1025 | 1.401% | 0.2258%
2017-08-16 | 11 | 9861 | 135.9844 | 1.379% | 21.9131 | 0.2222% | 157.8975 | 1.601% | 1565 | 9839.0869 | 9703.1025 | 1.401% | 0.2258%
2017-08-22 | 11 | 9865 | 136.062 | 1.379% | 21.9248 | 0.2222% | 157.9869 | 1.601% | 1566 | 9843.0752 | 9707.0131 | 1.402% | 0.2259%
2017-06-10 | 19 | 9867 | 136.1009 | 1.379% | 21.9307 | 0.2223% | 158.0316 | 1.602% | 1567 | 9845.0693 | 9708.9684 | 1.402% | 0.2259%
2017-06-14 | 12 | 9870 | 136.1591 | 1.38% | 21.9395 | 0.2223% | 158.0987 | 1.602% | 1568 | 9848.0605 | 9711.9013 | 1.402% | 0.2259%
2017-07-13 | 10 | 9871 | 136.1785 | 1.38% | 21.9425 | 0.2223% | 158.121 | 1.602% | 1569 | 9849.0575 | 9712.879 | 1.402% | 0.2259%
2017-06-15 | 12 | 9873 | 136.2174 | 1.38% | 21.9484 | 0.2223% | 158.1657 | 1.602% | 1570 | 9851.0516 | 9714.8343 | 1.402% | 0.2259%
2017-07-26 | 12 | 9874 | 136.2368 | 1.38% | 21.9513 | 0.2223% | 158.1881 | 1.602% | 1571 | 9852.0487 | 9715.8119 | 1.402% | 0.2259%
2017-08-01 | 20 | 9876 | 136.2756 | 1.38% | 21.9572 | 0.2223% | 158.2328 | 1.602% | 1572 | 9854.0428 | 9717.7672 | 1.402% | 0.2259%
2017-08-04 | 13 | 9876 | 136.2756 | 1.38% | 21.9572 | 0.2223% | 158.2328 | 1.602% | 1573 | 9854.0428 | 9717.7672 | 1.402% | 0.2259%
2017-06-17 | 14 | 9877 | 136.295 | 1.38% | 21.9601 | 0.2223% | 158.2552 | 1.602% | 1574 | 9855.0399 | 9718.7448 | 1.402% | 0.226%
2017-08-30 | 18 | 9879 | 136.3339 | 1.38% | 21.966 | 0.2224% | 158.2999 | 1.602% | 1575 | 9857.034 | 9720.7001 | 1.403% | 0.226%
2017-08-12 | 13 | 9884 | 136.431 | 1.38% | 21.9807 | 0.2224% | 158.4116 | 1.603% | 1576 | 9862.0193 | 9725.5884 | 1.403% | 0.226%
2017-06-17 | 17 | 9885 | 136.4504 | 1.38% | 21.9836 | 0.2224% | 158.434 | 1.603% | 1577 | 9863.0164 | 9726.566 | 1.403% | 0.226%
2017-08-23 | 22 | 9887 | 136.4892 | 1.38% | 21.9895 | 0.2224% | 158.4787 | 1.603% | 1578 | 9865.0105 | 9728.5213 | 1.403% | 0.226%
2017-08-31 | 14 | 9887 | 136.4892 | 1.38% | 21.9895 | 0.2224% | 158.4787 | 1.603% | 1579 | 9865.0105 | 9728.5213 | 1.403% | 0.226%
2017-06-19 | 11 | 9891 | 136.5669 | 1.381% | 22.0012 | 0.2224% | 158.5681 | 1.603% | 1580 | 9868.9988 | 9732.4319 | 1.403% | 0.2261%
2017-08-06 | 14 | 9894 | 136.6251 | 1.381% | 22.0101 | 0.2225% | 158.6352 | 1.603% | 1581 | 9871.9899 | 9735.3648 | 1.403% | 0.2261%
2017-06-17 | 15 | 9895 | 136.6446 | 1.381% | 22.013 | 0.2225% | 158.6576 | 1.603% | 1582 | 9872.987 | 9736.3424 | 1.403% | 0.2261%
2017-06-15 | 21 | 9896 | 136.664 | 1.381% | 22.0159 | 0.2225% | 158.6799 | 1.603% | 1583 | 9873.9841 | 9737.3201 | 1.404% | 0.2261%
2017-07-10 | 20 | 9897 | 136.6834 | 1.381% | 22.0189 | 0.2225% | 158.7023 | 1.604% | 1584 | 9874.9811 | 9738.2977 | 1.404% | 0.2261%
2017-07-10 | 12 | 9908 | 136.897 | 1.382% | 22.0512 | 0.2226% | 158.9482 | 1.604% | 1585 | 9885.9488 | 9749.0518 | 1.404% | 0.2262%
2017-08-11 | 20 | 9924 | 137.2076 | 1.383% | 22.0982 | 0.2227% | 159.3059 | 1.605% | 1586 | 9901.9018 | 9764.6941 | 1.405% | 0.2263%
2017-07-01 | 15 | 9926 | 137.2465 | 1.383% | 22.1041 | 0.2227% | 159.3506 | 1.605% | 1587 | 9903.8959 | 9766.6494 | 1.405% | 0.2263%
2017-07-04 | 13 | 9928 | 137.2853 | 1.383% | 22.11 | 0.2227% | 159.3953 | 1.606% | 1588 | 9905.89 | 9768.6047 | 1.405% | 0.2263%
2017-06-22 | 13 | 9929 | 137.3047 | 1.383% | 22.1129 | 0.2227% | 159.4176 | 1.606% | 1589 | 9906.8871 | 9769.5824 | 1.405% | 0.2263%
2017-08-26 | 15 | 9933 | 137.3824 | 1.383% | 22.1247 | 0.2227% | 159.5071 | 1.606% | 1590 | 9910.8753 | 9773.4929 | 1.406% | 0.2264%
2017-07-02 | 22 | 9934 | 137.4018 | 1.383% | 22.1276 | 0.2227% | 159.5294 | 1.606% | 1591 | 9911.8724 | 9774.4706 | 1.406% | 0.2264%
2017-08-13 | 18 | 9934 | 137.4018 | 1.383% | 22.1276 | 0.2227% | 159.5294 | 1.606% | 1592 | 9911.8724 | 9774.4706 | 1.406% | 0.2264%
2017-08-17 | 22 | 9934 | 137.4018 | 1.383% | 22.1276 | 0.2227% | 159.5294 | 1.606% | 1593 | 9911.8724 | 9774.4706 | 1.406% | 0.2264%
2017-06-16 | 20 | 9939 | 137.4989 | 1.383% | 22.1423 | 0.2228% | 159.6412 | 1.606% | 1594 | 9916.8577 | 9779.3588 | 1.406% | 0.2264%
2017-08-10 | 15 | 9945 | 137.6154 | 1.384% | 22.1599 | 0.2228% | 159.7753 | 1.607% | 1595 | 9922.8401 | 9785.2247 | 1.406% | 0.2265%
2017-06-25 | 16 | 9947 | 137.6542 | 1.384% | 22.1658 | 0.2228% | 159.82 | 1.607% | 1596 | 9924.8342 | 9787.18 | 1.406% | 0.2265%
2017-07-14 | 10 | 9947 | 137.6542 | 1.384% | 22.1658 | 0.2228% | 159.82 | 1.607% | 1597 | 9924.8342 | 9787.18 | 1.406% | 0.2265%
2017-08-15 | 11 | 9950 | 137.7125 | 1.384% | 22.1746 | 0.2229% | 159.8871 | 1.607% | 1598 | 9927.8254 | 9790.1129 | 1.407% | 0.2265%
2017-06-25 | 18 | 9956 | 137.829 | 1.384% | 22.1923 | 0.2229% | 160.0212 | 1.607% | 1599 | 9933.8077 | 9795.9788 | 1.407% | 0.2265%
2017-08-12 | 21 | 9960 | 137.9067 | 1.385% | 22.204 | 0.2229% | 160.1107 | 1.608% | 1600 | 9937.796 | 9799.8893 | 1.407% | 0.2266%
2017-06-03 | 16 | 9961 | 137.9261 | 1.385% | 22.2069 | 0.2229% | 160.133 | 1.608% | 1601 | 9938.7931 | 9800.867 | 1.407% | 0.2266%
2017-06-06 | 18 | 9964 | 137.9843 | 1.385% | 22.2158 | 0.223% | 160.2001 | 1.608% | 1602 | 9941.7842 | 9803.7999 | 1.407% | 0.2266%
2017-06-04 | 18 | 9972 | 138.1397 | 1.385% | 22.2393 | 0.223% | 160.3789 | 1.608% | 1603 | 9949.7607 | 9811.6211 | 1.408% | 0.2267%
2017-06-21 | 16 | 9972 | 138.1397 | 1.385% | 22.2393 | 0.223% | 160.3789 | 1.608% | 1604 | 9949.7607 | 9811.6211 | 1.408% | 0.2267%
2017-07-20 | 23 | 9972 | 138.1397 | 1.385% | 22.2393 | 0.223% | 160.3789 | 1.608% | 1605 | 9949.7607 | 9811.6211 | 1.408% | 0.2267%
2017-06-01 | 19 | 9979 | 138.2756 | 1.386% | 22.2598 | 0.2231% | 160.5354 | 1.609% | 1606 | 9956.7402 | 9818.4646 | 1.408% | 0.2267%
2017-06-05 | 18 | 9979 | 138.2756 | 1.386% | 22.2598 | 0.2231% | 160.5354 | 1.609% | 1607 | 9956.7402 | 9818.4646 | 1.408% | 0.2267%
2017-06-02 | 15 | 9980 | 138.295 | 1.386% | 22.2628 | 0.2231% | 160.5578 | 1.609% | 1608 | 9957.7372 | 9819.4422 | 1.408% | 0.2267%
2017-08-25 | 19 | 9980 | 138.295 | 1.386% | 22.2628 | 0.2231% | 160.5578 | 1.609% | 1609 | 9957.7372 | 9819.4422 | 1.408% | 0.2267%
2017-07-16 | 14 | 9982 | 138.3338 | 1.386% | 22.2687 | 0.2231% | 160.6025 | 1.609% | 1610 | 9959.7313 | 9821.3975 | 1.408% | 0.2267%
2017-06-01 | 14 | 9983 | 138.3532 | 1.386% | 22.2716 | 0.2231% | 160.6248 | 1.609% | 1611 | 9960.7284 | 9822.3752 | 1.409% | 0.2267%
2017-08-13 | 17 | 9994 | 138.5668 | 1.387% | 22.3039 | 0.2232% | 160.8707 | 1.61% | 1612 | 9971.6961 | 9833.1293 | 1.409% | 0.2268%
2017-08-26 | 18 | 9995 | 138.5862 | 1.387% | 22.3069 | 0.2232% | 160.8931 | 1.61% | 1613 | 9972.6931 | 9834.1069 | 1.409% | 0.2268%
2017-06-06 | 16 | 9997 | 138.6251 | 1.387% | 22.3127 | 0.2232% | 160.9378 | 1.61% | 1614 | 9974.6873 | 9836.0622 | 1.409% | 0.2268%
2017-06-10 | 17 | 9998 | 138.6445 | 1.387% | 22.3157 | 0.2232% | 160.9602 | 1.61% | 1615 | 9975.6843 | 9837.0398 | 1.409% | 0.2269%
2017-08-13 | 16 | 10002 | 138.7222 | 1.387% | 22.3274 | 0.2232% | 161.0496 | 1.61% | 1616 | 9979.6726 | 9840.9504 | 1.41% | 0.2269%
2017-06-02 | 19 | 10004 | 138.761 | 1.387% | 22.3333 | 0.2232% | 161.0943 | 1.61% | 1617 | 9981.6667 | 9842.9057 | 1.41% | 0.2269%
2017-07-26 | 22 | 10010 | 138.8775 | 1.387% | 22.3509 | 0.2233% | 161.2284 | 1.611% | 1618 | 9987.6491 | 9848.7716 | 1.41% | 0.2269%
2017-08-03 | 20 | 10012 | 138.9163 | 1.387% | 22.3568 | 0.2233% | 161.2731 | 1.611% | 1619 | 9989.6432 | 9850.7269 | 1.41% | 0.227%
2017-08-05 | 14 | 10016 | 138.994 | 1.388% | 22.3686 | 0.2233% | 161.3626 | 1.611% | 1620 | 9993.6314 | 9854.6374 | 1.41% | 0.227%
2017-07-01 | 20 | 10018 | 139.0328 | 1.388% | 22.3744 | 0.2233% | 161.4073 | 1.611% | 1621 | 9995.6256 | 9856.5927 | 1.411% | 0.227%
2017-06-19 | 21 | 10019 | 139.0522 | 1.388% | 22.3774 | 0.2233% | 161.4296 | 1.611% | 1622 | 9996.6226 | 9857.5704 | 1.411% | 0.227%
2017-06-29 | 20 | 10020 | 139.0717 | 1.388% | 22.3803 | 0.2234% | 161.452 | 1.611% | 1623 | 9997.6197 | 9858.548 | 1.411% | 0.227%
2017-06-24 | 19 | 10022 | 139.1105 | 1.388% | 22.3862 | 0.2234% | 161.4967 | 1.611% | 1624 | 9999.6138 | 9860.5033 | 1.411% | 0.227%
2017-06-04 | 15 | 10027 | 139.2076 | 1.388% | 22.4009 | 0.2234% | 161.6085 | 1.612% | 1625 | 10004.5991 | 9865.3915 | 1.411% | 0.2271%
2017-06-27 | 16 | 10029 | 139.2464 | 1.388% | 22.4068 | 0.2234% | 161.6532 | 1.612% | 1626 | 10006.5932 | 9867.3468 | 1.411% | 0.2271%
2017-07-18 | 20 | 10029 | 139.2464 | 1.388% | 22.4068 | 0.2234% | 161.6532 | 1.612% | 1627 | 10006.5932 | 9867.3468 | 1.411% | 0.2271%
2017-06-22 | 16 | 10030 | 139.2658 | 1.388% | 22.4097 | 0.2234% | 161.6755 | 1.612% | 1628 | 10007.5903 | 9868.3245 | 1.411% | 0.2271%
2017-07-23 | 21 | 10030 | 139.2658 | 1.388% | 22.4097 | 0.2234% | 161.6755 | 1.612% | 1629 | 10007.5903 | 9868.3245 | 1.411% | 0.2271%
2017-07-24 | 12 | 10035 | 139.3629 | 1.389% | 22.4244 | 0.2235% | 161.7873 | 1.612% | 1630 | 10012.5756 | 9873.2127 | 1.412% | 0.2271%
2017-06-10 | 18 | 10044 | 139.5377 | 1.389% | 22.4509 | 0.2235% | 161.9885 | 1.613% | 1631 | 10021.5491 | 9882.0115 | 1.412% | 0.2272%
2017-07-20 | 11 | 10051 | 139.6736 | 1.39% | 22.4714 | 0.2236% | 162.145 | 1.613% | 1632 | 10028.5286 | 9888.855 | 1.412% | 0.2272%
2017-06-12 | 13 | 10052 | 139.693 | 1.39% | 22.4744 | 0.2236% | 162.1674 | 1.613% | 1633 | 10029.5256 | 9889.8326 | 1.412% | 0.2272%
2017-06-05 | 16 | 10054 | 139.7318 | 1.39% | 22.4802 | 0.2236% | 162.2121 | 1.613% | 1634 | 10031.5198 | 9891.7879 | 1.413% | 0.2273%
2017-07-31 | 16 | 10054 | 139.7318 | 1.39% | 22.4802 | 0.2236% | 162.2121 | 1.613% | 1635 | 10031.5198 | 9891.7879 | 1.413% | 0.2273%
2017-06-27 | 18 | 10059 | 139.8289 | 1.39% | 22.4949 | 0.2236% | 162.3239 | 1.614% | 1636 | 10036.5051 | 9896.6761 | 1.413% | 0.2273%
2017-06-01 | 15 | 10064 | 139.926 | 1.39% | 22.5096 | 0.2237% | 162.4356 | 1.614% | 1637 | 10041.4904 | 9901.5644 | 1.413% | 0.2273%
2017-06-21 | 19 | 10065 | 139.9454 | 1.39% | 22.5126 | 0.2237% | 162.458 | 1.614% | 1638 | 10042.4874 | 9902.542 | 1.413% | 0.2273%
2017-08-07 | 21 | 10066 | 139.9648 | 1.39% | 22.5155 | 0.2237% | 162.4803 | 1.614% | 1639 | 10043.4845 | 9903.5197 | 1.413% | 0.2273%
2017-08-26 | 16 | 10067 | 139.9843 | 1.391% | 22.5184 | 0.2237% | 162.5027 | 1.614% | 1640 | 10044.4816 | 9904.4973 | 1.413% | 0.2274%
2017-06-26 | 16 | 10070 | 140.0425 | 1.391% | 22.5273 | 0.2237% | 162.5698 | 1.614% | 1641 | 10047.4727 | 9907.4302 | 1.414% | 0.2274%
2017-08-04 | 21 | 10071 | 140.0619 | 1.391% | 22.5302 | 0.2237% | 162.5921 | 1.614% | 1642 | 10048.4698 | 9908.4079 | 1.414% | 0.2274%
2017-06-28 | 19 | 10072 | 140.0813 | 1.391% | 22.5331 | 0.2237% | 162.6145 | 1.615% | 1643 | 10049.4669 | 9909.3855 | 1.414% | 0.2274%
2017-07-22 | 11 | 10072 | 140.0813 | 1.391% | 22.5331 | 0.2237% | 162.6145 | 1.615% | 1644 | 10049.4669 | 9909.3855 | 1.414% | 0.2274%
2017-07-09 | 20 | 10076 | 140.159 | 1.391% | 22.5449 | 0.2237% | 162.7039 | 1.615% | 1645 | 10053.4551 | 9913.2961 | 1.414% | 0.2274%
2017-08-20 | 22 | 10077 | 140.1784 | 1.391% | 22.5478 | 0.2238% | 162.7263 | 1.615% | 1646 | 10054.4522 | 9914.2737 | 1.414% | 0.2274%
2017-06-25 | 17 | 10082 | 140.2755 | 1.391% | 22.5625 | 0.2238% | 162.838 | 1.615% | 1647 | 10059.4375 | 9919.162 | 1.414% | 0.2275%
2017-07-08 | 21 | 10083 | 140.2949 | 1.391% | 22.5655 | 0.2238% | 162.8604 | 1.615% | 1648 | 10060.4345 | 9920.1396 | 1.414% | 0.2275%
2017-06-03 | 18 | 10085 | 140.3338 | 1.392% | 22.5713 | 0.2238% | 162.9051 | 1.615% | 1649 | 10062.4287 | 9922.0949 | 1.414% | 0.2275%
2017-08-24 | 18 | 10085 | 140.3338 | 1.392% | 22.5713 | 0.2238% | 162.9051 | 1.615% | 1650 | 10062.4287 | 9922.0949 | 1.414% | 0.2275%
2017-08-05 | 20 | 10088 | 140.392 | 1.392% | 22.5802 | 0.2238% | 162.9722 | 1.616% | 1651 | 10065.4198 | 9925.0278 | 1.415% | 0.2275%
2017-06-04 | 17 | 10092 | 140.4697 | 1.392% | 22.5919 | 0.2239% | 163.0616 | 1.616% | 1652 | 10069.4081 | 9928.9384 | 1.415% | 0.2275%
2017-06-11 | 15 | 10094 | 140.5085 | 1.392% | 22.5978 | 0.2239% | 163.1063 | 1.616% | 1653 | 10071.4022 | 9930.8937 | 1.415% | 0.2276%
2017-08-06 | 20 | 10094 | 140.5085 | 1.392% | 22.5978 | 0.2239% | 163.1063 | 1.616% | 1654 | 10071.4022 | 9930.8937 | 1.415% | 0.2276%
2017-06-04 | 16 | 10097 | 140.5668 | 1.392% | 22.6066 | 0.2239% | 163.1734 | 1.616% | 1655 | 10074.3934 | 9933.8266 | 1.415% | 0.2276%
2017-07-05 | 22 | 10098 | 140.5862 | 1.392% | 22.6095 | 0.2239% | 163.1957 | 1.616% | 1656 | 10075.3905 | 9934.8043 | 1.415% | 0.2276%
2017-08-24 | 15 | 10102 | 140.6639 | 1.392% | 22.6213 | 0.2239% | 163.2851 | 1.616% | 1657 | 10079.3787 | 9938.7149 | 1.415% | 0.2276%
2017-08-11 | 13 | 10103 | 140.6833 | 1.392% | 22.6242 | 0.2239% | 163.3075 | 1.616% | 1658 | 10080.3758 | 9939.6925 | 1.415% | 0.2276%
2017-08-21 | 22 | 10107 | 140.7609 | 1.393% | 22.636 | 0.224% | 163.3969 | 1.617% | 1659 | 10084.364 | 9943.6031 | 1.416% | 0.2276%
2017-07-09 | 14 | 10108 | 140.7804 | 1.393% | 22.6389 | 0.224% | 163.4193 | 1.617% | 1660 | 10085.3611 | 9944.5807 | 1.416% | 0.2277%
2017-07-16 | 18 | 10109 | 140.7998 | 1.393% | 22.6419 | 0.224% | 163.4416 | 1.617% | 1661 | 10086.3581 | 9945.5584 | 1.416% | 0.2277%
2017-08-07 | 13 | 10112 | 140.858 | 1.393% | 22.6507 | 0.224% | 163.5087 | 1.617% | 1662 | 10089.3493 | 9948.4913 | 1.416% | 0.2277%
2017-06-03 | 17 | 10113 | 140.8774 | 1.393% | 22.6536 | 0.224% | 163.5311 | 1.617% | 1663 | 10090.3464 | 9949.4689 | 1.416% | 0.2277%
2017-08-26 | 17 | 10114 | 140.8969 | 1.393% | 22.6566 | 0.224% | 163.5534 | 1.617% | 1664 | 10091.3434 | 9950.4466 | 1.416% | 0.2277%
2017-06-28 | 17 | 10116 | 140.9357 | 1.393% | 22.6624 | 0.224% | 163.5981 | 1.617% | 1665 | 10093.3376 | 9952.4019 | 1.416% | 0.2277%
2017-07-03 | 12 | 10122 | 141.0522 | 1.394% | 22.6801 | 0.2241% | 163.7323 | 1.618% | 1666 | 10099.3199 | 9958.2677 | 1.416% | 0.2278%
2017-07-13 | 23 | 10125 | 141.1104 | 1.394% | 22.6889 | 0.2241% | 163.7993 | 1.618% | 1667 | 10102.3111 | 9961.2007 | 1.417% | 0.2278%
2017-07-15 | 21 | 10125 | 141.1104 | 1.394% | 22.6889 | 0.2241% | 163.7993 | 1.618% | 1668 | 10102.3111 | 9961.2007 | 1.417% | 0.2278%
2017-08-31 | 15 | 10125 | 141.1104 | 1.394% | 22.6889 | 0.2241% | 163.7993 | 1.618% | 1669 | 10102.3111 | 9961.2007 | 1.417% | 0.2278%
2017-06-18 | 20 | 10127 | 141.1493 | 1.394% | 22.6948 | 0.2241% | 163.844 | 1.618% | 1670 | 10104.3052 | 9963.156 | 1.417% | 0.2278%
2017-07-05 | 12 | 10128 | 141.1687 | 1.394% | 22.6977 | 0.2241% | 163.8664 | 1.618% | 1671 | 10105.3023 | 9964.1336 | 1.417% | 0.2278%
2017-08-31 | 18 | 10130 | 141.2075 | 1.394% | 22.7036 | 0.2241% | 163.9111 | 1.618% | 1672 | 10107.2964 | 9966.0889 | 1.417% | 0.2278%
2017-06-06 | 17 | 10131 | 141.2269 | 1.394% | 22.7065 | 0.2241% | 163.9335 | 1.618% | 1673 | 10108.2935 | 9967.0665 | 1.417% | 0.2278%
2017-06-05 | 17 | 10137 | 141.3434 | 1.394% | 22.7241 | 0.2242% | 164.0676 | 1.619% | 1674 | 10114.2759 | 9972.9324 | 1.417% | 0.2279%
2017-07-02 | 13 | 10137 | 141.3434 | 1.394% | 22.7241 | 0.2242% | 164.0676 | 1.619% | 1675 | 10114.2759 | 9972.9324 | 1.417% | 0.2279%
2017-07-17 | 20 | 10137 | 141.3434 | 1.394% | 22.7241 | 0.2242% | 164.0676 | 1.619% | 1676 | 10114.2759 | 9972.9324 | 1.417% | 0.2279%
2017-08-02 | 14 | 10145 | 141.4988 | 1.395% | 22.7477 | 0.2242% | 164.2464 | 1.619% | 1677 | 10122.2523 | 9980.7536 | 1.418% | 0.2279%
2017-07-28 | 21 | 10148 | 141.557 | 1.395% | 22.7565 | 0.2242% | 164.3135 | 1.619% | 1678 | 10125.2435 | 9983.6865 | 1.418% | 0.2279%
2017-06-22 | 15 | 10150 | 141.5959 | 1.395% | 22.7623 | 0.2243% | 164.3582 | 1.619% | 1679 | 10127.2377 | 9985.6418 | 1.418% | 0.228%
2017-07-04 | 20 | 10160 | 141.79 | 1.396% | 22.7917 | 0.2243% | 164.5818 | 1.62% | 1680 | 10137.2083 | 9995.4182 | 1.419% | 0.228%
2017-07-03 | 19 | 10164 | 141.8677 | 1.396% | 22.8035 | 0.2244% | 164.6712 | 1.62% | 1681 | 10141.1965 | 9999.3288 | 1.419% | 0.2281%
2017-06-22 | 14 | 10165 | 141.8871 | 1.396% | 22.8064 | 0.2244% | 164.6935 | 1.62% | 1682 | 10142.1936 | 10000.3065 | 1.419% | 0.2281%
2017-07-19 | 22 | 10167 | 141.9259 | 1.396% | 22.8123 | 0.2244% | 164.7382 | 1.62% | 1683 | 10144.1877 | 10002.2618 | 1.419% | 0.2281%
2017-06-13 | 20 | 10173 | 142.0424 | 1.396% | 22.8299 | 0.2244% | 164.8724 | 1.621% | 1684 | 10150.1701 | 10008.1276 | 1.419% | 0.2281%
2017-06-26 | 19 | 10180 | 142.1784 | 1.397% | 22.8505 | 0.2245% | 165.0289 | 1.621% | 1685 | 10157.1495 | 10014.9711 | 1.42% | 0.2282%
2017-08-12 | 20 | 10182 | 142.2172 | 1.397% | 22.8564 | 0.2245% | 165.0736 | 1.621% | 1686 | 10159.1436 | 10016.9264 | 1.42% | 0.2282%
2017-08-14 | 22 | 10182 | 142.2172 | 1.397% | 22.8564 | 0.2245% | 165.0736 | 1.621% | 1687 | 10159.1436 | 10016.9264 | 1.42% | 0.2282%
2017-06-27 | 17 | 10184 | 142.256 | 1.397% | 22.8623 | 0.2245% | 165.1183 | 1.621% | 1688 | 10161.1377 | 10018.8817 | 1.42% | 0.2282%
2017-08-19 | 21 | 10190 | 142.3725 | 1.397% | 22.8799 | 0.2245% | 165.2524 | 1.622% | 1689 | 10167.1201 | 10024.7476 | 1.42% | 0.2282%
2017-08-02 | 20 | 10193 | 142.4308 | 1.397% | 22.8887 | 0.2246% | 165.3195 | 1.622% | 1690 | 10170.1113 | 10027.6805 | 1.42% | 0.2283%
2017-07-15 | 11 | 10194 | 142.4502 | 1.397% | 22.8916 | 0.2246% | 165.3418 | 1.622% | 1691 | 10171.1084 | 10028.6582 | 1.42% | 0.2283%
2017-08-10 | 19 | 10196 | 142.489 | 1.397% | 22.8975 | 0.2246% | 165.3866 | 1.622% | 1692 | 10173.1025 | 10030.6134 | 1.421% | 0.2283%
2017-06-28 | 18 | 10199 | 142.5473 | 1.398% | 22.9063 | 0.2246% | 165.4536 | 1.622% | 1693 | 10176.0937 | 10033.5464 | 1.421% | 0.2283%
2017-06-11 | 19 | 10201 | 142.5861 | 1.398% | 22.9122 | 0.2246% | 165.4983 | 1.622% | 1694 | 10178.0878 | 10035.5017 | 1.421% | 0.2283%
2017-07-25 | 11 | 10207 | 142.7026 | 1.398% | 22.9298 | 0.2246% | 165.6325 | 1.623% | 1695 | 10184.0702 | 10041.3675 | 1.421% | 0.2284%
2017-08-01 | 15 | 10207 | 142.7026 | 1.398% | 22.9298 | 0.2246% | 165.6325 | 1.623% | 1696 | 10184.0702 | 10041.3675 | 1.421% | 0.2284%
2017-08-14 | 13 | 10209 | 142.7415 | 1.398% | 22.9357 | 0.2247% | 165.6772 | 1.623% | 1697 | 10186.0643 | 10043.3228 | 1.421% | 0.2284%
2017-07-17 | 14 | 10219 | 142.9356 | 1.399% | 22.9651 | 0.2247% | 165.9007 | 1.623% | 1698 | 10196.0349 | 10053.0993 | 1.422% | 0.2284%
2017-07-18 | 14 | 10224 | 143.0327 | 1.399% | 22.9798 | 0.2248% | 166.0125 | 1.624% | 1699 | 10201.0202 | 10057.9875 | 1.422% | 0.2285%
2017-08-10 | 16 | 10229 | 143.1298 | 1.399% | 22.9945 | 0.2248% | 166.1243 | 1.624% | 1700 | 10206.0055 | 10062.8757 | 1.422% | 0.2285%
2017-06-21 | 17 | 10235 | 143.2463 | 1.4% | 23.0121 | 0.2248% | 166.2584 | 1.624% | 1701 | 10211.9879 | 10068.7416 | 1.423% | 0.2286%
2017-07-12 | 23 | 10236 | 143.2657 | 1.4% | 23.0151 | 0.2248% | 166.2808 | 1.624% | 1702 | 10212.9849 | 10069.7192 | 1.423% | 0.2286%
2017-08-07 | 20 | 10236 | 143.2657 | 1.4% | 23.0151 | 0.2248% | 166.2808 | 1.624% | 1703 | 10212.9849 | 10069.7192 | 1.423% | 0.2286%
2017-07-10 | 19 | 10240 | 143.3434 | 1.4% | 23.0268 | 0.2249% | 166.3702 | 1.625% | 1704 | 10216.9732 | 10073.6298 | 1.423% | 0.2286%
2017-07-23 | 11 | 10243 | 143.4016 | 1.4% | 23.0356 | 0.2249% | 166.4373 | 1.625% | 1705 | 10219.9644 | 10076.5627 | 1.423% | 0.2286%
2017-06-18 | 14 | 10245 | 143.4405 | 1.4% | 23.0415 | 0.2249% | 166.482 | 1.625% | 1706 | 10221.9585 | 10078.518 | 1.423% | 0.2286%
2017-08-31 | 16 | 10245 | 143.4405 | 1.4% | 23.0415 | 0.2249% | 166.482 | 1.625% | 1707 | 10221.9585 | 10078.518 | 1.423% | 0.2286%
2017-06-24 | 12 | 10246 | 143.4599 | 1.4% | 23.0445 | 0.2249% | 166.5043 | 1.625% | 1708 | 10222.9555 | 10079.4957 | 1.423% | 0.2286%
2017-06-23 | 22 | 10249 | 143.5181 | 1.4% | 23.0533 | 0.2249% | 166.5714 | 1.625% | 1709 | 10225.9467 | 10082.4286 | 1.423% | 0.2286%
2017-07-16 | 17 | 10249 | 143.5181 | 1.4% | 23.0533 | 0.2249% | 166.5714 | 1.625% | 1710 | 10225.9467 | 10082.4286 | 1.423% | 0.2286%
2017-08-25 | 14 | 10250 | 143.5376 | 1.4% | 23.0562 | 0.2249% | 166.5938 | 1.625% | 1711 | 10226.9438 | 10083.4062 | 1.424% | 0.2287%
2017-06-19 | 20 | 10255 | 143.6346 | 1.401% | 23.0709 | 0.225% | 166.7055 | 1.626% | 1712 | 10231.9291 | 10088.2945 | 1.424% | 0.2287%
2017-07-31 | 19 | 10256 | 143.6541 | 1.401% | 23.0738 | 0.225% | 166.7279 | 1.626% | 1713 | 10232.9262 | 10089.2721 | 1.424% | 0.2287%
2017-06-02 | 16 | 10258 | 143.6929 | 1.401% | 23.0797 | 0.225% | 166.7726 | 1.626% | 1714 | 10234.9203 | 10091.2274 | 1.424% | 0.2287%
2017-07-27 | 22 | 10259 | 143.7123 | 1.401% | 23.0827 | 0.225% | 166.795 | 1.626% | 1715 | 10235.9173 | 10092.205 | 1.424% | 0.2287%
2017-06-01 | 18 | 10262 | 143.7706 | 1.401% | 23.0915 | 0.225% | 166.862 | 1.626% | 1716 | 10238.9085 | 10095.138 | 1.424% | 0.2287%
2017-06-11 | 16 | 10263 | 143.79 | 1.401% | 23.0944 | 0.225% | 166.8844 | 1.626% | 1717 | 10239.9056 | 10096.1156 | 1.424% | 0.2287%
2017-06-21 | 18 | 10268 | 143.8871 | 1.401% | 23.1091 | 0.2251% | 166.9962 | 1.626% | 1718 | 10244.8909 | 10101.0038 | 1.424% | 0.2288%
2017-07-16 | 15 | 10280 | 144.1201 | 1.402% | 23.1444 | 0.2251% | 167.2644 | 1.627% | 1719 | 10256.8556 | 10112.7356 | 1.425% | 0.2289%
2017-08-04 | 14 | 10283 | 144.1783 | 1.402% | 23.1532 | 0.2252% | 167.3315 | 1.627% | 1720 | 10259.8468 | 10115.6685 | 1.425% | 0.2289%
2017-08-04 | 20 | 10285 | 144.2171 | 1.402% | 23.1591 | 0.2252% | 167.3762 | 1.627% | 1721 | 10261.8409 | 10117.6238 | 1.425% | 0.2289%
2017-08-06 | 15 | 10288 | 144.2754 | 1.402% | 23.1679 | 0.2252% | 167.4433 | 1.628% | 1722 | 10264.8321 | 10120.5567 | 1.426% | 0.2289%
2017-08-31 | 17 | 10291 | 144.3336 | 1.403% | 23.1767 | 0.2252% | 167.5103 | 1.628% | 1723 | 10267.8233 | 10123.4897 | 1.426% | 0.2289%
2017-08-12 | 14 | 10295 | 144.4113 | 1.403% | 23.1884 | 0.2252% | 167.5998 | 1.628% | 1724 | 10271.8116 | 10127.4002 | 1.426% | 0.229%
2017-06-02 | 18 | 10297 | 144.4501 | 1.403% | 23.1943 | 0.2253% | 167.6445 | 1.628% | 1725 | 10273.8057 | 10129.3555 | 1.426% | 0.229%
2017-08-24 | 16 | 10297 | 144.4501 | 1.403% | 23.1943 | 0.2253% | 167.6445 | 1.628% | 1726 | 10273.8057 | 10129.3555 | 1.426% | 0.229%
2017-06-29 | 15 | 10299 | 144.489 | 1.403% | 23.2002 | 0.2253% | 167.6892 | 1.628% | 1727 | 10275.7998 | 10131.3108 | 1.426% | 0.229%
2017-06-26 | 17 | 10302 | 144.5472 | 1.403% | 23.209 | 0.2253% | 167.7562 | 1.628% | 1728 | 10278.791 | 10134.2438 | 1.426% | 0.229%
2017-08-10 | 18 | 10302 | 144.5472 | 1.403% | 23.209 | 0.2253% | 167.7562 | 1.628% | 1729 | 10278.791 | 10134.2438 | 1.426% | 0.229%
2017-06-02 | 17 | 10305 | 144.6055 | 1.403% | 23.2178 | 0.2253% | 167.8233 | 1.629% | 1730 | 10281.7822 | 10137.1767 | 1.426% | 0.229%
2017-07-16 | 16 | 10308 | 144.6637 | 1.403% | 23.2266 | 0.2253% | 167.8904 | 1.629% | 1731 | 10284.7734 | 10140.1096 | 1.427% | 0.2291%
2017-08-24 | 17 | 10308 | 144.6637 | 1.403% | 23.2266 | 0.2253% | 167.8904 | 1.629% | 1732 | 10284.7734 | 10140.1096 | 1.427% | 0.2291%
2017-06-12 | 20 | 10316 | 144.8191 | 1.404% | 23.2502 | 0.2254% | 168.0692 | 1.629% | 1733 | 10292.7498 | 10147.9308 | 1.427% | 0.2291%
2017-07-01 | 16 | 10324 | 144.9744 | 1.404% | 23.2737 | 0.2254% | 168.2481 | 1.63% | 1734 | 10300.7263 | 10155.7519 | 1.428% | 0.2292%
2017-07-07 | 11 | 10328 | 145.0521 | 1.404% | 23.2854 | 0.2255% | 168.3375 | 1.63% | 1735 | 10304.7146 | 10159.6625 | 1.428% | 0.2292%
2017-07-22 | 23 | 10329 | 145.0715 | 1.405% | 23.2884 | 0.2255% | 168.3598 | 1.63% | 1736 | 10305.7116 | 10160.6402 | 1.428% | 0.2292%
2017-07-02 | 21 | 10330 | 145.0909 | 1.405% | 23.2913 | 0.2255% | 168.3822 | 1.63% | 1737 | 10306.7087 | 10161.6178 | 1.428% | 0.2292%
2017-06-14 | 21 | 10336 | 145.2074 | 1.405% | 23.3089 | 0.2255% | 168.5163 | 1.63% | 1738 | 10312.6911 | 10167.4837 | 1.428% | 0.2292%
2017-06-15 | 20 | 10337 | 145.2268 | 1.405% | 23.3119 | 0.2255% | 168.5387 | 1.63% | 1739 | 10313.6881 | 10168.4613 | 1.428% | 0.2293%
2017-07-27 | 12 | 10341 | 145.3045 | 1.405% | 23.3236 | 0.2255% | 168.6281 | 1.631% | 1740 | 10317.6764 | 10172.3719 | 1.428% | 0.2293%
2017-07-31 | 17 | 10341 | 145.3045 | 1.405% | 23.3236 | 0.2255% | 168.6281 | 1.631% | 1741 | 10317.6764 | 10172.3719 | 1.428% | 0.2293%
2017-06-26 | 18 | 10352 | 145.5181 | 1.406% | 23.3559 | 0.2256% | 168.874 | 1.631% | 1742 | 10328.6441 | 10183.126 | 1.429% | 0.2294%
2017-08-23 | 11 | 10353 | 145.5375 | 1.406% | 23.3589 | 0.2256% | 168.8964 | 1.631% | 1743 | 10329.6411 | 10184.1036 | 1.429% | 0.2294%
2017-06-23 | 13 | 10358 | 145.6346 | 1.406% | 23.3736 | 0.2257% | 169.0082 | 1.632% | 1744 | 10334.6264 | 10188.9918 | 1.429% | 0.2294%
2017-08-10 | 17 | 10362 | 145.7122 | 1.406% | 23.3853 | 0.2257% | 169.0976 | 1.632% | 1745 | 10338.6147 | 10192.9024 | 1.43% | 0.2294%
2017-07-07 | 22 | 10366 | 145.7899 | 1.406% | 23.3971 | 0.2257% | 169.187 | 1.632% | 1746 | 10342.6029 | 10196.813 | 1.43% | 0.2295%
2017-08-18 | 23 | 10366 | 145.7899 | 1.406% | 23.3971 | 0.2257% | 169.187 | 1.632% | 1747 | 10342.6029 | 10196.813 | 1.43% | 0.2295%
2017-06-16 | 13 | 10376 | 145.9841 | 1.407% | 23.4265 | 0.2258% | 169.4105 | 1.633% | 1748 | 10352.5735 | 10206.5895 | 1.43% | 0.2295%
2017-07-11 | 12 | 10391 | 146.2753 | 1.408% | 23.4705 | 0.2259% | 169.7459 | 1.634% | 1749 | 10367.5295 | 10221.2541 | 1.431% | 0.2296%
2017-07-04 | 14 | 10398 | 146.4113 | 1.408% | 23.4911 | 0.2259% | 169.9024 | 1.634% | 1750 | 10374.5089 | 10228.0976 | 1.431% | 0.2297%
2017-07-26 | 13 | 10407 | 146.586 | 1.409% | 23.5176 | 0.226% | 170.1036 | 1.635% | 1751 | 10383.4824 | 10236.8964 | 1.432% | 0.2297%
2017-08-17 | 21 | 10408 | 146.6054 | 1.409% | 23.5205 | 0.226% | 170.1259 | 1.635% | 1752 | 10384.4795 | 10237.8741 | 1.432% | 0.2297%
2017-08-25 | 18 | 10413 | 146.7025 | 1.409% | 23.5352 | 0.226% | 170.2377 | 1.635% | 1753 | 10389.4648 | 10242.7623 | 1.432% | 0.2298%
2017-08-03 | 19 | 10415 | 146.7413 | 1.409% | 23.5411 | 0.226% | 170.2824 | 1.635% | 1754 | 10391.4589 | 10244.7176 | 1.432% | 0.2298%
2017-07-09 | 15 | 10421 | 146.8578 | 1.409% | 23.5587 | 0.2261% | 170.4165 | 1.635% | 1755 | 10397.4413 | 10250.5835 | 1.433% | 0.2298%
2017-07-21 | 11 | 10422 | 146.8773 | 1.409% | 23.5616 | 0.2261% | 170.4389 | 1.635% | 1756 | 10398.4384 | 10251.5611 | 1.433% | 0.2298%
2017-06-11 | 18 | 10430 | 147.0326 | 1.41% | 23.5852 | 0.2261% | 170.6177 | 1.636% | 1757 | 10406.4148 | 10259.3823 | 1.433% | 0.2299%
2017-06-11 | 17 | 10431 | 147.052 | 1.41% | 23.5881 | 0.2261% | 170.6401 | 1.636% | 1758 | 10407.4119 | 10260.3599 | 1.433% | 0.2299%
2017-07-31 | 18 | 10434 | 147.1103 | 1.41% | 23.5969 | 0.2262% | 170.7072 | 1.636% | 1759 | 10410.4031 | 10263.2928 | 1.433% | 0.2299%
2017-07-10 | 13 | 10436 | 147.1491 | 1.41% | 23.6028 | 0.2262% | 170.7519 | 1.636% | 1760 | 10412.3972 | 10265.2481 | 1.433% | 0.2299%
2017-07-14 | 23 | 10440 | 147.2268 | 1.41% | 23.6145 | 0.2262% | 170.8413 | 1.636% | 1761 | 10416.3855 | 10269.1587 | 1.434% | 0.23%
2017-07-28 | 20 | 10456 | 147.5374 | 1.411% | 23.6616 | 0.2263% | 171.199 | 1.637% | 1762 | 10432.3384 | 10284.801 | 1.435% | 0.2301%
2017-08-15 | 22 | 10458 | 147.5763 | 1.411% | 23.6674 | 0.2263% | 171.2437 | 1.637% | 1763 | 10434.3326 | 10286.7563 | 1.435% | 0.2301%
2017-06-13 | 14 | 10461 | 147.6345 | 1.411% | 23.6763 | 0.2263% | 171.3108 | 1.638% | 1764 | 10437.3237 | 10289.6892 | 1.435% | 0.2301%
2017-08-01 | 19 | 10462 | 147.6539 | 1.411% | 23.6792 | 0.2263% | 171.3331 | 1.638% | 1765 | 10438.3208 | 10290.6669 | 1.435% | 0.2301%
2017-08-05 | 15 | 10470 | 147.8093 | 1.412% | 23.7027 | 0.2264% | 171.512 | 1.638% | 1766 | 10446.2973 | 10298.488 | 1.435% | 0.2302%
2017-07-26 | 21 | 10473 | 147.8675 | 1.412% | 23.7115 | 0.2264% | 171.579 | 1.638% | 1767 | 10449.2885 | 10301.421 | 1.435% | 0.2302%
2017-07-06 | 12 | 10475 | 147.9064 | 1.412% | 23.7174 | 0.2264% | 171.6237 | 1.638% | 1768 | 10451.2826 | 10303.3763 | 1.436% | 0.2302%
2017-06-18 | 19 | 10476 | 147.9258 | 1.412% | 23.7203 | 0.2264% | 171.6461 | 1.638% | 1769 | 10452.2797 | 10304.3539 | 1.436% | 0.2302%
2017-08-03 | 14 | 10476 | 147.9258 | 1.412% | 23.7203 | 0.2264% | 171.6461 | 1.638% | 1770 | 10452.2797 | 10304.3539 | 1.436% | 0.2302%
2017-08-11 | 19 | 10477 | 147.9452 | 1.412% | 23.7233 | 0.2264% | 171.6685 | 1.639% | 1771 | 10453.2767 | 10305.3315 | 1.436% | 0.2302%
2017-07-23 | 20 | 10482 | 148.0423 | 1.412% | 23.738 | 0.2265% | 171.7802 | 1.639% | 1772 | 10458.262 | 10310.2198 | 1.436% | 0.2302%
2017-07-28 | 12 | 10483 | 148.0617 | 1.412% | 23.7409 | 0.2265% | 171.8026 | 1.639% | 1773 | 10459.2591 | 10311.1974 | 1.436% | 0.2302%
2017-06-01 | 17 | 10485 | 148.1005 | 1.412% | 23.7468 | 0.2265% | 171.8473 | 1.639% | 1774 | 10461.2532 | 10313.1527 | 1.436% | 0.2303%
2017-08-12 | 15 | 10485 | 148.1005 | 1.412% | 23.7468 | 0.2265% | 171.8473 | 1.639% | 1775 | 10461.2532 | 10313.1527 | 1.436% | 0.2303%
2017-08-17 | 11 | 10496 | 148.3141 | 1.413% | 23.7791 | 0.2266% | 172.0932 | 1.64% | 1776 | 10472.2209 | 10323.9068 | 1.437% | 0.2303%
2017-08-19 | 20 | 10498 | 148.3529 | 1.413% | 23.785 | 0.2266% | 172.1379 | 1.64% | 1777 | 10474.215 | 10325.8621 | 1.437% | 0.2303%
2017-08-19 | 12 | 10499 | 148.3724 | 1.413% | 23.7879 | 0.2266% | 172.1603 | 1.64% | 1778 | 10475.2121 | 10326.8397 | 1.437% | 0.2304%
2017-06-18 | 15 | 10500 | 148.3918 | 1.413% | 23.7909 | 0.2266% | 172.1826 | 1.64% | 1779 | 10476.2091 | 10327.8174 | 1.437% | 0.2304%
2017-07-01 | 19 | 10507 | 148.5277 | 1.414% | 23.8114 | 0.2266% | 172.3391 | 1.64% | 1780 | 10483.1886 | 10334.6609 | 1.437% | 0.2304%
2017-07-25 | 22 | 10511 | 148.6054 | 1.414% | 23.8232 | 0.2267% | 172.4285 | 1.64% | 1781 | 10487.1768 | 10338.5715 | 1.437% | 0.2304%
2017-08-11 | 14 | 10517 | 148.7219 | 1.414% | 23.8408 | 0.2267% | 172.5627 | 1.641% | 1782 | 10493.1592 | 10344.4373 | 1.438% | 0.2305%
2017-08-25 | 15 | 10521 | 148.7995 | 1.414% | 23.8526 | 0.2267% | 172.6521 | 1.641% | 1783 | 10497.1474 | 10348.3479 | 1.438% | 0.2305%
2017-07-19 | 13 | 10525 | 148.8772 | 1.415% | 23.8643 | 0.2267% | 172.7415 | 1.641% | 1784 | 10501.1357 | 10352.2585 | 1.438% | 0.2305%
2017-08-20 | 13 | 10528 | 148.9354 | 1.415% | 23.8731 | 0.2268% | 172.8086 | 1.641% | 1785 | 10504.1269 | 10355.1914 | 1.438% | 0.2305%
2017-07-17 | 15 | 10532 | 149.0131 | 1.415% | 23.8849 | 0.2268% | 172.898 | 1.642% | 1786 | 10508.1151 | 10359.102 | 1.438% | 0.2306%
2017-07-09 | 19 | 10533 | 149.0325 | 1.415% | 23.8878 | 0.2268% | 172.9204 | 1.642% | 1787 | 10509.1122 | 10360.0796 | 1.439% | 0.2306%
2017-08-16 | 22 | 10539 | 149.149 | 1.415% | 23.9055 | 0.2268% | 173.0545 | 1.642% | 1788 | 10515.0945 | 10365.9455 | 1.439% | 0.2306%
2017-06-19 | 19 | 10541 | 149.1879 | 1.415% | 23.9113 | 0.2268% | 173.0992 | 1.642% | 1789 | 10517.0887 | 10367.9008 | 1.439% | 0.2306%
2017-06-15 | 13 | 10548 | 149.3238 | 1.416% | 23.9319 | 0.2269% | 173.2557 | 1.643% | 1790 | 10524.0681 | 10374.7443 | 1.439% | 0.2307%
2017-08-16 | 12 | 10550 | 149.3626 | 1.416% | 23.9378 | 0.2269% | 173.3004 | 1.643% | 1791 | 10526.0622 | 10376.6996 | 1.439% | 0.2307%
2017-08-17 | 20 | 10550 | 149.3626 | 1.416% | 23.9378 | 0.2269% | 173.3004 | 1.643% | 1792 | 10526.0622 | 10376.6996 | 1.439% | 0.2307%
2017-07-17 | 19 | 10555 | 149.4597 | 1.416% | 23.9525 | 0.2269% | 173.4122 | 1.643% | 1793 | 10531.0475 | 10381.5878 | 1.44% | 0.2307%
2017-06-23 | 21 | 10557 | 149.4985 | 1.416% | 23.9584 | 0.2269% | 173.4569 | 1.643% | 1794 | 10533.0416 | 10383.5431 | 1.44% | 0.2307%
2017-06-14 | 13 | 10558 | 149.518 | 1.416% | 23.9613 | 0.2269% | 173.4793 | 1.643% | 1795 | 10534.0387 | 10384.5207 | 1.44% | 0.2307%
2017-07-12 | 11 | 10560 | 149.5568 | 1.416% | 23.9672 | 0.227% | 173.524 | 1.643% | 1796 | 10536.0328 | 10386.476 | 1.44% | 0.2308%
2017-06-12 | 14 | 10563 | 149.615 | 1.416% | 23.976 | 0.227% | 173.591 | 1.643% | 1797 | 10539.024 | 10389.409 | 1.44% | 0.2308%
2017-08-01 | 16 | 10565 | 149.6539 | 1.417% | 23.9819 | 0.227% | 173.6357 | 1.643% | 1798 | 10541.0181 | 10391.3643 | 1.44% | 0.2308%
2017-08-23 | 21 | 10573 | 149.8092 | 1.417% | 24.0054 | 0.227% | 173.8146 | 1.644% | 1799 | 10548.9946 | 10399.1854 | 1.441% | 0.2308%
2017-07-09 | 16 | 10577 | 149.8869 | 1.417% | 24.0171 | 0.2271% | 173.904 | 1.644% | 1800 | 10552.9829 | 10403.096 | 1.441% | 0.2309%
2017-07-18 | 19 | 10579 | 149.9257 | 1.417% | 24.023 | 0.2271% | 173.9487 | 1.644% | 1801 | 10554.977 | 10405.0513 | 1.441% | 0.2309%
2017-08-18 | 11 | 10580 | 149.9451 | 1.417% | 24.0259 | 0.2271% | 173.9711 | 1.644% | 1802 | 10555.9741 | 10406.0289 | 1.441% | 0.2309%
2017-06-19 | 12 | 10589 | 150.1199 | 1.418% | 24.0524 | 0.2271% | 174.1723 | 1.645% | 1803 | 10564.9476 | 10414.8277 | 1.441% | 0.2309%
2017-06-29 | 19 | 10591 | 150.1587 | 1.418% | 24.0583 | 0.2272% | 174.217 | 1.645% | 1804 | 10566.9417 | 10416.783 | 1.442% | 0.231%
2017-08-07 | 19 | 10592 | 150.1781 | 1.418% | 24.0612 | 0.2272% | 174.2393 | 1.645% | 1805 | 10567.9388 | 10417.7607 | 1.442% | 0.231%
2017-08-21 | 12 | 10594 | 150.217 | 1.418% | 24.0671 | 0.2272% | 174.284 | 1.645% | 1806 | 10569.9329 | 10419.716 | 1.442% | 0.231%
2017-08-04 | 15 | 10597 | 150.2752 | 1.418% | 24.0759 | 0.2272% | 174.3511 | 1.645% | 1807 | 10572.9241 | 10422.6489 | 1.442% | 0.231%
2017-07-08 | 12 | 10601 | 150.3529 | 1.418% | 24.0877 | 0.2272% | 174.4405 | 1.646% | 1808 | 10576.9123 | 10426.5595 | 1.442% | 0.231%
2017-07-10 | 18 | 10603 | 150.3917 | 1.418% | 24.0935 | 0.2272% | 174.4852 | 1.646% | 1809 | 10578.9065 | 10428.5148 | 1.442% | 0.231%
2017-07-01 | 17 | 10607 | 150.4694 | 1.419% | 24.1053 | 0.2273% | 174.5747 | 1.646% | 1810 | 10582.8947 | 10432.4253 | 1.442% | 0.2311%
2017-07-24 | 22 | 10610 | 150.5276 | 1.419% | 24.1141 | 0.2273% | 174.6417 | 1.646% | 1811 | 10585.8859 | 10435.3583 | 1.442% | 0.2311%
2017-08-07 | 14 | 10610 | 150.5276 | 1.419% | 24.1141 | 0.2273% | 174.6417 | 1.646% | 1812 | 10585.8859 | 10435.3583 | 1.442% | 0.2311%
2017-06-29 | 16 | 10612 | 150.5665 | 1.419% | 24.12 | 0.2273% | 174.6864 | 1.646% | 1813 | 10587.88 | 10437.3136 | 1.443% | 0.2311%
2017-07-11 | 22 | 10614 | 150.6053 | 1.419% | 24.1259 | 0.2273% | 174.7312 | 1.646% | 1814 | 10589.8741 | 10439.2688 | 1.443% | 0.2311%
2017-07-24 | 13 | 10617 | 150.6636 | 1.419% | 24.1347 | 0.2273% | 174.7982 | 1.646% | 1815 | 10592.8653 | 10442.2018 | 1.443% | 0.2311%
2017-07-19 | 21 | 10621 | 150.7412 | 1.419% | 24.1464 | 0.2273% | 174.8876 | 1.647% | 1816 | 10596.8536 | 10446.1124 | 1.443% | 0.2312%
2017-08-06 | 16 | 10622 | 150.7606 | 1.419% | 24.1494 | 0.2274% | 174.91 | 1.647% | 1817 | 10597.8506 | 10447.09 | 1.443% | 0.2312%
2017-08-12 | 19 | 10627 | 150.8577 | 1.42% | 24.1641 | 0.2274% | 175.0218 | 1.647% | 1818 | 10602.8359 | 10451.9782 | 1.443% | 0.2312%
2017-06-24 | 13 | 10636 | 151.0325 | 1.42% | 24.1905 | 0.2274% | 175.223 | 1.647% | 1819 | 10611.8095 | 10460.777 | 1.444% | 0.2312%
2017-06-24 | 18 | 10642 | 151.149 | 1.42% | 24.2081 | 0.2275% | 175.3571 | 1.648% | 1820 | 10617.7919 | 10466.6429 | 1.444% | 0.2313%
2017-07-21 | 22 | 10642 | 151.149 | 1.42% | 24.2081 | 0.2275% | 175.3571 | 1.648% | 1821 | 10617.7919 | 10466.6429 | 1.444% | 0.2313%
2017-06-01 | 16 | 10643 | 151.1684 | 1.42% | 24.2111 | 0.2275% | 175.3795 | 1.648% | 1822 | 10618.7889 | 10467.6205 | 1.444% | 0.2313%
2017-07-02 | 14 | 10647 | 151.2461 | 1.421% | 24.2228 | 0.2275% | 175.4689 | 1.648% | 1823 | 10622.7772 | 10471.5311 | 1.444% | 0.2313%
2017-08-22 | 22 | 10647 | 151.2461 | 1.421% | 24.2228 | 0.2275% | 175.4689 | 1.648% | 1824 | 10622.7772 | 10471.5311 | 1.444% | 0.2313%
2017-08-25 | 17 | 10650 | 151.3043 | 1.421% | 24.2316 | 0.2275% | 175.536 | 1.648% | 1825 | 10625.7684 | 10474.464 | 1.445% | 0.2313%
2017-07-05 | 21 | 10652 | 151.3431 | 1.421% | 24.2375 | 0.2275% | 175.5807 | 1.648% | 1826 | 10627.7625 | 10476.4193 | 1.445% | 0.2314%
2017-08-05 | 19 | 10652 | 151.3431 | 1.421% | 24.2375 | 0.2275% | 175.5807 | 1.648% | 1827 | 10627.7625 | 10476.4193 | 1.445% | 0.2314%
2017-07-15 | 20 | 10657 | 151.4402 | 1.421% | 24.2522 | 0.2276% | 175.6924 | 1.649% | 1828 | 10632.7478 | 10481.3076 | 1.445% | 0.2314%
2017-08-22 | 12 | 10663 | 151.5567 | 1.421% | 24.2699 | 0.2276% | 175.8266 | 1.649% | 1829 | 10638.7301 | 10487.1734 | 1.445% | 0.2314%
2017-08-25 | 16 | 10666 | 151.615 | 1.421% | 24.2787 | 0.2276% | 175.8936 | 1.649% | 1830 | 10641.7213 | 10490.1064 | 1.445% | 0.2314%
2017-08-06 | 19 | 10668 | 151.6538 | 1.422% | 24.2845 | 0.2276% | 175.9384 | 1.649% | 1831 | 10643.7155 | 10492.0616 | 1.445% | 0.2315%
2017-08-01 | 18 | 10671 | 151.7121 | 1.422% | 24.2934 | 0.2277% | 176.0054 | 1.649% | 1832 | 10646.7066 | 10494.9946 | 1.446% | 0.2315%
2017-08-02 | 19 | 10674 | 151.7703 | 1.422% | 24.3022 | 0.2277% | 176.0725 | 1.65% | 1833 | 10649.6978 | 10497.9275 | 1.446% | 0.2315%
2017-07-18 | 15 | 10680 | 151.8868 | 1.422% | 24.3198 | 0.2277% | 176.2066 | 1.65% | 1834 | 10655.6802 | 10503.7934 | 1.446% | 0.2315%
2017-08-02 | 15 | 10688 | 152.0421 | 1.423% | 24.3433 | 0.2278% | 176.3855 | 1.65% | 1835 | 10663.6567 | 10511.6145 | 1.446% | 0.2316%
2017-06-16 | 19 | 10689 | 152.0616 | 1.423% | 24.3463 | 0.2278% | 176.4078 | 1.65% | 1836 | 10664.6537 | 10512.5922 | 1.446% | 0.2316%
2017-07-03 | 13 | 10709 | 152.4499 | 1.424% | 24.405 | 0.2279% | 176.8549 | 1.651% | 1837 | 10684.595 | 10532.1451 | 1.447% | 0.2317%
2017-07-01 | 18 | 10711 | 152.4887 | 1.424% | 24.4109 | 0.2279% | 176.8996 | 1.652% | 1838 | 10686.5891 | 10534.1004 | 1.448% | 0.2317%
2017-07-03 | 18 | 10719 | 152.6441 | 1.424% | 24.4344 | 0.228% | 177.0785 | 1.652% | 1839 | 10694.5656 | 10541.9215 | 1.448% | 0.2318%
2017-08-20 | 21 | 10720 | 152.6635 | 1.424% | 24.4374 | 0.228% | 177.1008 | 1.652% | 1840 | 10695.5626 | 10542.8992 | 1.448% | 0.2318%
2017-07-27 | 21 | 10730 | 152.8577 | 1.425% | 24.4667 | 0.228% | 177.3244 | 1.653% | 1841 | 10705.5333 | 10552.6756 | 1.449% | 0.2319%
2017-08-12 | 16 | 10732 | 152.8965 | 1.425% | 24.4726 | 0.228% | 177.3691 | 1.653% | 1842 | 10707.5274 | 10554.6309 | 1.449% | 0.2319%
2017-06-18 | 16 | 10736 | 152.9742 | 1.425% | 24.4844 | 0.2281% | 177.4585 | 1.653% | 1843 | 10711.5156 | 10558.5415 | 1.449% | 0.2319%
2017-06-29 | 18 | 10739 | 153.0324 | 1.425% | 24.4932 | 0.2281% | 177.5256 | 1.653% | 1844 | 10714.5068 | 10561.4744 | 1.449% | 0.2319%
2017-08-03 | 18 | 10740 | 153.0518 | 1.425% | 24.4961 | 0.2281% | 177.548 | 1.653% | 1845 | 10715.5039 | 10562.452 | 1.449% | 0.2319%
2017-07-04 | 15 | 10742 | 153.0907 | 1.425% | 24.502 | 0.2281% | 177.5927 | 1.653% | 1846 | 10717.498 | 10564.4073 | 1.449% | 0.2319%
2017-07-17 | 16 | 10747 | 153.1877 | 1.425% | 24.5167 | 0.2281% | 177.7044 | 1.654% | 1847 | 10722.4833 | 10569.2956 | 1.449% | 0.232%
2017-08-15 | 12 | 10747 | 153.1877 | 1.425% | 24.5167 | 0.2281% | 177.7044 | 1.654% | 1848 | 10722.4833 | 10569.2956 | 1.449% | 0.232%
2017-07-17 | 18 | 10748 | 153.2072 | 1.425% | 24.5196 | 0.2281% | 177.7268 | 1.654% | 1849 | 10723.4804 | 10570.2732 | 1.449% | 0.232%
2017-07-08 | 20 | 10756 | 153.3625 | 1.426% | 24.5431 | 0.2282% | 177.9056 | 1.654% | 1850 | 10731.4569 | 10578.0944 | 1.45% | 0.232%
2017-07-09 | 17 | 10759 | 153.4207 | 1.426% | 24.552 | 0.2282% | 177.9727 | 1.654% | 1851 | 10734.448 | 10581.0273 | 1.45% | 0.232%
2017-08-05 | 16 | 10760 | 153.4402 | 1.426% | 24.5549 | 0.2282% | 177.9951 | 1.654% | 1852 | 10735.4451 | 10582.0049 | 1.45% | 0.232%
2017-06-19 | 18 | 10762 | 153.479 | 1.426% | 24.5608 | 0.2282% | 178.0398 | 1.654% | 1853 | 10737.4392 | 10583.9602 | 1.45% | 0.2321%
2017-06-18 | 18 | 10763 | 153.4984 | 1.426% | 24.5637 | 0.2282% | 178.0621 | 1.654% | 1854 | 10738.4363 | 10584.9379 | 1.45% | 0.2321%
2017-07-13 | 11 | 10765 | 153.5373 | 1.426% | 24.5696 | 0.2282% | 178.1068 | 1.654% | 1855 | 10740.4304 | 10586.8932 | 1.45% | 0.2321%
2017-07-04 | 19 | 10770 | 153.6343 | 1.427% | 24.5843 | 0.2283% | 178.2186 | 1.655% | 1856 | 10745.4157 | 10591.7814 | 1.451% | 0.2321%
2017-07-06 | 22 | 10772 | 153.6732 | 1.427% | 24.5902 | 0.2283% | 178.2633 | 1.655% | 1857 | 10747.4098 | 10593.7367 | 1.451% | 0.2321%
2017-08-04 | 19 | 10774 | 153.712 | 1.427% | 24.596 | 0.2283% | 178.308 | 1.655% | 1858 | 10749.404 | 10595.692 | 1.451% | 0.2321%
2017-06-29 | 17 | 10775 | 153.7314 | 1.427% | 24.599 | 0.2283% | 178.3304 | 1.655% | 1859 | 10750.401 | 10596.6696 | 1.451% | 0.2321%
2017-07-09 | 18 | 10775 | 153.7314 | 1.427% | 24.599 | 0.2283% | 178.3304 | 1.655% | 1860 | 10750.401 | 10596.6696 | 1.451% | 0.2321%
2017-08-01 | 17 | 10778 | 153.7897 | 1.427% | 24.6078 | 0.2283% | 178.3975 | 1.655% | 1861 | 10753.3922 | 10599.6025 | 1.451% | 0.2322%
2017-08-11 | 15 | 10784 | 153.9062 | 1.427% | 24.6254 | 0.2284% | 178.5316 | 1.656% | 1862 | 10759.3746 | 10605.4684 | 1.451% | 0.2322%
2017-06-13 | 19 | 10786 | 153.945 | 1.427% | 24.6313 | 0.2284% | 178.5763 | 1.656% | 1863 | 10761.3687 | 10607.4237 | 1.451% | 0.2322%
2017-08-14 | 21 | 10788 | 153.9838 | 1.427% | 24.6372 | 0.2284% | 178.621 | 1.656% | 1864 | 10763.3628 | 10609.379 | 1.451% | 0.2322%
2017-07-07 | 21 | 10789 | 154.0033 | 1.427% | 24.6401 | 0.2284% | 178.6434 | 1.656% | 1865 | 10764.3599 | 10610.3566 | 1.451% | 0.2322%
2017-06-12 | 19 | 10791 | 154.0421 | 1.428% | 24.646 | 0.2284% | 178.6881 | 1.656% | 1866 | 10766.354 | 10612.3119 | 1.452% | 0.2322%
2017-06-13 | 15 | 10804 | 154.2945 | 1.428% | 24.6842 | 0.2285% | 178.9787 | 1.657% | 1867 | 10779.3158 | 10625.0213 | 1.452% | 0.2323%
2017-08-11 | 18 | 10804 | 154.2945 | 1.428% | 24.6842 | 0.2285% | 178.9787 | 1.657% | 1868 | 10779.3158 | 10625.0213 | 1.452% | 0.2323%
2017-08-06 | 17 | 10806 | 154.3333 | 1.428% | 24.6901 | 0.2285% | 179.0234 | 1.657% | 1869 | 10781.3099 | 10626.9766 | 1.452% | 0.2323%
2017-08-14 | 14 | 10807 | 154.3528 | 1.428% | 24.693 | 0.2285% | 179.0458 | 1.657% | 1870 | 10782.307 | 10627.9542 | 1.452% | 0.2323%
2017-07-05 | 13 | 10813 | 154.4693 | 1.429% | 24.7106 | 0.2285% | 179.1799 | 1.657% | 1871 | 10788.2894 | 10633.8201 | 1.453% | 0.2324%
2017-07-17 | 17 | 10821 | 154.6246 | 1.429% | 24.7342 | 0.2286% | 179.3587 | 1.658% | 1872 | 10796.2658 | 10641.6413 | 1.453% | 0.2324%
2017-08-12 | 18 | 10822 | 154.644 | 1.429% | 24.7371 | 0.2286% | 179.3811 | 1.658% | 1873 | 10797.2629 | 10642.6189 | 1.453% | 0.2324%
2017-06-15 | 19 | 10826 | 154.7217 | 1.429% | 24.7488 | 0.2286% | 179.4705 | 1.658% | 1874 | 10801.2512 | 10646.5295 | 1.453% | 0.2325%
2017-08-12 | 17 | 10847 | 155.1294 | 1.43% | 24.8106 | 0.2287% | 179.94 | 1.659% | 1875 | 10822.1894 | 10667.06 | 1.454% | 0.2326%
2017-07-18 | 18 | 10853 | 155.2459 | 1.43% | 24.8282 | 0.2288% | 180.0741 | 1.659% | 1876 | 10828.1718 | 10672.9259 | 1.455% | 0.2326%
2017-06-16 | 14 | 10861 | 155.4013 | 1.431% | 24.8517 | 0.2288% | 180.253 | 1.66% | 1877 | 10836.1483 | 10680.747 | 1.455% | 0.2327%
2017-08-07 | 15 | 10863 | 155.4401 | 1.431% | 24.8576 | 0.2288% | 180.2977 | 1.66% | 1878 | 10838.1424 | 10682.7023 | 1.455% | 0.2327%
2017-08-21 | 21 | 10867 | 155.5178 | 1.431% | 24.8693 | 0.2289% | 180.3871 | 1.66% | 1879 | 10842.1307 | 10686.6129 | 1.455% | 0.2327%
2017-06-23 | 14 | 10868 | 155.5372 | 1.431% | 24.8723 | 0.2289% | 180.4095 | 1.66% | 1880 | 10843.1277 | 10687.5905 | 1.455% | 0.2327%
2017-07-10 | 14 | 10873 | 155.6343 | 1.431% | 24.887 | 0.2289% | 180.5212 | 1.66% | 1881 | 10848.113 | 10692.4788 | 1.456% | 0.2328%
2017-07-25 | 12 | 10873 | 155.6343 | 1.431% | 24.887 | 0.2289% | 180.5212 | 1.66% | 1882 | 10848.113 | 10692.4788 | 1.456% | 0.2328%
2017-08-17 | 19 | 10881 | 155.7896 | 1.432% | 24.9105 | 0.2289% | 180.7001 | 1.661% | 1883 | 10856.0895 | 10700.2999 | 1.456% | 0.2328%
2017-07-14 | 11 | 10883 | 155.8284 | 1.432% | 24.9163 | 0.2289% | 180.7448 | 1.661% | 1884 | 10858.0837 | 10702.2552 | 1.456% | 0.2328%
2017-07-20 | 22 | 10885 | 155.8673 | 1.432% | 24.9222 | 0.229% | 180.7895 | 1.661% | 1885 | 10860.0778 | 10704.2105 | 1.456% | 0.2328%
2017-07-02 | 20 | 10891 | 155.9838 | 1.432% | 24.9399 | 0.229% | 180.9236 | 1.661% | 1886 | 10866.0601 | 10710.0764 | 1.456% | 0.2329%
2017-08-06 | 18 | 10891 | 155.9838 | 1.432% | 24.9399 | 0.229% | 180.9236 | 1.661% | 1887 | 10866.0601 | 10710.0764 | 1.456% | 0.2329%
2017-08-23 | 20 | 10891 | 155.9838 | 1.432% | 24.9399 | 0.229% | 180.9236 | 1.661% | 1888 | 10866.0601 | 10710.0764 | 1.456% | 0.2329%
2017-07-15 | 12 | 10895 | 156.0614 | 1.432% | 24.9516 | 0.229% | 181.0131 | 1.661% | 1889 | 10870.0484 | 10713.9869 | 1.457% | 0.2329%
2017-06-12 | 15 | 10901 | 156.1779 | 1.433% | 24.9692 | 0.2291% | 181.1472 | 1.662% | 1890 | 10876.0308 | 10719.8528 | 1.457% | 0.2329%
2017-06-18 | 17 | 10903 | 156.2168 | 1.433% | 24.9751 | 0.2291% | 181.1919 | 1.662% | 1891 | 10878.0249 | 10721.8081 | 1.457% | 0.2329%
2017-07-10 | 17 | 10903 | 156.2168 | 1.433% | 24.9751 | 0.2291% | 181.1919 | 1.662% | 1892 | 10878.0249 | 10721.8081 | 1.457% | 0.2329%
2017-07-26 | 14 | 10915 | 156.4498 | 1.433% | 25.0104 | 0.2291% | 181.4602 | 1.662% | 1893 | 10889.9896 | 10733.5398 | 1.458% | 0.233%
2017-08-04 | 16 | 10916 | 156.4692 | 1.433% | 25.0133 | 0.2291% | 181.4825 | 1.663% | 1894 | 10890.9867 | 10734.5175 | 1.458% | 0.233%
2017-07-22 | 12 | 10919 | 156.5275 | 1.434% | 25.0221 | 0.2292% | 181.5496 | 1.663% | 1895 | 10893.9779 | 10737.4504 | 1.458% | 0.233%
2017-08-05 | 18 | 10928 | 156.7022 | 1.434% | 25.0486 | 0.2292% | 181.7508 | 1.663% | 1896 | 10902.9514 | 10746.2492 | 1.458% | 0.2331%
2017-07-18 | 16 | 10936 | 156.8575 | 1.434% | 25.0721 | 0.2293% | 181.9296 | 1.664% | 1897 | 10910.9279 | 10754.0704 | 1.459% | 0.2331%
2017-07-28 | 19 | 10936 | 156.8575 | 1.434% | 25.0721 | 0.2293% | 181.9296 | 1.664% | 1898 | 10910.9279 | 10754.0704 | 1.459% | 0.2331%
2017-08-05 | 17 | 10936 | 156.8575 | 1.434% | 25.0721 | 0.2293% | 181.9296 | 1.664% | 1899 | 10910.9279 | 10754.0704 | 1.459% | 0.2331%
2017-08-07 | 18 | 10942 | 156.974 | 1.435% | 25.0897 | 0.2293% | 182.0638 | 1.664% | 1900 | 10916.9103 | 10759.9362 | 1.459% | 0.2332%
2017-06-14 | 20 | 10943 | 156.9935 | 1.435% | 25.0927 | 0.2293% | 182.0861 | 1.664% | 1901 | 10917.9073 | 10760.9139 | 1.459% | 0.2332%
2017-07-20 | 12 | 10944 | 157.0129 | 1.435% | 25.0956 | 0.2293% | 182.1085 | 1.664% | 1902 | 10918.9044 | 10761.8915 | 1.459% | 0.2332%
2017-08-11 | 17 | 10948 | 157.0905 | 1.435% | 25.1074 | 0.2293% | 182.1979 | 1.664% | 1903 | 10922.8926 | 10765.8021 | 1.459% | 0.2332%
2017-07-26 | 20 | 10951 | 157.1488 | 1.435% | 25.1162 | 0.2294% | 182.265 | 1.664% | 1904 | 10925.8838 | 10768.735 | 1.459% | 0.2332%
2017-07-10 | 15 | 10956 | 157.2459 | 1.435% | 25.1309 | 0.2294% | 182.3767 | 1.665% | 1905 | 10930.8691 | 10773.6233 | 1.46% | 0.2333%
2017-08-02 | 18 | 10959 | 157.3041 | 1.435% | 25.1397 | 0.2294% | 182.4438 | 1.665% | 1906 | 10933.8603 | 10776.5562 | 1.46% | 0.2333%
2017-08-11 | 16 | 10965 | 157.4206 | 1.436% | 25.1573 | 0.2294% | 182.5779 | 1.665% | 1907 | 10939.8427 | 10782.4221 | 1.46% | 0.2333%
2017-07-18 | 17 | 10972 | 157.5565 | 1.436% | 25.1779 | 0.2295% | 182.7344 | 1.665% | 1908 | 10946.8221 | 10789.2656 | 1.46% | 0.2334%
2017-08-03 | 15 | 10982 | 157.7507 | 1.436% | 25.2073 | 0.2295% | 182.958 | 1.666% | 1909 | 10956.7927 | 10799.042 | 1.461% | 0.2334%
2017-06-24 | 14 | 10989 | 157.8866 | 1.437% | 25.2278 | 0.2296% | 183.1145 | 1.666% | 1910 | 10963.7722 | 10805.8855 | 1.461% | 0.2335%
2017-07-04 | 16 | 10989 | 157.8866 | 1.437% | 25.2278 | 0.2296% | 183.1145 | 1.666% | 1911 | 10963.7722 | 10805.8855 | 1.461% | 0.2335%
2017-07-02 | 15 | 10992 | 157.9449 | 1.437% | 25.2367 | 0.2296% | 183.1815 | 1.666% | 1912 | 10966.7633 | 10808.8185 | 1.461% | 0.2335%
2017-08-19 | 13 | 10997 | 158.042 | 1.437% | 25.2513 | 0.2296% | 183.2933 | 1.667% | 1913 | 10971.7487 | 10813.7067 | 1.461% | 0.2335%
2017-06-13 | 18 | 11001 | 158.1196 | 1.437% | 25.2631 | 0.2296% | 183.3827 | 1.667% | 1914 | 10975.7369 | 10817.6173 | 1.462% | 0.2335%
2017-07-27 | 20 | 11008 | 158.2556 | 1.438% | 25.2837 | 0.2297% | 183.5392 | 1.667% | 1915 | 10982.7163 | 10824.4608 | 1.462% | 0.2336%
2017-06-23 | 20 | 11010 | 158.2944 | 1.438% | 25.2895 | 0.2297% | 183.5839 | 1.667% | 1916 | 10984.7105 | 10826.4161 | 1.462% | 0.2336%
2017-08-19 | 19 | 11010 | 158.2944 | 1.438% | 25.2895 | 0.2297% | 183.5839 | 1.667% | 1917 | 10984.7105 | 10826.4161 | 1.462% | 0.2336%
2017-07-13 | 22 | 11015 | 158.3915 | 1.438% | 25.3042 | 0.2297% | 183.6957 | 1.668% | 1918 | 10989.6958 | 10831.3043 | 1.462% | 0.2336%
2017-06-12 | 18 | 11016 | 158.4109 | 1.438% | 25.3072 | 0.2297% | 183.7181 | 1.668% | 1919 | 10990.6928 | 10832.2819 | 1.462% | 0.2336%
2017-07-28 | 13 | 11016 | 158.4109 | 1.438% | 25.3072 | 0.2297% | 183.7181 | 1.668% | 1920 | 10990.6928 | 10832.2819 | 1.462% | 0.2336%
2017-07-27 | 13 | 11018 | 158.4497 | 1.438% | 25.3131 | 0.2297% | 183.7628 | 1.668% | 1921 | 10992.6869 | 10834.2372 | 1.462% | 0.2336%
2017-06-12 | 16 | 11021 | 158.508 | 1.438% | 25.3219 | 0.2298% | 183.8298 | 1.668% | 1922 | 10995.6781 | 10837.1702 | 1.463% | 0.2337%
2017-07-25 | 21 | 11021 | 158.508 | 1.438% | 25.3219 | 0.2298% | 183.8298 | 1.668% | 1923 | 10995.6781 | 10837.1702 | 1.463% | 0.2337%
2017-08-02 | 16 | 11021 | 158.508 | 1.438% | 25.3219 | 0.2298% | 183.8298 | 1.668% | 1924 | 10995.6781 | 10837.1702 | 1.463% | 0.2337%
2017-08-20 | 20 | 11023 | 158.5468 | 1.438% | 25.3278 | 0.2298% | 183.8746 | 1.668% | 1925 | 10997.6722 | 10839.1254 | 1.463% | 0.2337%
2017-07-07 | 12 | 11024 | 158.5662 | 1.438% | 25.3307 | 0.2298% | 183.8969 | 1.668% | 1926 | 10998.6693 | 10840.1031 | 1.463% | 0.2337%
2017-07-22 | 22 | 11025 | 158.5856 | 1.438% | 25.3336 | 0.2298% | 183.9193 | 1.668% | 1927 | 10999.6664 | 10841.0807 | 1.463% | 0.2337%
2017-08-20 | 14 | 11029 | 158.6633 | 1.439% | 25.3454 | 0.2298% | 184.0087 | 1.668% | 1928 | 11003.6546 | 10844.9913 | 1.463% | 0.2337%
2017-06-24 | 17 | 11043 | 158.9351 | 1.439% | 25.3865 | 0.2299% | 184.3217 | 1.669% | 1929 | 11017.6135 | 10858.6783 | 1.464% | 0.2338%
2017-08-07 | 16 | 11047 | 159.0128 | 1.439% | 25.3983 | 0.2299% | 184.4111 | 1.669% | 1930 | 11021.6017 | 10862.5889 | 1.464% | 0.2338%
2017-06-19 | 17 | 11049 | 159.0516 | 1.44% | 25.4042 | 0.2299% | 184.4558 | 1.669% | 1931 | 11023.5958 | 10864.5442 | 1.464% | 0.2338%
2017-07-10 | 16 | 11059 | 159.2458 | 1.44% | 25.4335 | 0.23% | 184.6794 | 1.67% | 1932 | 11033.5665 | 10874.3206 | 1.464% | 0.2339%
2017-07-04 | 18 | 11061 | 159.2847 | 1.44% | 25.4394 | 0.23% | 184.7241 | 1.67% | 1933 | 11035.5606 | 10876.2759 | 1.465% | 0.2339%
2017-06-12 | 17 | 11063 | 159.3235 | 1.44% | 25.4453 | 0.23% | 184.7688 | 1.67% | 1934 | 11037.5547 | 10878.2312 | 1.465% | 0.2339%
2017-07-21 | 21 | 11063 | 159.3235 | 1.44% | 25.4453 | 0.23% | 184.7688 | 1.67% | 1935 | 11037.5547 | 10878.2312 | 1.465% | 0.2339%
2017-06-15 | 14 | 11064 | 159.3429 | 1.44% | 25.4482 | 0.23% | 184.7911 | 1.67% | 1936 | 11038.5518 | 10879.2089 | 1.465% | 0.2339%
2017-08-03 | 17 | 11065 | 159.3623 | 1.44% | 25.4512 | 0.23% | 184.8135 | 1.67% | 1937 | 11039.5488 | 10880.1865 | 1.465% | 0.2339%
2017-06-13 | 17 | 11069 | 159.44 | 1.44% | 25.4629 | 0.23% | 184.9029 | 1.67% | 1938 | 11043.5371 | 10884.0971 | 1.465% | 0.2339%
2017-06-19 | 13 | 11071 | 159.4788 | 1.441% | 25.4688 | 0.23% | 184.9476 | 1.671% | 1939 | 11045.5312 | 10886.0524 | 1.465% | 0.234%
2017-07-03 | 17 | 11071 | 159.4788 | 1.441% | 25.4688 | 0.23% | 184.9476 | 1.671% | 1940 | 11045.5312 | 10886.0524 | 1.465% | 0.234%
2017-08-07 | 17 | 11072 | 159.4982 | 1.441% | 25.4717 | 0.2301% | 184.97 | 1.671% | 1941 | 11046.5283 | 10887.03 | 1.465% | 0.234%
2017-08-14 | 20 | 11077 | 159.5953 | 1.441% | 25.4864 | 0.2301% | 185.0818 | 1.671% | 1942 | 11051.5136 | 10891.9182 | 1.465% | 0.234%
2017-06-16 | 18 | 11078 | 159.6147 | 1.441% | 25.4894 | 0.2301% | 185.1041 | 1.671% | 1943 | 11052.5106 | 10892.8959 | 1.465% | 0.234%
2017-07-24 | 21 | 11083 | 159.7118 | 1.441% | 25.5041 | 0.2301% | 185.2159 | 1.671% | 1944 | 11057.4959 | 10897.7841 | 1.466% | 0.234%
2017-06-15 | 18 | 11095 | 159.9448 | 1.442% | 25.5393 | 0.2302% | 185.4842 | 1.672% | 1945 | 11069.4607 | 10909.5158 | 1.466% | 0.2341%
2017-07-23 | 12 | 11097 | 159.9837 | 1.442% | 25.5452 | 0.2302% | 185.5289 | 1.672% | 1946 | 11071.4548 | 10911.4711 | 1.466% | 0.2341%
2017-07-04 | 17 | 11098 | 160.0031 | 1.442% | 25.5481 | 0.2302% | 185.5512 | 1.672% | 1947 | 11072.4519 | 10912.4488 | 1.466% | 0.2341%
2017-08-04 | 18 | 11101 | 160.0613 | 1.442% | 25.557 | 0.2302% | 185.6183 | 1.672% | 1948 | 11075.443 | 10915.3817 | 1.466% | 0.2341%
2017-06-13 | 16 | 11104 | 160.1196 | 1.442% | 25.5658 | 0.2302% | 185.6854 | 1.672% | 1949 | 11078.4342 | 10918.3146 | 1.467% | 0.2342%
2017-08-15 | 21 | 11111 | 160.2555 | 1.442% | 25.5863 | 0.2303% | 185.8418 | 1.673% | 1950 | 11085.4137 | 10925.1582 | 1.467% | 0.2342%
2017-07-08 | 13 | 11113 | 160.2943 | 1.442% | 25.5922 | 0.2303% | 185.8866 | 1.673% | 1951 | 11087.4078 | 10927.1134 | 1.467% | 0.2342%
2017-07-11 | 13 | 11118 | 160.3914 | 1.443% | 25.6069 | 0.2303% | 185.9983 | 1.673% | 1952 | 11092.3931 | 10932.0017 | 1.467% | 0.2342%
2017-07-11 | 21 | 11124 | 160.5079 | 1.443% | 25.6246 | 0.2304% | 186.1325 | 1.673% | 1953 | 11098.3754 | 10937.8675 | 1.467% | 0.2343%
2017-08-04 | 17 | 11126 | 160.5467 | 1.443% | 25.6304 | 0.2304% | 186.1772 | 1.673% | 1954 | 11100.3696 | 10939.8228 | 1.468% | 0.2343%
2017-07-05 | 20 | 11130 | 160.6244 | 1.443% | 25.6422 | 0.2304% | 186.2666 | 1.674% | 1955 | 11104.3578 | 10943.7334 | 1.468% | 0.2343%
2017-08-21 | 20 | 11140 | 160.8186 | 1.444% | 25.6716 | 0.2304% | 186.4902 | 1.674% | 1956 | 11114.3284 | 10953.5098 | 1.468% | 0.2344%
2017-06-16 | 15 | 11142 | 160.8574 | 1.444% | 25.6774 | 0.2305% | 186.5349 | 1.674% | 1957 | 11116.3226 | 10955.4651 | 1.468% | 0.2344%
2017-06-24 | 16 | 11146 | 160.9351 | 1.444% | 25.6892 | 0.2305% | 186.6243 | 1.674% | 1958 | 11120.3108 | 10959.3757 | 1.468% | 0.2344%
2017-06-19 | 16 | 11148 | 160.9739 | 1.444% | 25.6951 | 0.2305% | 186.669 | 1.674% | 1959 | 11122.3049 | 10961.331 | 1.469% | 0.2344%
2017-08-23 | 12 | 11150 | 161.0128 | 1.444% | 25.701 | 0.2305% | 186.7137 | 1.675% | 1960 | 11124.299 | 10963.2863 | 1.469% | 0.2344%
2017-07-03 | 14 | 11157 | 161.1487 | 1.444% | 25.7215 | 0.2305% | 186.8702 | 1.675% | 1961 | 11131.2785 | 10970.1298 | 1.469% | 0.2345%
2017-08-02 | 17 | 11159 | 161.1875 | 1.444% | 25.7274 | 0.2306% | 186.9149 | 1.675% | 1962 | 11133.2726 | 10972.0851 | 1.469% | 0.2345%
2017-08-03 | 16 | 11159 | 161.1875 | 1.444% | 25.7274 | 0.2306% | 186.9149 | 1.675% | 1963 | 11133.2726 | 10972.0851 | 1.469% | 0.2345%
2017-06-14 | 14 | 11160 | 161.2069 | 1.445% | 25.7303 | 0.2306% | 186.9373 | 1.675% | 1964 | 11134.2697 | 10973.0627 | 1.469% | 0.2345%
2017-06-24 | 15 | 11160 | 161.2069 | 1.445% | 25.7303 | 0.2306% | 186.9373 | 1.675% | 1965 | 11134.2697 | 10973.0627 | 1.469% | 0.2345%
2017-07-12 | 22 | 11168 | 161.3623 | 1.445% | 25.7538 | 0.2306% | 187.1161 | 1.675% | 1966 | 11142.2462 | 10980.8839 | 1.469% | 0.2345%
2017-08-17 | 18 | 11169 | 161.3817 | 1.445% | 25.7568 | 0.2306% | 187.1385 | 1.676% | 1967 | 11143.2432 | 10981.8615 | 1.47% | 0.2345%
2017-08-18 | 22 | 11171 | 161.4205 | 1.445% | 25.7627 | 0.2306% | 187.1832 | 1.676% | 1968 | 11145.2373 | 10983.8168 | 1.47% | 0.2346%
2017-08-16 | 13 | 11182 | 161.6341 | 1.445% | 25.795 | 0.2307% | 187.4291 | 1.676% | 1969 | 11156.205 | 10994.5709 | 1.47% | 0.2346%
2017-07-19 | 14 | 11196 | 161.9059 | 1.446% | 25.8361 | 0.2308% | 187.7421 | 1.677% | 1970 | 11170.1639 | 11008.2579 | 1.471% | 0.2347%
2017-08-16 | 21 | 11198 | 161.9448 | 1.446% | 25.842 | 0.2308% | 187.7868 | 1.677% | 1971 | 11172.158 | 11010.2132 | 1.471% | 0.2347%
2017-07-24 | 14 | 11212 | 162.2166 | 1.447% | 25.8831 | 0.2309% | 188.0997 | 1.678% | 1972 | 11186.1169 | 11023.9003 | 1.471% | 0.2348%
2017-07-14 | 22 | 11219 | 162.3525 | 1.447% | 25.9037 | 0.2309% | 188.2562 | 1.678% | 1973 | 11193.0963 | 11030.7438 | 1.472% | 0.2348%
2017-07-19 | 20 | 11225 | 162.469 | 1.447% | 25.9214 | 0.2309% | 188.3904 | 1.678% | 1974 | 11199.0786 | 11036.6096 | 1.472% | 0.2349%
2017-06-16 | 16 | 11226 | 162.4884 | 1.447% | 25.9243 | 0.2309% | 188.4127 | 1.678% | 1975 | 11200.0757 | 11037.5873 | 1.472% | 0.2349%
2017-07-02 | 16 | 11226 | 162.4884 | 1.447% | 25.9243 | 0.2309% | 188.4127 | 1.678% | 1976 | 11200.0757 | 11037.5873 | 1.472% | 0.2349%
2017-07-06 | 13 | 11234 | 162.6438 | 1.448% | 25.9478 | 0.231% | 188.5916 | 1.679% | 1977 | 11208.0522 | 11045.4084 | 1.473% | 0.2349%
2017-07-21 | 12 | 11249 | 162.935 | 1.448% | 25.9919 | 0.2311% | 188.9269 | 1.679% | 1978 | 11223.0081 | 11060.0731 | 1.473% | 0.235%
2017-07-03 | 16 | 11258 | 163.1098 | 1.449% | 26.0183 | 0.2311% | 189.1281 | 1.68% | 1979 | 11231.9817 | 11068.8719 | 1.474% | 0.2351%
2017-08-21 | 13 | 11263 | 163.2069 | 1.449% | 26.033 | 0.2311% | 189.2399 | 1.68% | 1980 | 11236.967 | 11073.7601 | 1.474% | 0.2351%
2017-08-22 | 13 | 11263 | 163.2069 | 1.449% | 26.033 | 0.2311% | 189.2399 | 1.68% | 1981 | 11236.967 | 11073.7601 | 1.474% | 0.2351%
2017-07-12 | 12 | 11264 | 163.2263 | 1.449% | 26.036 | 0.2311% | 189.2622 | 1.68% | 1982 | 11237.964 | 11074.7378 | 1.474% | 0.2351%
2017-06-16 | 17 | 11277 | 163.4787 | 1.45% | 26.0742 | 0.2312% | 189.5529 | 1.681% | 1983 | 11250.9258 | 11087.4471 | 1.474% | 0.2352%
2017-06-23 | 15 | 11278 | 163.4981 | 1.45% | 26.0771 | 0.2312% | 189.5752 | 1.681% | 1984 | 11251.9229 | 11088.4248 | 1.474% | 0.2352%
2017-07-26 | 15 | 11279 | 163.5175 | 1.45% | 26.08 | 0.2312% | 189.5976 | 1.681% | 1985 | 11252.92 | 11089.4024 | 1.475% | 0.2352%
2017-08-19 | 18 | 11290 | 163.7311 | 1.45% | 26.1124 | 0.2313% | 189.8435 | 1.682% | 1986 | 11263.8876 | 11100.1565 | 1.475% | 0.2352%
2017-08-14 | 15 | 11294 | 163.8088 | 1.45% | 26.1241 | 0.2313% | 189.9329 | 1.682% | 1987 | 11267.8759 | 11104.0671 | 1.475% | 0.2353%
2017-08-21 | 16 | 11314 | 164.1971 | 1.451% | 26.1829 | 0.2314% | 190.38 | 1.683% | 1988 | 11287.8171 | 11123.62 | 1.476% | 0.2354%
2017-07-23 | 19 | 11317 | 164.2554 | 1.451% | 26.1917 | 0.2314% | 190.4471 | 1.683% | 1989 | 11290.8083 | 11126.5529 | 1.476% | 0.2354%
2017-07-06 | 21 | 11322 | 164.3525 | 1.452% | 26.2064 | 0.2315% | 190.5589 | 1.683% | 1990 | 11295.7936 | 11131.4411 | 1.476% | 0.2354%
2017-06-15 | 17 | 11324 | 164.3913 | 1.452% | 26.2123 | 0.2315% | 190.6036 | 1.683% | 1991 | 11297.7877 | 11133.3964 | 1.477% | 0.2354%
2017-07-15 | 19 | 11329 | 164.4884 | 1.452% | 26.227 | 0.2315% | 190.7153 | 1.683% | 1992 | 11302.773 | 11138.2847 | 1.477% | 0.2355%
2017-06-14 | 19 | 11335 | 164.6049 | 1.452% | 26.2446 | 0.2315% | 190.8495 | 1.684% | 1993 | 11308.7554 | 11144.1505 | 1.477% | 0.2355%
2017-07-03 | 15 | 11336 | 164.6243 | 1.452% | 26.2475 | 0.2315% | 190.8718 | 1.684% | 1994 | 11309.7525 | 11145.1282 | 1.477% | 0.2355%
2017-07-22 | 21 | 11337 | 164.6437 | 1.452% | 26.2505 | 0.2315% | 190.8942 | 1.684% | 1995 | 11310.7495 | 11146.1058 | 1.477% | 0.2355%
2017-07-02 | 19 | 11354 | 164.9738 | 1.453% | 26.3004 | 0.2316% | 191.2742 | 1.685% | 1996 | 11327.6996 | 11162.7258 | 1.478% | 0.2356%
2017-07-20 | 21 | 11356 | 165.0126 | 1.453% | 26.3063 | 0.2317% | 191.3189 | 1.685% | 1997 | 11329.6937 | 11164.6811 | 1.478% | 0.2356%
2017-07-05 | 14 | 11372 | 165.3233 | 1.454% | 26.3533 | 0.2317% | 191.6766 | 1.686% | 1998 | 11345.6467 | 11180.3234 | 1.479% | 0.2357%
2017-08-17 | 12 | 11375 | 165.3816 | 1.454% | 26.3621 | 0.2318% | 191.7437 | 1.686% | 1999 | 11348.6379 | 11183.2563 | 1.479% | 0.2357%
2017-06-19 | 15 | 11377 | 165.4204 | 1.454% | 26.368 | 0.2318% | 191.7884 | 1.686% | 2000 | 11350.632 | 11185.2116 | 1.479% | 0.2357%
2017-06-15 | 15 | 11380 | 165.4786 | 1.454% | 26.3768 | 0.2318% | 191.8555 | 1.686% | 2001 | 11353.6232 | 11188.1445 | 1.479% | 0.2358%
2017-08-22 | 21 | 11387 | 165.6146 | 1.454% | 26.3974 | 0.2318% | 192.012 | 1.686% | 2002 | 11360.6026 | 11194.988 | 1.479% | 0.2358%
2017-07-02 | 17 | 11401 | 165.8864 | 1.455% | 26.4385 | 0.2319% | 192.3249 | 1.687% | 2003 | 11374.5615 | 11208.6751 | 1.48% | 0.2359%
2017-07-28 | 14 | 11402 | 165.9058 | 1.455% | 26.4415 | 0.2319% | 192.3473 | 1.687% | 2004 | 11375.5585 | 11209.6527 | 1.48% | 0.2359%
2017-08-21 | 15 | 11408 | 166.0223 | 1.455% | 26.4591 | 0.2319% | 192.4814 | 1.687% | 2005 | 11381.5409 | 11215.5186 | 1.48% | 0.2359%
2017-06-15 | 16 | 11415 | 166.1582 | 1.456% | 26.4797 | 0.232% | 192.6379 | 1.688% | 2006 | 11388.5203 | 11222.3621 | 1.481% | 0.236%
2017-07-07 | 20 | 11416 | 166.1776 | 1.456% | 26.4826 | 0.232% | 192.6603 | 1.688% | 2007 | 11389.5174 | 11223.3397 | 1.481% | 0.236%
2017-06-14 | 15 | 11423 | 166.3136 | 1.456% | 26.5032 | 0.232% | 192.8168 | 1.688% | 2008 | 11396.4968 | 11230.1832 | 1.481% | 0.236%
2017-08-19 | 14 | 11424 | 166.333 | 1.456% | 26.5061 | 0.232% | 192.8391 | 1.688% | 2009 | 11397.4939 | 11231.1609 | 1.481% | 0.236%
2017-07-13 | 21 | 11425 | 166.3524 | 1.456% | 26.5091 | 0.232% | 192.8615 | 1.688% | 2010 | 11398.4909 | 11232.1385 | 1.481% | 0.236%
2017-06-23 | 19 | 11446 | 166.7602 | 1.457% | 26.5708 | 0.2321% | 193.3309 | 1.689% | 2011 | 11419.4292 | 11252.6691 | 1.482% | 0.2361%
2017-08-15 | 20 | 11448 | 166.799 | 1.457% | 26.5767 | 0.2322% | 193.3756 | 1.689% | 2012 | 11421.4233 | 11254.6244 | 1.482% | 0.2361%
2017-08-17 | 17 | 11455 | 166.9349 | 1.457% | 26.5972 | 0.2322% | 193.5321 | 1.689% | 2013 | 11428.4028 | 11261.4679 | 1.482% | 0.2362%
2017-07-02 | 18 | 11458 | 166.9932 | 1.457% | 26.606 | 0.2322% | 193.5992 | 1.69% | 2014 | 11431.394 | 11264.4008 | 1.482% | 0.2362%
2017-06-19 | 14 | 11460 | 167.032 | 1.458% | 26.6119 | 0.2322% | 193.6439 | 1.69% | 2015 | 11433.3881 | 11266.3561 | 1.483% | 0.2362%
2017-08-14 | 19 | 11465 | 167.1291 | 1.458% | 26.6266 | 0.2322% | 193.7557 | 1.69% | 2016 | 11438.3734 | 11271.2443 | 1.483% | 0.2362%
2017-07-26 | 19 | 11471 | 167.2456 | 1.458% | 26.6442 | 0.2323% | 193.8898 | 1.69% | 2017 | 11444.3558 | 11277.1102 | 1.483% | 0.2363%
2017-08-15 | 13 | 11471 | 167.2456 | 1.458% | 26.6442 | 0.2323% | 193.8898 | 1.69% | 2018 | 11444.3558 | 11277.1102 | 1.483% | 0.2363%
2017-06-14 | 18 | 11472 | 167.265 | 1.458% | 26.6472 | 0.2323% | 193.9122 | 1.69% | 2019 | 11445.3528 | 11278.0878 | 1.483% | 0.2363%
2017-07-28 | 18 | 11472 | 167.265 | 1.458% | 26.6472 | 0.2323% | 193.9122 | 1.69% | 2020 | 11445.3528 | 11278.0878 | 1.483% | 0.2363%
2017-08-20 | 19 | 11478 | 167.3815 | 1.458% | 26.6648 | 0.2323% | 194.0463 | 1.691% | 2021 | 11451.3352 | 11283.9537 | 1.483% | 0.2363%
2017-08-23 | 19 | 11478 | 167.3815 | 1.458% | 26.6648 | 0.2323% | 194.0463 | 1.691% | 2022 | 11451.3352 | 11283.9537 | 1.483% | 0.2363%
2017-07-08 | 19 | 11483 | 167.4786 | 1.458% | 26.6795 | 0.2323% | 194.1581 | 1.691% | 2023 | 11456.3205 | 11288.8419 | 1.484% | 0.2363%
2017-08-19 | 17 | 11484 | 167.498 | 1.459% | 26.6825 | 0.2323% | 194.1804 | 1.691% | 2024 | 11457.3175 | 11289.8196 | 1.484% | 0.2363%
2017-08-14 | 16 | 11488 | 167.5757 | 1.459% | 26.6942 | 0.2324% | 194.2699 | 1.691% | 2025 | 11461.3058 | 11293.7301 | 1.484% | 0.2364%
2017-07-13 | 12 | 11495 | 167.7116 | 1.459% | 26.7148 | 0.2324% | 194.4264 | 1.691% | 2026 | 11468.2852 | 11300.5736 | 1.484% | 0.2364%
2017-08-18 | 12 | 11495 | 167.7116 | 1.459% | 26.7148 | 0.2324% | 194.4264 | 1.691% | 2027 | 11468.2852 | 11300.5736 | 1.484% | 0.2364%
2017-08-20 | 15 | 11499 | 167.7892 | 1.459% | 26.7265 | 0.2324% | 194.5158 | 1.692% | 2028 | 11472.2735 | 11304.4842 | 1.484% | 0.2364%
2017-08-16 | 20 | 11502 | 167.8475 | 1.459% | 26.7353 | 0.2324% | 194.5828 | 1.692% | 2029 | 11475.2647 | 11307.4172 | 1.484% | 0.2364%
2017-07-15 | 13 | 11503 | 167.8669 | 1.459% | 26.7383 | 0.2324% | 194.6052 | 1.692% | 2030 | 11476.2617 | 11308.3948 | 1.484% | 0.2364%
2017-07-07 | 13 | 11514 | 168.0805 | 1.46% | 26.7706 | 0.2325% | 194.8511 | 1.692% | 2031 | 11487.2294 | 11319.1489 | 1.485% | 0.2365%
2017-06-23 | 18 | 11517 | 168.1388 | 1.46% | 26.7794 | 0.2325% | 194.9182 | 1.692% | 2032 | 11490.2206 | 11322.0818 | 1.485% | 0.2365%
2017-07-25 | 20 | 11535 | 168.4883 | 1.461% | 26.8323 | 0.2326% | 195.3206 | 1.693% | 2033 | 11508.1677 | 11339.6794 | 1.486% | 0.2366%
2017-06-23 | 16 | 11538 | 168.5465 | 1.461% | 26.8411 | 0.2326% | 195.3876 | 1.693% | 2034 | 11511.1589 | 11342.6124 | 1.486% | 0.2366%
2017-07-08 | 14 | 11543 | 168.6436 | 1.461% | 26.8558 | 0.2327% | 195.4994 | 1.694% | 2035 | 11516.1442 | 11347.5006 | 1.486% | 0.2367%
2017-07-20 | 13 | 11545 | 168.6824 | 1.461% | 26.8617 | 0.2327% | 195.5441 | 1.694% | 2036 | 11518.1383 | 11349.4559 | 1.486% | 0.2367%
2017-07-21 | 20 | 11551 | 168.7989 | 1.461% | 26.8793 | 0.2327% | 195.6783 | 1.694% | 2037 | 11524.1207 | 11355.3217 | 1.487% | 0.2367%
2017-07-27 | 19 | 11552 | 168.8183 | 1.461% | 26.8823 | 0.2327% | 195.7006 | 1.694% | 2038 | 11525.1177 | 11356.2994 | 1.487% | 0.2367%
2017-08-19 | 16 | 11555 | 168.8766 | 1.462% | 26.8911 | 0.2327% | 195.7677 | 1.694% | 2039 | 11528.1089 | 11359.2323 | 1.487% | 0.2367%
2017-07-24 | 20 | 11558 | 168.9348 | 1.462% | 26.8999 | 0.2327% | 195.8348 | 1.694% | 2040 | 11531.1001 | 11362.1652 | 1.487% | 0.2367%
2017-07-25 | 13 | 11569 | 169.1484 | 1.462% | 26.9322 | 0.2328% | 196.0807 | 1.695% | 2041 | 11542.0678 | 11372.9193 | 1.487% | 0.2368%
2017-07-26 | 16 | 11571 | 169.1873 | 1.462% | 26.9381 | 0.2328% | 196.1254 | 1.695% | 2042 | 11544.0619 | 11374.8746 | 1.487% | 0.2368%
2017-07-27 | 14 | 11577 | 169.3038 | 1.462% | 26.9557 | 0.2328% | 196.2595 | 1.695% | 2043 | 11550.0443 | 11380.7405 | 1.488% | 0.2369%
2017-07-11 | 20 | 11580 | 169.362 | 1.463% | 26.9646 | 0.2329% | 196.3266 | 1.695% | 2044 | 11553.0354 | 11383.6734 | 1.488% | 0.2369%
2017-06-23 | 17 | 11588 | 169.5174 | 1.463% | 26.9881 | 0.2329% | 196.5054 | 1.696% | 2045 | 11561.0119 | 11391.4946 | 1.488% | 0.2369% | 11595.287
2017-08-14 | 17 | 11596 | 169.655 | 1.463% | 27.0112 | 0.2329% | 196.6662 | 1.696% | 2046 | 11568.9888 | 11399.3338 | 1.488% | 0.237%
2017-07-12 | 21 | 11602 | 169.6357 | 1.462% | 27.0258 | 0.2329% | 196.6615 | 1.695% | 2047 | 11574.9742 | 11405.3385 | 1.487% | 0.237%
2017-08-19 | 15 | 11618 | 169.5842 | 1.46% | 27.0649 | 0.233% | 196.6491 | 1.693% | 2048 | 11590.9351 | 11421.3509 | 1.485% | 0.237%
2017-07-14 | 21 | 11619 | 169.581 | 1.46% | 27.0673 | 0.233% | 196.6483 | 1.692% | 2049 | 11591.9327 | 11422.3517 | 1.485% | 0.237%
2017-08-21 | 19 | 11622 | 169.5714 | 1.459% | 27.0746 | 0.233% | 196.646 | 1.692% | 2050 | 11594.9254 | 11425.354 | 1.484% | 0.237%
2017-07-19 | 15 | 11629 | 169.5489 | 1.458% | 27.0917 | 0.233% | 196.6406 | 1.691% | 2051 | 11601.9083 | 11432.3594 | 1.483% | 0.237%
2017-07-28 | 15 | 11635 | 169.5296 | 1.457% | 27.1063 | 0.233% | 196.6359 | 1.69% | 2052 | 11607.8937 | 11438.3641 | 1.482% | 0.237%
2017-06-14 | 16 | 11637 | 169.5231 | 1.457% | 27.1112 | 0.233% | 196.6344 | 1.69% | 2053 | 11609.8888 | 11440.3656 | 1.482% | 0.237%
2017-07-05 | 19 | 11640 | 169.5135 | 1.456% | 27.1185 | 0.233% | 196.632 | 1.689% | 2054 | 11612.8815 | 11443.368 | 1.481% | 0.237%
2017-07-14 | 12 | 11643 | 169.5038 | 1.456% | 27.1259 | 0.233% | 196.6297 | 1.689% | 2055 | 11615.8741 | 11446.3703 | 1.481% | 0.237%
2017-08-14 | 18 | 11643 | 169.5038 | 1.456% | 27.1259 | 0.233% | 196.6297 | 1.689% | 2056 | 11615.8741 | 11446.3703 | 1.481% | 0.237%
2017-07-22 | 13 | 11657 | 169.4588 | 1.454% | 27.16 | 0.233% | 196.6188 | 1.687% | 2057 | 11629.84 | 11460.3812 | 1.479% | 0.237%
2017-06-14 | 17 | 11663 | 169.4395 | 1.453% | 27.1747 | 0.233% | 196.6142 | 1.686% | 2058 | 11635.8253 | 11466.3858 | 1.478% | 0.237%
2017-08-22 | 20 | 11663 | 169.4395 | 1.453% | 27.1747 | 0.233% | 196.6142 | 1.686% | 2059 | 11635.8253 | 11466.3858 | 1.478% | 0.237%
2017-07-26 | 18 | 11667 | 169.4266 | 1.452% | 27.1844 | 0.233% | 196.6111 | 1.685% | 2060 | 11639.8156 | 11470.3889 | 1.477% | 0.237%
2017-08-21 | 14 | 11670 | 169.417 | 1.452% | 27.1917 | 0.233% | 196.6087 | 1.685% | 2061 | 11642.8083 | 11473.3913 | 1.477% | 0.237%
2017-08-17 | 16 | 11683 | 169.3752 | 1.45% | 27.2235 | 0.233% | 196.5986 | 1.683% | 2062 | 11655.7765 | 11486.4014 | 1.475% | 0.237%
2017-07-05 | 18 | 11685 | 169.3688 | 1.449% | 27.2283 | 0.233% | 196.5971 | 1.682% | 2063 | 11657.7717 | 11488.4029 | 1.474% | 0.237%
2017-07-26 | 17 | 11686 | 169.3655 | 1.449% | 27.2308 | 0.233% | 196.5963 | 1.682% | 2064 | 11658.7692 | 11489.4037 | 1.474% | 0.237%
2017-08-16 | 14 | 11686 | 169.3655 | 1.449% | 27.2308 | 0.233% | 196.5963 | 1.682% | 2065 | 11658.7692 | 11489.4037 | 1.474% | 0.237%
2017-07-05 | 15 | 11692 | 169.3462 | 1.448% | 27.2454 | 0.233% | 196.5917 | 1.681% | 2066 | 11664.7546 | 11495.4083 | 1.473% | 0.237%
2017-07-24 | 15 | 11695 | 169.3366 | 1.448% | 27.2527 | 0.233% | 196.5893 | 1.681% | 2067 | 11667.7473 | 11498.4107 | 1.473% | 0.237%
2017-07-15 | 18 | 11705 | 169.3044 | 1.446% | 27.2771 | 0.233% | 196.5816 | 1.679% | 2068 | 11677.7229 | 11508.4184 | 1.471% | 0.237%
2017-07-28 | 17 | 11717 | 169.2658 | 1.445% | 27.3064 | 0.233% | 196.5722 | 1.678% | 2069 | 11689.6936 | 11520.4278 | 1.469% | 0.237%
2017-08-21 | 17 | 11725 | 169.2401 | 1.443% | 27.3259 | 0.2331% | 196.566 | 1.676% | 2070 | 11697.6741 | 11528.434 | 1.468% | 0.237%
2017-08-18 | 21 | 11728 | 169.2304 | 1.443% | 27.3333 | 0.2331% | 196.5637 | 1.676% | 2071 | 11700.6667 | 11531.4363 | 1.468% | 0.237%
2017-07-11 | 14 | 11735 | 169.2079 | 1.442% | 27.3503 | 0.2331% | 196.5583 | 1.675% | 2072 | 11707.6497 | 11538.4417 | 1.466% | 0.237%
2017-07-23 | 13 | 11737 | 169.2015 | 1.442% | 27.3552 | 0.2331% | 196.5567 | 1.675% | 2073 | 11709.6448 | 11540.4433 | 1.466% | 0.237%
2017-07-28 | 16 | 11737 | 169.2015 | 1.442% | 27.3552 | 0.2331% | 196.5567 | 1.675% | 2074 | 11709.6448 | 11540.4433 | 1.466% | 0.237%
2017-07-19 | 19 | 11751 | 169.1565 | 1.44% | 27.3894 | 0.2331% | 196.5458 | 1.673% | 2075 | 11723.6106 | 11554.4542 | 1.464% | 0.237%
2017-08-22 | 14 | 11751 | 169.1565 | 1.44% | 27.3894 | 0.2331% | 196.5458 | 1.673% | 2076 | 11723.6106 | 11554.4542 | 1.464% | 0.237%
2017-08-20 | 16 | 11761 | 169.1243 | 1.438% | 27.4138 | 0.2331% | 196.5381 | 1.671% | 2077 | 11733.5862 | 11564.4619 | 1.462% | 0.2371%
2017-08-20 | 18 | 11766 | 169.1082 | 1.437% | 27.426 | 0.2331% | 196.5342 | 1.67% | 2078 | 11738.574 | 11569.4658 | 1.462% | 0.2371%
2017-07-08 | 15 | 11788 | 169.0375 | 1.434% | 27.4796 | 0.2331% | 196.5171 | 1.667% | 2079 | 11760.5204 | 11591.4829 | 1.458% | 0.2371%
2017-07-15 | 14 | 11802 | 168.9924 | 1.432% | 27.5138 | 0.2331% | 196.5062 | 1.665% | 2080 | 11774.4862 | 11605.4938 | 1.456% | 0.2371%
2017-08-23 | 13 | 11804 | 168.986 | 1.432% | 27.5187 | 0.2331% | 196.5047 | 1.665% | 2081 | 11776.4813 | 11607.4953 | 1.456% | 0.2371%
2017-08-21 | 18 | 11820 | 168.9345 | 1.429% | 27.5577 | 0.2331% | 196.4923 | 1.662% | 2082 | 11792.4423 | 11623.5077 | 1.453% | 0.2371%
2017-07-27 | 18 | 11822 | 168.9281 | 1.429% | 27.5626 | 0.2331% | 196.4907 | 1.662% | 2083 | 11794.4374 | 11625.5093 | 1.453% | 0.2371%
2017-07-05 | 16 | 11831 | 168.8992 | 1.428% | 27.5846 | 0.2332% | 196.4837 | 1.661% | 2084 | 11803.4154 | 11634.5163 | 1.452% | 0.2371%
2017-07-08 | 18 | 11833 | 168.8927 | 1.427% | 27.5894 | 0.2332% | 196.4822 | 1.66% | 2085 | 11805.4106 | 11636.5178 | 1.451% | 0.2371%
2017-07-07 | 14 | 11834 | 168.8895 | 1.427% | 27.5919 | 0.2332% | 196.4814 | 1.66% | 2086 | 11806.4081 | 11637.5186 | 1.451% | 0.2371%
2017-07-06 | 14 | 11838 | 168.8766 | 1.427% | 27.6016 | 0.2332% | 196.4783 | 1.66% | 2087 | 11810.3984 | 11641.5217 | 1.451% | 0.2371%
2017-08-15 | 19 | 11839 | 168.8734 | 1.426% | 27.6041 | 0.2332% | 196.4775 | 1.66% | 2088 | 11811.3959 | 11642.5225 | 1.45% | 0.2371%
2017-07-12 | 13 | 11843 | 168.8606 | 1.426% | 27.6138 | 0.2332% | 196.4744 | 1.659% | 2089 | 11815.3862 | 11646.5256 | 1.45% | 0.2371%
2017-07-06 | 20 | 11852 | 168.8316 | 1.424% | 27.6358 | 0.2332% | 196.4674 | 1.658% | 2090 | 11824.3642 | 11655.5326 | 1.449% | 0.2371%
2017-07-05 | 17 | 11853 | 168.8284 | 1.424% | 27.6382 | 0.2332% | 196.4666 | 1.658% | 2091 | 11825.3618 | 11656.5334 | 1.448% | 0.2371%
2017-08-15 | 14 | 11859 | 168.8091 | 1.423% | 27.6529 | 0.2332% | 196.462 | 1.657% | 2092 | 11831.3471 | 11662.538 | 1.447% | 0.2371%
2017-07-22 | 20 | 11861 | 168.8027 | 1.423% | 27.6578 | 0.2332% | 196.4604 | 1.656% | 2093 | 11833.3422 | 11664.5396 | 1.447% | 0.2371%
2017-08-20 | 17 | 11882 | 168.7351 | 1.42% | 27.709 | 0.2332% | 196.4441 | 1.653% | 2094 | 11854.291 | 11685.5559 | 1.444% | 0.2371%
2017-07-20 | 20 | 11886 | 168.7223 | 1.42% | 27.7188 | 0.2332% | 196.441 | 1.653% | 2095 | 11858.2812 | 11689.559 | 1.443% | 0.2371%
2017-07-15 | 15 | 11901 | 168.674 | 1.417% | 27.7554 | 0.2332% | 196.4294 | 1.651% | 2096 | 11873.2446 | 11704.5706 | 1.441% | 0.2371%
2017-07-27 | 15 | 11903 | 168.6676 | 1.417% | 27.7602 | 0.2332% | 196.4278 | 1.65% | 2097 | 11875.2398 | 11706.5722 | 1.441% | 0.2371%
2017-07-08 | 16 | 11921 | 168.6097 | 1.414% | 27.8042 | 0.2332% | 196.4138 | 1.648% | 2098 | 11893.1958 | 11724.5862 | 1.438% | 0.2371%
2017-07-23 | 18 | 11928 | 168.5872 | 1.413% | 27.8212 | 0.2332% | 196.4084 | 1.647% | 2099 | 11900.1788 | 11731.5916 | 1.437% | 0.2371%
2017-07-19 | 18 | 11930 | 168.5807 | 1.413% | 27.8261 | 0.2332% | 196.4069 | 1.646% | 2100 | 11902.1739 | 11733.5931 | 1.437% | 0.2371%
2017-07-08 | 17 | 11933 | 168.5711 | 1.413% | 27.8334 | 0.2332% | 196.4045 | 1.646% | 2101 | 11905.1666 | 11736.5955 | 1.436% | 0.2372%
2017-08-15 | 18 | 11937 | 168.5582 | 1.412% | 27.8432 | 0.2333% | 196.4014 | 1.645% | 2102 | 11909.1568 | 11740.5986 | 1.436% | 0.2372%
2017-07-13 | 20 | 11944 | 168.5357 | 1.411% | 27.8603 | 0.2333% | 196.396 | 1.644% | 2103 | 11916.1397 | 11747.604 | 1.435% | 0.2372%
2017-07-19 | 16 | 11945 | 168.5325 | 1.411% | 27.8627 | 0.2333% | 196.3952 | 1.644% | 2104 | 11917.1373 | 11748.6048 | 1.434% | 0.2372%
2017-07-07 | 19 | 11946 | 168.5293 | 1.411% | 27.8652 | 0.2333% | 196.3944 | 1.644% | 2105 | 11918.1348 | 11749.6056 | 1.434% | 0.2372%
2017-07-15 | 16 | 11958 | 168.4907 | 1.409% | 27.8944 | 0.2333% | 196.3851 | 1.642% | 2106 | 11930.1056 | 11761.6149 | 1.433% | 0.2372%
2017-07-15 | 17 | 11962 | 168.4778 | 1.408% | 27.9042 | 0.2333% | 196.382 | 1.642% | 2107 | 11934.0958 | 11765.618 | 1.432% | 0.2372%
2017-07-21 | 13 | 11966 | 168.465 | 1.408% | 27.9139 | 0.2333% | 196.3789 | 1.641% | 2108 | 11938.0861 | 11769.6211 | 1.431% | 0.2372%
2017-07-07 | 18 | 11967 | 168.4617 | 1.408% | 27.9164 | 0.2333% | 196.3781 | 1.641% | 2109 | 11939.0836 | 11770.6219 | 1.431% | 0.2372%
2017-08-18 | 20 | 11975 | 168.436 | 1.407% | 27.9359 | 0.2333% | 196.3719 | 1.64% | 2110 | 11947.0641 | 11778.6281 | 1.43% | 0.2372%
2017-07-11 | 19 | 11978 | 168.4264 | 1.406% | 27.9432 | 0.2333% | 196.3696 | 1.639% | 2111 | 11950.0568 | 11781.6304 | 1.43% | 0.2372%
2017-08-16 | 16 | 11979 | 168.4231 | 1.406% | 27.9457 | 0.2333% | 196.3688 | 1.639% | 2112 | 11951.0543 | 11782.6312 | 1.429% | 0.2372%
2017-08-16 | 19 | 12003 | 168.3459 | 1.403% | 28.0042 | 0.2333% | 196.3502 | 1.636% | 2113 | 11974.9958 | 11806.6498 | 1.426% | 0.2372%
2017-08-17 | 13 | 12005 | 168.3395 | 1.402% | 28.0091 | 0.2333% | 196.3486 | 1.636% | 2114 | 11976.9909 | 11808.6514 | 1.426% | 0.2372%
2017-07-14 | 20 | 12006 | 168.3363 | 1.402% | 28.0115 | 0.2333% | 196.3478 | 1.635% | 2115 | 11977.9885 | 11809.6522 | 1.425% | 0.2372%
2017-07-27 | 17 | 12014 | 168.3106 | 1.401% | 28.0311 | 0.2333% | 196.3416 | 1.634% | 2116 | 11985.9689 | 11817.6584 | 1.424% | 0.2372%
2017-08-16 | 15 | 12015 | 168.3073 | 1.401% | 28.0335 | 0.2333% | 196.3409 | 1.634% | 2117 | 11986.9665 | 11818.6591 | 1.424% | 0.2372%
2017-08-15 | 15 | 12016 | 168.3041 | 1.401% | 28.0359 | 0.2333% | 196.3401 | 1.634% | 2118 | 11987.9641 | 11819.6599 | 1.424% | 0.2372%
2017-08-23 | 18 | 12029 | 168.2623 | 1.399% | 28.0677 | 0.2333% | 196.33 | 1.632% | 2119 | 12000.9323 | 11832.67 | 1.422% | 0.2372%
2017-07-27 | 16 | 12033 | 168.2495 | 1.398% | 28.0774 | 0.2333% | 196.3269 | 1.632% | 2120 | 12004.9226 | 11836.6731 | 1.421% | 0.2372%
2017-07-12 | 20 | 12046 | 168.2076 | 1.396% | 28.1091 | 0.2333% | 196.3168 | 1.63% | 2121 | 12017.8909 | 11849.6832 | 1.42% | 0.2372%
2017-07-19 | 17 | 12050 | 168.1948 | 1.396% | 28.1189 | 0.2334% | 196.3137 | 1.629% | 2122 | 12021.8811 | 11853.6863 | 1.419% | 0.2372%
2017-07-11 | 18 | 12053 | 168.1851 | 1.395% | 28.1262 | 0.2334% | 196.3113 | 1.629% | 2123 | 12024.8738 | 11856.6887 | 1.418% | 0.2372%
2017-07-24 | 16 | 12053 | 168.1851 | 1.395% | 28.1262 | 0.2334% | 196.3113 | 1.629% | 2124 | 12024.8738 | 11856.6887 | 1.418% | 0.2372%
2017-07-11 | 15 | 12058 | 168.169 | 1.395% | 28.1384 | 0.2334% | 196.3075 | 1.628% | 2125 | 12029.8616 | 11861.6925 | 1.418% | 0.2372%
2017-07-13 | 13 | 12072 | 168.124 | 1.393% | 28.1726 | 0.2334% | 196.2966 | 1.626% | 2126 | 12043.8274 | 11875.7034 | 1.416% | 0.2372%
2017-07-25 | 14 | 12072 | 168.124 | 1.393% | 28.1726 | 0.2334% | 196.2966 | 1.626% | 2127 | 12043.8274 | 11875.7034 | 1.416% | 0.2372%
2017-07-22 | 14 | 12091 | 168.0629 | 1.39% | 28.2189 | 0.2334% | 196.2818 | 1.623% | 2128 | 12062.7811 | 11894.7182 | 1.413% | 0.2372%
2017-07-07 | 15 | 12095 | 168.05 | 1.389% | 28.2287 | 0.2334% | 196.2787 | 1.623% | 2129 | 12066.7713 | 11898.7213 | 1.412% | 0.2372%
2017-07-06 | 15 | 12096 | 168.0468 | 1.389% | 28.2311 | 0.2334% | 196.278 | 1.623% | 2130 | 12067.7689 | 11899.722 | 1.412% | 0.2372%
2017-07-25 | 19 | 12096 | 168.0468 | 1.389% | 28.2311 | 0.2334% | 196.278 | 1.623% | 2131 | 12067.7689 | 11899.722 | 1.412% | 0.2372%
2017-07-24 | 19 | 12100 | 168.034 | 1.389% | 28.2409 | 0.2334% | 196.2749 | 1.622% | 2132 | 12071.7591 | 11903.7251 | 1.412% | 0.2372%
2017-08-18 | 13 | 12100 | 168.034 | 1.389% | 28.2409 | 0.2334% | 196.2749 | 1.622% | 2133 | 12071.7591 | 11903.7251 | 1.412% | 0.2372%
2017-07-07 | 16 | 12106 | 168.0147 | 1.388% | 28.2555 | 0.2334% | 196.2702 | 1.621% | 2134 | 12077.7445 | 11909.7298 | 1.411% | 0.2372%
2017-08-17 | 15 | 12108 | 168.0082 | 1.388% | 28.2604 | 0.2334% | 196.2686 | 1.621% | 2135 | 12079.7396 | 11911.7314 | 1.41% | 0.2372%
2017-07-21 | 19 | 12110 | 168.0018 | 1.387% | 28.2653 | 0.2334% | 196.2671 | 1.621% | 2136 | 12081.7347 | 11913.7329 | 1.41% | 0.2372%
2017-08-15 | 17 | 12110 | 168.0018 | 1.387% | 28.2653 | 0.2334% | 196.2671 | 1.621% | 2137 | 12081.7347 | 11913.7329 | 1.41% | 0.2372%
2017-07-23 | 14 | 12111 | 167.9986 | 1.387% | 28.2677 | 0.2334% | 196.2663 | 1.621% | 2138 | 12082.7323 | 11914.7337 | 1.41% | 0.2373%
2017-07-11 | 17 | 12121 | 167.9664 | 1.386% | 28.2921 | 0.2334% | 196.2585 | 1.619% | 2139 | 12092.7079 | 11924.7415 | 1.409% | 0.2373%
2017-08-22 | 15 | 12146 | 167.886 | 1.382% | 28.3531 | 0.2334% | 196.2391 | 1.616% | 2140 | 12117.6469 | 11949.7609 | 1.405% | 0.2373%
2017-07-20 | 14 | 12159 | 167.8442 | 1.38% | 28.3848 | 0.2334% | 196.229 | 1.614% | 2141 | 12130.6152 | 11962.771 | 1.403% | 0.2373%
2017-08-16 | 18 | 12161 | 167.8378 | 1.38% | 28.3897 | 0.2334% | 196.2275 | 1.614% | 2142 | 12132.6103 | 11964.7725 | 1.403% | 0.2373%
2017-07-11 | 16 | 12168 | 167.8152 | 1.379% | 28.4068 | 0.2335% | 196.2221 | 1.613% | 2143 | 12139.5932 | 11971.7779 | 1.402% | 0.2373%
2017-08-15 | 16 | 12175 | 167.7927 | 1.378% | 28.4239 | 0.2335% | 196.2166 | 1.612% | 2144 | 12146.5761 | 11978.7834 | 1.401% | 0.2373%
2017-07-06 | 18 | 12203 | 167.7027 | 1.374% | 28.4922 | 0.2335% | 196.1949 | 1.608% | 2145 | 12174.5078 | 12006.8051 | 1.397% | 0.2373%
2017-07-24 | 18 | 12207 | 167.6898 | 1.374% | 28.502 | 0.2335% | 196.1918 | 1.607% | 2146 | 12178.498 | 12010.8082 | 1.396% | 0.2373%
2017-08-17 | 14 | 12208 | 167.6866 | 1.374% | 28.5044 | 0.2335% | 196.191 | 1.607% | 2147 | 12179.4956 | 12011.809 | 1.396% | 0.2373%
2017-08-16 | 17 | 12210 | 167.6802 | 1.373% | 28.5093 | 0.2335% | 196.1894 | 1.607% | 2148 | 12181.4907 | 12013.8106 | 1.396% | 0.2373%
2017-08-22 | 19 | 12223 | 167.6383 | 1.371% | 28.541 | 0.2335% | 196.1793 | 1.605% | 2149 | 12194.459 | 12026.8207 | 1.394% | 0.2373%
2017-07-24 | 17 | 12225 | 167.6319 | 1.371% | 28.5459 | 0.2335% | 196.1778 | 1.605% | 2150 | 12196.4541 | 12028.8222 | 1.394% | 0.2373%
2017-07-06 | 16 | 12229 | 167.619 | 1.371% | 28.5556 | 0.2335% | 196.1747 | 1.604% | 2151 | 12200.4444 | 12032.8253 | 1.393% | 0.2373%
2017-07-06 | 19 | 12237 | 167.5933 | 1.37% | 28.5752 | 0.2335% | 196.1685 | 1.603% | 2152 | 12208.4248 | 12040.8315 | 1.392% | 0.2373%
2017-07-07 | 17 | 12244 | 167.5708 | 1.369% | 28.5922 | 0.2335% | 196.163 | 1.602% | 2153 | 12215.4078 | 12047.837 | 1.391% | 0.2373%
2017-07-23 | 17 | 12252 | 167.5451 | 1.367% | 28.6118 | 0.2335% | 196.1568 | 1.601% | 2154 | 12223.3882 | 12055.8432 | 1.39% | 0.2373%
2017-07-12 | 14 | 12262 | 167.5129 | 1.366% | 28.6362 | 0.2335% | 196.1491 | 1.6% | 2155 | 12233.3638 | 12065.8509 | 1.388% | 0.2373%
2017-07-14 | 13 | 12269 | 167.4904 | 1.365% | 28.6532 | 0.2335% | 196.1436 | 1.599% | 2156 | 12240.3468 | 12072.8564 | 1.387% | 0.2373%
2017-07-23 | 15 | 12303 | 167.381 | 1.36% | 28.7362 | 0.2336% | 196.1172 | 1.594% | 2157 | 12274.2638 | 12106.8828 | 1.383% | 0.2374%
2017-07-06 | 17 | 12322 | 167.3199 | 1.358% | 28.7826 | 0.2336% | 196.1025 | 1.591% | 2158 | 12293.2174 | 12125.8975 | 1.38% | 0.2374%
2017-08-18 | 19 | 12340 | 167.262 | 1.355% | 28.8265 | 0.2336% | 196.0885 | 1.589% | 2159 | 12311.1735 | 12143.9115 | 1.377% | 0.2374%
2017-07-14 | 19 | 12355 | 167.2138 | 1.353% | 28.8631 | 0.2336% | 196.0769 | 1.587% | 2160 | 12326.1369 | 12158.9231 | 1.375% | 0.2374%
2017-08-23 | 14 | 12360 | 167.1977 | 1.353% | 28.8753 | 0.2336% | 196.073 | 1.586% | 2161 | 12331.1247 | 12163.927 | 1.375% | 0.2374%
2017-08-22 | 18 | 12369 | 167.1688 | 1.352% | 28.8972 | 0.2336% | 196.066 | 1.585% | 2162 | 12340.1028 | 12172.934 | 1.373% | 0.2374%
2017-07-21 | 18 | 12370 | 167.1655 | 1.351% | 28.8997 | 0.2336% | 196.0652 | 1.585% | 2163 | 12341.1003 | 12173.9348 | 1.373% | 0.2374%
2017-07-22 | 15 | 12372 | 167.1591 | 1.351% | 28.9045 | 0.2336% | 196.0637 | 1.585% | 2164 | 12343.0955 | 12175.9363 | 1.373% | 0.2374%
2017-07-25 | 15 | 12372 | 167.1591 | 1.351% | 28.9045 | 0.2336% | 196.0637 | 1.585% | 2165 | 12343.0955 | 12175.9363 | 1.373% | 0.2374%
2017-07-23 | 16 | 12384 | 167.1205 | 1.349% | 28.9338 | 0.2336% | 196.0543 | 1.583% | 2166 | 12355.0662 | 12187.9457 | 1.371% | 0.2374%
2017-07-25 | 18 | 12386 | 167.1141 | 1.349% | 28.9387 | 0.2336% | 196.0528 | 1.583% | 2167 | 12357.0613 | 12189.9472 | 1.371% | 0.2374%
2017-07-22 | 19 | 12394 | 167.0883 | 1.348% | 28.9582 | 0.2336% | 196.0466 | 1.582% | 2168 | 12365.0418 | 12197.9534 | 1.37% | 0.2374%
2017-08-23 | 17 | 12395 | 167.0851 | 1.348% | 28.9607 | 0.2336% | 196.0458 | 1.582% | 2169 | 12366.0393 | 12198.9542 | 1.37% | 0.2374%
2017-07-12 | 19 | 12407 | 167.0465 | 1.346% | 28.9899 | 0.2337% | 196.0365 | 1.58% | 2170 | 12378.0101 | 12210.9635 | 1.368% | 0.2374%
2017-07-12 | 15 | 12411 | 167.0337 | 1.346% | 28.9997 | 0.2337% | 196.0334 | 1.58% | 2171 | 12382.0003 | 12214.9666 | 1.367% | 0.2374%
2017-07-20 | 19 | 12412 | 167.0304 | 1.346% | 29.0021 | 0.2337% | 196.0326 | 1.579% | 2172 | 12382.9979 | 12215.9674 | 1.367% | 0.2374%
2017-08-18 | 14 | 12427 | 166.9822 | 1.344% | 29.0387 | 0.2337% | 196.0209 | 1.577% | 2173 | 12397.9613 | 12230.9791 | 1.365% | 0.2374%
2017-07-20 | 15 | 12435 | 166.9565 | 1.343% | 29.0583 | 0.2337% | 196.0147 | 1.576% | 2174 | 12405.9417 | 12238.9853 | 1.364% | 0.2374%
2017-08-22 | 17 | 12449 | 166.9114 | 1.341% | 29.0924 | 0.2337% | 196.0039 | 1.574% | 2175 | 12419.9076 | 12252.9961 | 1.362% | 0.2374%
2017-07-12 | 18 | 12461 | 166.8728 | 1.339% | 29.1217 | 0.2337% | 195.9945 | 1.573% | 2176 | 12431.8783 | 12265.0055 | 1.361% | 0.2374%
2017-08-22 | 16 | 12469 | 166.8471 | 1.338% | 29.1412 | 0.2337% | 195.9883 | 1.572% | 2177 | 12439.8588 | 12273.0117 | 1.359% | 0.2374%
2017-07-13 | 19 | 12472 | 166.8375 | 1.338% | 29.1485 | 0.2337% | 195.986 | 1.571% | 2178 | 12442.8515 | 12276.014 | 1.359% | 0.2374%
2017-07-22 | 18 | 12478 | 166.8182 | 1.337% | 29.1632 | 0.2337% | 195.9813 | 1.571% | 2179 | 12448.8368 | 12282.0187 | 1.358% | 0.2374%
2017-07-12 | 16 | 12488 | 166.786 | 1.336% | 29.1876 | 0.2337% | 195.9736 | 1.569% | 2180 | 12458.8124 | 12292.0264 | 1.357% | 0.2375%
2017-07-14 | 18 | 12498 | 166.7538 | 1.334% | 29.212 | 0.2337% | 195.9658 | 1.568% | 2181 | 12468.788 | 12302.0342 | 1.355% | 0.2375%
2017-08-18 | 18 | 12499 | 166.7506 | 1.334% | 29.2144 | 0.2337% | 195.965 | 1.568% | 2182 | 12469.7856 | 12303.035 | 1.355% | 0.2375%
2017-07-22 | 17 | 12501 | 166.7442 | 1.334% | 29.2193 | 0.2337% | 195.9635 | 1.568% | 2183 | 12471.7807 | 12305.0365 | 1.355% | 0.2375%
2017-07-20 | 18 | 12503 | 166.7378 | 1.334% | 29.2242 | 0.2337% | 195.9619 | 1.567% | 2184 | 12473.7758 | 12307.0381 | 1.355% | 0.2375%
2017-07-22 | 16 | 12503 | 166.7378 | 1.334% | 29.2242 | 0.2337% | 195.9619 | 1.567% | 2185 | 12473.7758 | 12307.0381 | 1.355% | 0.2375%
2017-07-21 | 14 | 12505 | 166.7313 | 1.333% | 29.2291 | 0.2337% | 195.9604 | 1.567% | 2186 | 12475.7709 | 12309.0396 | 1.355% | 0.2375%
2017-07-25 | 17 | 12505 | 166.7313 | 1.333% | 29.2291 | 0.2337% | 195.9604 | 1.567% | 2187 | 12475.7709 | 12309.0396 | 1.355% | 0.2375%
2017-07-12 | 17 | 12523 | 166.6734 | 1.331% | 29.273 | 0.2338% | 195.9464 | 1.565% | 2188 | 12493.727 | 12327.0536 | 1.352% | 0.2375%
2017-07-25 | 16 | 12523 | 166.6734 | 1.331% | 29.273 | 0.2338% | 195.9464 | 1.565% | 2189 | 12493.727 | 12327.0536 | 1.352% | 0.2375%
2017-07-13 | 18 | 12563 | 166.5448 | 1.326% | 29.3706 | 0.2338% | 195.9153 | 1.559% | 2190 | 12533.6294 | 12367.0847 | 1.347% | 0.2375%
2017-08-23 | 15 | 12574 | 166.5094 | 1.324% | 29.3974 | 0.2338% | 195.9068 | 1.558% | 2191 | 12544.6026 | 12378.0932 | 1.345% | 0.2375%
2017-07-13 | 14 | 12582 | 166.4837 | 1.323% | 29.4169 | 0.2338% | 195.9006 | 1.557% | 2192 | 12552.5831 | 12386.0994 | 1.344% | 0.2375%
2017-07-21 | 17 | 12583 | 166.4804 | 1.323% | 29.4194 | 0.2338% | 195.8998 | 1.557% | 2193 | 12553.5806 | 12387.1002 | 1.344% | 0.2375%
2017-07-21 | 15 | 12602 | 166.4193 | 1.321% | 29.4657 | 0.2338% | 195.8851 | 1.554% | 2194 | 12572.5343 | 12406.1149 | 1.341% | 0.2375%
2017-08-18 | 15 | 12602 | 166.4193 | 1.321% | 29.4657 | 0.2338% | 195.8851 | 1.554% | 2195 | 12572.5343 | 12406.1149 | 1.341% | 0.2375%
2017-08-23 | 16 | 12603 | 166.4161 | 1.32% | 29.4682 | 0.2338% | 195.8843 | 1.554% | 2196 | 12573.5318 | 12407.1157 | 1.341% | 0.2375%
2017-08-18 | 17 | 12615 | 166.3775 | 1.319% | 29.4974 | 0.2338% | 195.875 | 1.553% | 2197 | 12585.5026 | 12419.125 | 1.34% | 0.2375%
2017-07-20 | 16 | 12625 | 166.3454 | 1.318% | 29.5218 | 0.2338% | 195.8672 | 1.551% | 2198 | 12595.4782 | 12429.1328 | 1.338% | 0.2375%
2017-07-20 | 17 | 12640 | 166.2971 | 1.316% | 29.5584 | 0.2338% | 195.8556 | 1.549% | 2199 | 12610.4416 | 12444.1444 | 1.336% | 0.2375%
2017-07-21 | 16 | 12650 | 166.265 | 1.314% | 29.5828 | 0.2339% | 195.8478 | 1.548% | 2200 | 12620.4172 | 12454.1522 | 1.335% | 0.2375%
2017-07-13 | 15 | 12662 | 166.2264 | 1.313% | 29.6121 | 0.2339% | 195.8385 | 1.547% | 2201 | 12632.3879 | 12466.1615 | 1.333% | 0.2375%
2017-07-14 | 17 | 12663 | 166.2231 | 1.313% | 29.6146 | 0.2339% | 195.8377 | 1.547% | 2202 | 12633.3854 | 12467.1623 | 1.333% | 0.2375%
2017-07-14 | 14 | 12676 | 166.1813 | 1.311% | 29.6463 | 0.2339% | 195.8276 | 1.545% | 2203 | 12646.3537 | 12480.1724 | 1.332% | 0.2375%
2017-08-18 | 16 | 12684 | 166.1556 | 1.31% | 29.6658 | 0.2339% | 195.8214 | 1.544% | 2204 | 12654.3342 | 12488.1786 | 1.331% | 0.2376% | 12698.4059
2017-07-13 | 16 | 12750 | 165.9433 | 1.302% | 29.8268 | 0.2339% | 195.7701 | 1.535% | 2205 | 12720.1732 | 12554.2299 | 1.322% | 0.2376%
2017-07-14 | 15 | 12756 | 165.924 | 1.301% | 29.8415 | 0.2339% | 195.7655 | 1.535% | 2206 | 12726.1585 | 12560.2345 | 1.321% | 0.2376%
2017-07-14 | 16 | 12774 | 165.8661 | 1.298% | 29.8854 | 0.234% | 195.7515 | 1.532% | 2207 | 12744.1146 | 12578.2485 | 1.319% | 0.2376%
2017-07-13 | 17 | 12784 | 165.834 | 1.297% | 29.9098 | 0.234% | 195.7437 | 1.531% | 2208 | 12754.0902 | 12588.2563 | 1.317% | 0.2376%
|  | 18947554 | 276115.8536 | 1.457% | 44146.3064 | 0.233% | 320262.16 | 1.69% |  | 18903407.6936 | 18627291.84 | 1.482% | 0.237%
Note on C3: Quaintance, William Harford: Measured at generator energy meter
Note on C4: Quaintance, William Harford: Keep sorted by MW load, smallest to largest

## Losses from PSSE
|  | GSU + Transmission Losses |  |  |  | Transmission Losses Only |  |  |  | GSU Losses Only |  |  |  | CPLE & CPLW Load (MW)
PSSE Case Name | CPLE & CPLW PSSE Load(MW) | Line & Copper Losses (MW) | Core Losses (MW) | Line, Copper, & Core Losses (MW) | Line, Copper, & Core Losses (%) | Line & Copper Losses (MW) | Core Losses (MW) | Line, Copper, & Core Losses (MW) | Line, Copper, & Core Losses (%) | Copper Losses (MW) | Core Losses (MW) | Copper & Core Losses (MW) | Copper & Core Losses (%) | POD (PSSE) LOAD | GEN HIGH SIDE LOAD | GEN LOW SIDE LOAD
Hour_001_2017_06_09_03.sav | 4711.6794 | 112.4787 | 17.7516 | 130.2303 | 2.764% | 104.2369 | 10.8045 | 115.0414 | 2.442% | 8.2418 | 6.9471 | 15.189 | 0.3224% | 4711.6794 | 4826.7207 | 4841.9097
Hour_001_2017_07_02_03.sav | 5866.6014 | 101.5547 | 17.7516 | 119.3063 | 2.034% | 92.4629 | 10.8045 | 103.2673 | 1.76% | 9.0919 | 6.9471 | 16.039 | 0.2734% | 5866.6014 | 5969.8687 | 5985.9077
Hour_001_2017_07_16_10.sav | 8657.0359 | 116.2258 | 17.7516 | 133.9774 | 1.548% | 104.4041 | 10.8045 | 115.2086 | 1.331% | 11.8217 | 6.9471 | 18.7688 | 0.2168% | 8657.0359 | 8772.2445 | 8791.0133
Hour_001_2017_07_11_18.sav | 11398.5521 | 178.9152 | 17.7516 | 196.6668 | 1.725% | 158.853 | 10.8045 | 169.6575 | 1.488% | 20.0621 | 6.9471 | 27.0093 | 0.237% | 11398.5521 | 11568.2096 | 11595.2189
Hour_001_2017_08_18_14.sav | 12502.6651 | 178.0585 | 17.7516 | 195.8102 | 1.566% | 155.3046 | 10.8045 | 166.109 | 1.329% | 22.754 | 6.9471 | 29.7011 | 0.2376% | 12502.6651 | 12668.7741 | 12698.4753
From power flow model
From core losses sheet
Calculated values |  |  |  | Note: PSSE Loads are equivalent to POD loads
Note on Q3: Quaintance, William Harford: Represents POD load plus transmission losses
Note on R3: Quaintance, William Harford: Represents POD load plus transmission and GSU losses, equivalent to BA load from control center

## Core Losses
| From: | LS FeLossDoc2018 03-26-18.xlsx
MW
6.9471 | GSU Core Losses
10.8045 | T-T Core Losses
17.7516 | Total