DUKE ELECTRIC TRANSMISSION
Facility Connection Requirements

August 21, 2008

REVISIONS

| revision Number |  | date |  | reason for revision |
| --- | --- | --- | --- | --- |
| 0 |  |  |  | Approved by SERC |
| 1 |  | 8/5/01 |  | Include specific generator reactive support requirements in section IV.D.6.c |
| 2 |  | 9/10/03 |  | Clarify load connection requirements in section III.C.2. Clarify joint study requirements in section III.B and IV.B. Add statement that future project data changes may require additional study of impact. |
| 3 |  | 8/25/06 |  | Reformatting only of fonts and alignment. No technical changes. |
| 4 |  | 10/1/06 |  | Added section III D 1 i and associated definitions |
| 5 |  | 12/1/06 |  | Revised sections III.D.1.d and IV.D.1.e requirements for voltage flicker per IEEE Standard 1453-2004. |
| 6 |  | 6/20/08 |  | Section IV E-4 “Protective System Coordination”, additional clarifying language. |

Table of Contents

I.	INTRODUCTION	5

II.	DEFINITIONS	6

III.	FACILITY CONNECTION REQUIREMENTS – LOAD DELIVERIES	9

A.	Scope	9

B.	Connection and System Impact Studies and Project Sponsor-Supplied Information	10

1.	Connection Configuration	10

2.	Power Flow	10

3.	Protection	11

4.	Power Quality and Reliability	11

5.	Changes to Project Sponsor-Supplied Information	13

6.	Required Project Sponsor-Supplied Information	13

C.	General Requirements	14

1.	Safety	14

2.	Connection Point Considerations	15

3.	Substation Grounding	19

4.	Insulation Coordination	20

5.	Inspection, Testing, Calibration and Maintenance	21

6.	Station Service	22

D.	Performance Requirements	23

1.	Project Performance Criteria	23

2.	Duke ET System Characteristics	27

E.	Protection Requirements	28

1.	Protective Relaying Philosophy	28

2.	100-kV Load Delivery (radial load at Connection Point)	29

3.	100-kV Load Delivery Requiring a New Duke ET -Owned Tap Line	30

4.	Dual Feeds to Project, 44-kV, 230-kV and Higher, etc.	31

F.	Metering and Telecommunication Requirements	31

1.	Supervisory Control and Data Acquisition (SCADA)	31

2.	Metering	31

3.	Voice Communication	33

4.	Telecommunications for SCADA	33

5.	Telecommunications for Revenue-accuracy metering	33

6.	Telecommunications for Protection Systems	33

IV.	FACILITY CONNECTION REQUIREMENTS – GENERATION AND INTERCONNECTION FACILITIES	34

A.	Scope	34

B.	Request for Generation and Interconnection Studies	35

1.	Connection Configuration	35

2.	Power Flow	35

3.	Protection	36

4.	Power Quality and Reliability	36

5.	Changes to Project Sponsor-Supplied Information	38

6.	Required Project Sponsor-Supplied Information	38

C.	General Requirements	40

1.	Safety	40

2.	Connection Point Considerations	41

3.	Substation Grounding	42

4.	Insulation Coordination	42

5.	Inspection, Testing, Calibration and Maintenance	44

6.	Station Service	45

7.	Isolating, Synchronizing and Black Starts	45

D.	Performance Requirements	47

1.	Project Performance Criteria	47

2.	Duke ET System Characteristics	50

3.	Switchgear	51

4.	Excitation System and Power System Stabilizers	52

5.	Governor Speed and Frequency Control	53

6.	Voltage Regulation and Reactive Power Requirements	53

7.	Voltage and Frequency Operation During Disturbances	56

E.	Protection Requirements	56

1.	Protection Criteria	57

2.	Implications for Project Connection to an Existing Customer Service Substation	59

3.	Protection Measures	59

4.	Protective System Coordination	62

5.	Protective System Maintenance	63

6.	Protective System Fault Analysis	63

7.	System Modifications Beyond the Connection Point	63

F.	System Dispatching, Operation & Control, Power Scheduling, and Reserves	66

1.	General	66

2.	Scheduling	66

3.	Load Following	66

4.	Regulation	66

5.	Reserves	66

G.	Metering and Telecommunication Requirements	66

1.	Supervisory Control and Data Acquisition (SCADA)	67

2.	Metering	67

3.	Voice Communications	69

4.	Data Communications	69

5.	Telecommunications for Revenue-accuracy Metering	69

6.	Telecommunications for Control & Protection	70

H.	Exceptions	70

V.	REFERENCES	71

# INTRODUCTION

Standard (.C.S1 of the NERC (North American Electric Reliability Council) Planning Standards issued September, 1997 state that Facility Connection Requirements for all facilities involved in the generation, transmission, and use of electricity be documented.  All electric industry participants are required to document the facility connection requirements for their system.

Duke Electric Transmission (Duke ET) has prepared this document to identify technical requirements for connecting load deliveries, generation facilities, and control area Interconnections to the Duke Electric Transmission System (Duke ET System) which typically consists of 44-, 100-, 230-, and 500-kV transmission lines and stations.  This document is divided into two major sections: 1) Load Delivery Requirements and 2) Generation and Interconnection Requirements.  Important terms used in this document are capitalized and italicized (e.g. Project, Project Sponsor, Connection Point) and explained in the Definitions section.  Some projects may have both load and generation on site.  Load Delivery Requirements apply to projects having generating capability of less than 25% of minimum load.  These technical requirements are designed to ensure the safe operation, integrity, and reliability of the Duke ET System.

These requirements do not supersede existing contracts such as the Catawba Agreements.  The document may be used to interpret some of the provisions of existing contracts, for example, where “Prudent Utility Practice” applies.  The document can also be used in developing contracts, operating agreements, etc. to specify requirements of individual projects connecting to the Duke ET System.  These requirements will be adhered to for all connections, including those owned by Duke Energy.

Technical requirements are addressed, but contractual matters, such as costs, ownership, leasing options, scheduling, and billing are not the focus of this document.  In general, the Project Sponsor assumes the cost of all design, construction, inspection, analysis, maintenance, operations, monitoring, and all associated facilities needed to satisfy the technical requirements identified for integration of the Project into the Duke ET System.  Enforcement of these requirements will be covered in the contracts, operating agreements, and/or other legal documents applicable to the specific Project.

The Project Sponsor submits the proposal for a new Project.  Duke ET evaluates these proposals on a case-by-case basis and specific connection requirements are provided accordingly.  Physical laws that govern the behavior of electric systems do not recognize boundaries of electric facility ownership.  Thus, to properly design a connection, the electric systems must be studied and analyzed without regard to ownership. Duke ET will study any proposed connection to its system using existing and forecasted system data and data supplied by the Project Sponsor.  In these studies, Duke ET considers short-circuit duties, transient voltages, reactive power requirements, stability requirements, harmonics, safety, operations, maintenance and Prudent Electric Utility Practices.  Duke ET will develop connection proposals for review with the Project Sponsor.

This document is not intended as a design specification or an instruction manual.  Technical requirements stated herein are intended to be consistent with North American Electric Reliability Council (NERC) and Southeastern Electric Reliability Council (SERC) planning and operating policies, principles, practices, and standards.  Compliance with NERC standards is expected and nothing in this document relieves the Project Sponsor of the industry expectation to meet them. The information presented in this document is subject to change.

# DEFINITIONS

Important terms used in this document are capitalized and italicized (e.g. Project, Project Sponsor, Connection Point) and defined in this Section.

For industry standard definitions of electric industry terminology, please refer to:

The New IEEE Standard Dictionary of Electrical and Electronic Terms, IEEE Std 100-1992.

For the purposes of this document the following definitions apply:

Absolute Voltage Limits - The upper and lower voltage operating limits of each bus on the system.  The absolute voltage limits are expressed as a percent of Duke’s nominal voltage.  The system is managed such that all voltages should be maintained within the appropriate absolute voltage bounds for all conditions.

Bulk System - The portion of the Duke Electric Transmission System used for transferring large amounts of power and includes all 500-kV lines, 500-kV substations, 500/230-kV transformers, and 230-kV lines.

Connection Point - The physical location on the power system of the change of ownership between Duke ET and the Project or Interconnecting Utility.

Connection Review – The review of a Project proposal to connect to the transmission system.  This includes all studies required by the Tariff along with verification that all technical requirements in this document are properly addressed.

Contingency Voltage Drop - The decrease in voltage due to a single contingency.

Customer Equivalent – Power Delivery Asset Management methodology used to normalize customers of unequal size. Customers are converted to “customer equivalents”.  For large customers, divide the peak KWD by 5 KW.

Duke Electric Transmission (Duke ET) – Business unit responsible for the planning and operation of the Duke Electric Transmission System.

Duke Electric Transmission System (Duke ET System) - The integrated electrical transmission facilities owned by Duke Energy including primarily 500-kV, 230-kV, 100-kV, and 44-kV lines and stations.

Effectively Grounded - A system that provides an X0/X1<3 & R0/X1<1 where X0 and R0 are zero sequence reactance and resistance, and X1 is positive sequence reactance.

Equivalent Fault – A fault of sufficient magnitude and duration to trip a utility owned line or circuit protective device, whether such a protective device exists or not.

Incapacitating Disturbance – For a customer, a power problem equivalent in effect and severity to a sustained outage, and not limited to equipment malfunctions (e.g. severe “flicker” disturbs humans, not machines).  Typical examples are sustained outages, momentary interruptions, and severe voltage sags. These disturbances must be shown to cause the customers a problem.

Infeed – Contribution from a positive or zero sequence source, a transformer or generator, to a fault.

# Interconnection – Transmission system tie point between two control areas.

Joint Use Breaker Agreement – Legal document specifying details between Duke ET and a Project Operator regarding the operation and control of equipment (e.g., circuit breaker) that is accessible to both parties.

Interconnecting Utility - The utility that owns the transmission or distribution system that connects the Project to the Duke Electric Transmission System at the Connection Point.

MAIFI - refers to the average number of momentary interruptions per year.

Momentary interruptions – Outages, zero voltage, lasting 1 minute or less.

# NERC - North American Electric Reliability Council and its successors

Planning Standards - Duke Electric Transmission Planning Guidelines document, which is part of Duke’s annual FERC 715 filing, the SERC Planning Principles and Guides, or the NERC Planning Standards.

Project - The load delivery, Interconnection, or generation facility and all equipment associated with integration of the Project up to the Connection Point with Duke Electric Transmission System.  None of the facilities that make up the Project are owned by Duke Electric Transmission.

Project Operator - The company that operates a load delivery, Interconnection, or generation facility.

Project Sponsor - A company that owns and/or develops a new load delivery, Interconnection or generation facility.

Protection Station - Facility that satisfies the requirements necessary to provide complete protection for the Project immediately beyond the Connection Point.

Prudent Electric Utility Practices or Prudent Utility Practice - The generally accepted design, practices, methods, and operation of a power system, to achieve safety, dependability, efficiency, and economy, and to meet utility and industry codes, standards, and regulations.

Reliability and Integrity – Aspects of the transmission system that affects the customer outage experience and concerns the safe maintenance of utility assets, in good working condition, at the lowest overall cost while preserving corporate reputation.

SAIFI - The average number of sustained interruptions per customer per year.

SCADA (Supervisory Control and Data Acquisition) - A system of remote control and telemetry used to monitor and control the transmission system.

# SERC - Southeastern Electric Reliability Council

Station Service - The electric supply for the ancillary equipment used to operate a generating station or substation.

SOC – Duke Energy’s System Operating Center located in Charlotte, NC responsible for generator dispatch and control area monitoring.

Sustained Outages - Outages, zero voltage, lasting for more than 1 minute.

# TCC – Duke Energy’s Transmission Control Center located in Charlotte, NC.

Voltage Regulation - The difference between expected maximum and minimum voltages at any particular delivery point.  The voltage regulation limits are expressed as a percent of the nominal voltage and are defined for both normal and contingency conditions.  Voltage regulation for delivery point voltages should not exceed the guidelines.

Voltage Unbalance - The percent deviation of one phase rms voltage value from the average of all three phases’ rms voltage values.

# FACILITY CONNECTION REQUIREMENTS – LOAD DELIVERIES

## Scope

The technical requirements contained herein generally apply to all load deliveries connected to the Duke ET System except those noted in the Introduction.  The location of the delivery and the impacts on the Duke ET System, or another utility’s system, determine the specific requirements.  The Project must not degrade the safe operation, integrity, or reliability of the Duke ET System.

- Applicable Codes, Standards, Criteria and Regulations

To the extent that the Codes, Standards, Criteria and Regulations are applicable, the Project shall be in compliance with those listed in the References section of this document and others that are applicable.

- Safety, Protection, and Reliability

Duke ET, after consultation with the Project Sponsor and other relevant parties, shall make the sole and final determination as to whether the Duke ET System is properly protected from any problems that the Project might cause before a connection is closed.  The Project Sponsor is responsible for correcting such problems before connected operation begins.  The Project Sponsor is responsible for safety, protection, and reliability on the Project side of the Connection Point.

- Non-Duke ET Responsibilities

Project Sponsors and Project Operators shall comply with NERC Planning Standards and Operating Policies.  The Project Sponsor is responsible for the planning, design, construction, reliability, protection, and safe operation of non-Duke ET System-owned facilities.  This will normally require the Project to include a Protection Station immediately beyond the Connection Point.  The design and operation of the Project is subject to applicable local, state and federal statutes and regulations.

- Cost of Connection Reviews

The Project Sponsor requesting Duke ET to perform a Connection Review will reimburse Duke ET for its actual costs to perform the study.  This includes costs associated with verifying that all technical requirements in this document are properly addressed.

## Connection and System Impact Studies and Project Sponsor-Supplied Information

Project Sponsors should contact Duke Electric Transmission as early as possible in the planning process for any potential new or modified load connection to the Duke ET System.  The Project Sponsor should not make its own assumptions about the final location, voltage, or connection requirements.  Certain areas within the Duke ET System can accept only limited amounts of additional load without costly reinforcements.  Duke ET  may have to add to or modify its transmission system substantially before connecting a new Project.  A Connection Review must be performed to determine the required connection facilities and modifications to accommodate the Project.  This study may also address the transmission system capability, transient stability, voltage stability, losses, voltage regulation, harmonics, voltage flicker, electromagnetic transients, ferroresonance, metering requirements, protective relaying, substation grounding, and fault duties.  If necessary, joint study with neighboring control areas may be performed to assess the impact of the Project.  The data that the Project Sponsor is required to provide to enable the completion of these studies is listed in the Project Sponsor Supplied Information section.

Part of the Connection Review will include a high level review of the design, construction, maintenance, and operation rules and standards that will be used before and after connection is made to the Duke ET System.  If any portions of this review need further investigation or justification to prove all facility connection requirements will be met, it will be the responsibility of the Project Sponsor to provide the necessary information to illustrate the justification or provide an alternative solution to meet the facility connection requirements.  This high level review is intended to identify moderate to major discrepancies and the Project Sponsor remains responsible for meeting the facility connection requirements before and after connection is made to the Duke ET System regardless of the results of the Connection Review.

### Connection Configuration

Projects may be connected to the Duke ET System by tapping an existing transmission line(s) or by connecting directly into an existing transmission station.  In rare instances, a new transmission switching station may be built in the middle of an existing transmission line.  Load deliveries are almost always connected to Duke ET System’s 100-kV and 44-kV transmission systems.  Duke ET System’s 500-kV and 230-kV transmission systems are typically reserved for the bulk transport of large amounts of electricity.

The number of available connection options is dependent upon many factors, including location of the desired Connection Point relative to existing Duke ET System transmission facilities, the size of the Project’s load, and other requirements of the Project.  The most feasible option(s) will be considered in the Connection Review, with the most economic option meeting all requirements being selected.

### Power Flow

The Project is incorporated into power flow models by Duke ET using the data provided by the Project Sponsor.  Power flow simulations are performed to determine the impact of the Project on the transmission system.  The primary intent is to determine if the new load causes any violations of the Duke Electric Transmission Planning Guidelines (Planning Guidelines), which is part of Duke’s annual FERC 715 filing, the SERC Planning Principles and Guides, or the NERC Planning Standards (collectively, Planning Standards).  A summary of these guidelines is provided below:

#### Thermal and Voltage Screening

The purpose of this study is to ensure that the connection of the Project does not create any thermal loadings or voltage levels outside of the limits provided in the Planning Guidelines.  Project information obtained from the Project Sponsor is used to model the Project.  Power system simulation tools are used to model a wide range of transmission system operating conditions to determine the thermal loading and voltage level changes created by the Project on the Duke ET System.

#### Transfer Capability

The purpose of this study is to ensure that the connection of the Project does not reduce any Transfer Capabilities below limits provided in the Planning Guidelines.  Power transfers are simulated across the Duke Electric Transmission System in various directions to determine how the Project affects Duke ET System’s ability to transfer power across its system.

### Protection

After studying the possible ways to connect the Project to the Duke ET System, the protective requirements will be determined.  This will include an impedance model at the Connection Point (short-circuit data), protective changes to the transmission system, protective requirements for the delivery and any special protective needs for the Project.  See the General Requirements and Protection Requirements sections for more details on these requirements.

### Power Quality and Reliability

There is a very diverse set of users connected to the Duke ET System with differing system requirements.  In the past, most customers were only concerned with extended interruptions.  However, the increased use of highly sensitive power electronic devices within all customer sectors has changed the definition of reliability.  Due to the sensitivity of many industrial and commercial loads such as adjustable speed drives (ASDs) and computer controlled processes, reliability is no longer only defined by the frequency and duration of sustained interruptions.  There are many power quality variations other than sustained interruptions that may constitute inadequate service for the proper operation of customer equipment.  Variations such as Voltage Unbalance, voltage flicker, harmonic distortion, transient overvoltages, temporary overvoltages and steady-state voltage regulation can adversely affect customer processes.

The challenge for the transmission owner is to design and operate the transmission system such that it meets the requirements of this diverse set of users.  To meet this challenge, Duke Electric Transmission performs studies to determine the power quality and reliability impacts of any new Project on the Duke ET System at the Connection Point.  The intent of these studies is to ensure that the connection of the Project does not compromise the reliability and integrity of the Duke ET System.

The studies performed for each new Project may include:

#### Voltage Unbalance

The purpose of this study is to ensure that the operation of any new Project does not create a Voltage Unbalance condition in excess of the limits provided in the Performance Requirements section.  Project information obtained from the Project Sponsor is added to the power system model.  Using power system simulation tools, studies are performed over a wide range of transmission system operating conditions to determine the range of Voltage Unbalance created by the Project at the Connection Point.

#### Voltage Flicker

The purpose of this study is to ensure that the operation of any new Project does not create voltage fluctuations in excess of the limits provided in the Performance Requirements section.  Project information obtained from the Project Sponsor is added to the power system model.  Using power system simulation tools, studies are performed over a wide range of transmission system operating conditions to determine the range of voltage fluctuations created by the Project at the Connection Point.

#### Harmonic Distortion

The purpose of this study is to ensure that the operation of any new Project does not create harmonic current injections in excess of the limits provided in the Performance Requirements section.  Project information obtained from the Project Sponsor is added to the power system model.  Using power system simulation tools, studies are performed over a wide range of transmission system operating conditions to determine the range of harmonic distortion created by the Project at the Connection Point.

#### Transient Overvoltage

The purpose of this study is to ensure that the operation of any new Project does not create a transient overvoltage condition in excess of the limits provided in the Performance Requirements section.  Project information obtained from the Project Sponsor is added to the power system model.  Using power system simulation tools, studies are performed over a wide range of transmission system operating conditions to determine the range of transient overvoltages created by the Project at the Connection Point.

#### Temporary Overvoltage

The purpose of this study is to ensure that the operation of any new Project does not create a temporary overvoltage condition in excess of the limits provided in the Performance Requirements section.  Project information obtained from the Project Sponsor is added to the power system model.  Using power system simulation tools, studies are performed over a wide range of transmission system operating conditions to determine the range of temporary overvoltages created by the Project at the Connection Point.

#### Temporary Undervoltage

The purpose of this study is to ensure that the operation of any new Project does not create a temporary undervoltage condition in excess of the limits provided in the Performance Requirements section.  Project information obtained from the Project Sponsor is added to the power system model.  Using power system simulation tools, studies are performed over a wide range of transmission system operating conditions to determine the range of temporary undervoltages created by the Project at the Connection Point.

#### Insulation Coordination

The purpose of this study is to ensure that the operation of any new Project does not create a condition that will require intervention of Duke ET System-owned transmission equipment in excess of the limits provided in the Performance Requirements section.

### Changes to Project Sponsor-Supplied Information

If any data previously supplied pursuant to these connection requirements  changes, the Project Sponsors or Project Operator will notify Duke ET in writing without delay.  Data changes may require additional studies to examine the impact.  This notification will include:

- the time and date at which the change became, or is expected to become, effective

- if the change is only temporary, an estimate of the time and date at which the data will revert to the previously supplied form.

A request for a change in Connection Point to the Duke ET System must be submitted as a new request.  A new completion date will be negotiated with the Project Sponsor or Project Operator when Project data is changed.

Duke ET will request load growth projections after the initial connection is made.  This will require an annual submittal for the Project detailing the load projections for each of the next 5 years.

### Required Project Sponsor-Supplied Information

Any Project Sponsor desiring a new connection or modification of an existing connection must provide the following information:

- Facility name and contact name

- Address

- Phone number, fax number, e-mail address of contact name

- Effective date of new connection or modification

- Proposed location of Project

- One-line diagram of Project

- Preferred supply voltage

- Load demand under normal and emergency conditions

- Power factor

- Expansion plans (type and size of potential loads)

- Transmission line voltage, conductor rating, impedance, length, insulation, grounding, etc.

- Transformer ratings, connections, voltage taps, impedances, and grounding

- Lightning protection designs for transmission lines and stations

- Special requirements (e.g. sensitive equipment, dual feeds, etc.)

- Preferred method of connection (series, automatic high side swapover, etc.)

- Relay schemes, relay settings, protection equipment

- Maintenance schedules and procedures

For industrial plants served directly from the Duke ET System, or for load serving entities serving large industrial plants close to the Duke ET System, the following additional information is needed:

- One-line diagram of plant distribution system and loads

- Power factor correction capacitors size, connection, and control scheme

- In-plant switchgear and protective device information

- Motor application/loads, rate horsepower, rated voltage, type (synchronous, induction), starting frequency, full load current, locked rotor current, power factor, efficiency, starting time (starting current versus time curves), etc.

- Method of motor starting

- Size, location, and characteristics of single-phase loads

- Size, location, and characteristics of large fluctuating loads (arc furnaces, welders, etc.)

- Size, location, and characteristics of harmonic producing loads (variable speed drives, induction furnaces, etc.)

- Size, method of operation, and location of on-site generation

- Size, location, and characteristics of power conditioning equipment

## General Requirements

### Safety

All safety and operating procedures for joint use equipment shall be in compliance with the Occupational Safety and Health Administration (OSHA) standard 29 CFR 1910.269, the National Electrical Safety Code (NESC), the Duke Power Safe Work Practices Manual, the Duke Electric Transmission Operating Procedures Manual and the Project Sponsor’s safety manuals.

#### Isolation Requirements

The Project Operator shall not energize any Duke ET System line or equipment unless the Duke Transmission Control Center (TCC) specifically approves energization.  If, for any reason, a protective device operation separates the Project from the Duke ET System, the Project Operator will contact the Duke TCC before attempting to restore the connection to the Duke ET System.

At the Connection Point with the Duke ET System, a disconnect switch shall be provided for the purpose of physically and visibly isolating the Project from the Duke ET System.  With the consent of Duke ET and the Project Sponsor, the disconnect switch may be installed at another location, other than the Connection Point, provided that the purpose described herein is satisfied. The device:

- Must be accessible by Duke ET and under Duke TCC jurisdiction.

- If gang-operated, must be lockable in the open position by Duke ET.

- Must be suitable for safe operation under the conditions of use.

- Would not be operated without advance notice to either party, unless an emergency condition requires that the device be opened to isolate the Project.

Duke ET personnel may open the switch:

- If it is necessary for the protection of Duke ET maintenance crew personnel when working on de-energized circuits.

- If the Project or Duke ET System equipment presents a hazardous condition.

Consideration shall be given as to the design and capacity of the switch on a case-by-case basis.  The switch is required for safety and may not be required to interrupt load or energization (charging) current.  However, a suitable switch for the safety requirements herein described may also be used to provide for other operational purposes.

#### Generation Served by the Project

The Project Sponsor shall maintain a record of all generation customers served by the Project and such record shall be made available to Duke ET.  For the requirements of energized line maintenance or line construction on the Duke ET System, the Project Sponsor will ensure that all generation customers served by the Project will disconnect their generation upon request by Duke ET.

### Connection Point Considerations

#### Protection and Monitoring of the Project

The Project Sponsor and/or Project Operator are responsible for protecting the Project from fault conditions and other undesirable conditions (e.g., single phasing).  The Project Sponsor must demonstrate that the entire Project is protected from fault conditions before connection will be made.  This includes providing adequate protection for any transmission line sections that are part of the Project.  The Project Sponsor and/or Project Operator will also be responsible for monitoring the Project to demonstrate that the Project performance criteria are being met.  A Protection Station at the Connection Point is a common prerequisite to meet these requirements.

The Project Sponsor may arrange alternate arrangements with the transmission provider to provide protection for portions of the Project although the responsibility is still with the Project Sponsor to provide protection.  However, monitoring is required to measure performance at the Connection Point.  Although “low-side” meters may be used to help calculate parameters at the Connection Point such as power factor and voltage flicker, they can not indicate items such as faults on the source side of the meters or temporary undervoltages at the Connection Point.  The Project Sponsor is encouraged to meet these requirements using any means necessary although at this point in time, a Protection Station appears to be a prerequisite to meeting both the protection and monitoring requirements set forth in these facility connection requirements.

#### General Configurations and Constraints

Integration of Projects into the Duke ET System usually falls into one of two categories:

1)  Connection into a 44-kV or 100-kV substation, with (depending on the bus configuration) the transmission lines terminated into one or more breakers.  Switching station buses are either double-bus or breaker-and-a-half arrangements.  Connection at voltages below 44-kV are not usually considered part of the transmission system, even at stations that have voltages of 44-kV or higher.

2)  Connection at 44-kV or 100-kV by tapping a transmission line.  This tap may be as simple as tying hard and fast to the conductor where isolating switches are immediately adjacent in the substation, or may be as complex as requiring a new switching station in the transmission line.

#### Special Configurations and Constraints

The constraints and considerations described below may substantially affect the costs of a particular integration plan, sometimes making an alternate Connection Point for the Project more desirable.

##### Connection to the Bulk System

Duke Power’s transmission system may be separated by function into two main parts: the Bulk System (230 kV and 500 kV networks) and the Regional System (44 kV, 66 kV, 100, and 161 kV networks).  Each part of the transmission system plays an important role in the delivery of energy from generators to end-users.  The Regional System is a group of electric transmission lines and tie-stations whose primary function is the distribution of energy to large industrial and large commercial customers and to retail stations in its geographical area.  The Bulk System is a highly inter-connected group of high-voltage electric transmission lines and tie-stations whose purpose is to enable the movement or transfer of electric energy in bulk between generators and major points of delivery.  To accomplish this function effectively, the Bulk System has been designed and built to maintain the integrity and security of the interconnected generation and transmission network.  The following list describes some of the major functional and design differences of the Bulk System compared to the Regional System:  the Bulk System provides the primary means for bulk energy transfer across the SERC Region supporting Eastern Interconnection reliability, allows energy from dispersed generation to be moved over large geographical areas supporting economic dispatch and reliable system operation during generation contingencies; allows bulk energy to be transported with lower line losses reducing the overall cost of energy;  and, the much reduced number of taps and stations on the Bulk System lowers exposure to faults and equipment failures, resulting in fewer disturbances that adversely impact generation reliability.  As a result of the function of the Bulk System, individual load connections to transmission lines are not allowed because of the overall detrimental affect on system reliability.

##### Connection to 100- and 44-kV Lines

Most Projects are connected to the Duke ET System with a Connection Point at one of these voltages.  A radial extension of the line can be provided to reach the Project.  Some lines have two circuits available from a double-bussed substation arrangement such that several special service arrangements are available at additional cost.  Almost all 44-kV lines are operated radially without this option available.

##### Connection to Network Lines

Duke ET will own and operate any equipment in series with a transmission line that is part of the Duke ET System.  Therefore, any equipment that is required for connection of a Project that will be in series with a transmission line will be owned and operated by Duke ET.  This includes radial sections of transmission lines that carry load for more than one Connection Point.

##### Multi-Terminal Lines

A multi-terminal line can be defined as a customer connection that could back feed to a Duke transmission line.  The sources could be generators, connections to other parts of the power system, or ground sources (e.g., transformers connected grounded-wye at the connection voltage).  These types of terminals affect Duke ET’s ability to protect, operate, dispatch, and maintain the transmission line.  The increased complexity of the control and protection schemes affects system stability and reliability.  Duke ET determines the feasibility of multi-terminal line connections on a case-by-case basis, often relying on the results of Connection Studies.  If such a connection would have an unacceptable impact on the Duke ET System, a substation at the transmission voltage level would need to be developed.

#### Other Considerations

Below are some of the other issues considered when evaluating Project proposals:

##### Equipment

Existing electrical equipment, such as transformers, power circuit breakers, disconnect switches, and line conductors were purchased based on existing and forecast system conditions.  However, with the connection of new loads, some equipment may become overloaded and need to be replaced.  All equipment purchased by Duke ET and the Project Sponsor as part of the Project must meet the applicable NESC and all appropriate IEEE standards for equipment testing and application.  Duke ET reserves the right to review and set forth requirements for the specification and application of all equipment used in the Project that could impact the Performance Requirements for the Project.

##### System Stability and Reliability

The Duke ET System has been developed with careful consideration for system stability and reliability during disturbances.  The size of the Project, equipment configurations, and the ability to set protective relays will affect where and how the Connection Point is made.  The Project may also be required to participate in special protection schemes.

##### Control and Protection

Duke ET coordinates its protective relays and control schemes to provide for personnel safety and equipment protection and to minimize disruption of services during disturbances.  Project connection usually requires the addition or modification of protective relays and/or control schemes.  This may also include the use of communication channels to provide protection for tap lines, dual customer feeds, generation or other special requirements of the customers. New Projects must be compatible with existing protective relay schemes. Duke ET System uses a pilot tripping scheme on all 500-kV, 230-kV lines and some 100-kV lines.  A conventional zone protection is usually used at 100-kV and below.  The Project shall not provide a ground source at any voltage level unless specifically approved and coordinated with Duke ET.

##### Protection Stations

A major purpose of the Protection Station is to provide the primary protection requirements for the Project.  Protection Stations must provide adequate protection to all of the Project facilities as stated in the Protection Requirements section without relying on any Duke ET System protective devices to provide primary protection beyond the Connection Point.  The other purposes of the Protection Station include preventing Duke ET System facilities from being interrupted for faults within the Project, controlling reclosing practices when testing lines, monitoring equipment for Performance Requirements, and metering requirements.  It is possible that Duke ET, or another company, will provide and operate the Protection Station for the Project Sponsor.  The Sponsor will be held responsible for its design, construction, testing, maintenance, operation, and all associated costs with these activities.

Duke ET reserves the right to review and set forth requirements for the specification and coordination of the Protection Station.  These stations must be designed such that the Project Operator and Duke Electric Transmission can have access to and control of the station.  A Joint Use Breaker Agreement, or similar agreement, will be developed to allow Duke ET to operate and control this station under certain specified conditions.  Duke ET may modify the reclosing requirements after connection is made if the Project fails to meet any of the provisions in the Performance Requirements section of this document.  Duke ET may also require a dedicated set of current transformers that can be used by Duke ET to set relays to monitor and control the Protection Station if any of the provisions in the Performance Requirements are not met.

Duke ET reserves the right to require protective stations at any Connection Point before or after initial connection is made to the Duke ET System.  Duke ET may install its own Protection Station, at the Project Sponsor’s expense, if the provisions in the Performance Requirements section are violated on a regular basis.

##### Phase Orientation

Duke ET uses a phase rotation of ZYX (phase "Z" voltage leads phase "Y" voltage by 120 degrees).  It is important that the Project Sponsor and Project Operator understand this phase sequence and coordinate with Duke ET before connection is made to ensure intended phase rotation is achieved.  Duke ET can typically provide the phase sequence desired by the project sponsor at 100kV, however there may be limitations in a given Project.  Duke ET cannot guarantee a requested phase sequence connection until each connection request is reviewed in detail.  Duke ET will not typically "roll phases" at the Connection Point for a Project unless Duke ET did not provide adequate or accurate information regarding the phase sequence to be provided at the Connection Point.

##### Outage Coordination & Maintenance

Duke ET operates and maintains its system to provide reliable customer service while meeting the seasonal and daily peak loads even during equipment outages and disturbances.  Project integration requires that the equipment at the Project not restrict timely outage coordination, automatic switching or equipment maintenance scheduling.  Preserving reliable service to all Duke ET System customers is essential and may require additional switchgear, equipment redundancy, or bypass capabilities at the Project for acceptable operation of the Duke ET System.

##### Atmospheric & Seismic

The effects resulting from wind storms, floods, lightning, altitude, temperature extremes, and earthquakes must be considered in the design and operation of the Project.  The Project Sponsor is responsible for determining that the appropriate standards are met, including, but not limited to, the Uniform Building Code (UBC) and the National Electrical Safety Code (NESC).  Depending on Project location, size, type, and importance, Duke ET may request that additional capabilities be designed into the Project.  Lightning is one of the most predominant causes of transmission line outages in the Duke ET System service area and can be mitigated with proper design and grounding improvements.  The Project Sponsor is expected to design its power system to withstand reasonable lightning activity as is typical to the area in which it will be installed and still meet the Performance Requirements for the Project.

### Substation Grounding

Each generation site and/or connecting substation must have a ground grid that solidly grounds all metallic structures and other non-energized metallic equipment.  This grid shall limit the ground potential gradients to such voltage and current levels that will not endanger the safety of people or damage equipment which are in, or immediately adjacent to, the station under normal and fault conditions.

If the Project is physically close to another substation, it is recommended that the two ground grids be connected.  The interconnecting cables must have sufficient capacity to handle fault currents and control ground grid voltage rises.  Duke ET must approve any connection to a Duke substation ground grid.  If the ground grids must be isolated for operational reasons, there must be no metallic ground connections between the two substation ground grids.  Cable shields, cable sheaths, station service ground sheaths, and overhead transmission shield wires can all inadvertently connect ground grids.  Fiber-optic cables are an  excellent choice for telecommunications and control between two substations to maintain isolated ground grids. In the case where the Project is physically close to another substation but the ground grids are isolated, the Project Sponsor must demonstrate that the ground grids are properly isolated and in compliance with all applicable codes and standards.  Duke ET prefers to connect static wires on incoming transmission lines to the station ground grid.  If the Project Sponsor prefers not to connect static wires on incoming transmission lines to the station ground grid; the Project Sponsor must notify Duke ET in writing and demonstrate that relay performance, lightning protection, and personnel safety are not compromised by isolating the static wires from the station ground grid.

The Project ground grid should be designed to ANSI/IEEE Std. 80-1986, IEEE Guide for Safety in AC Substation Grounding, and should be measured in accordance with IEEE - 81 Part 1: Guide for Measuring Earth Resistivity, Ground Impedance, and Earth Potentials and Part 2: Measurement of Impedance and Safety Characteristics of Large, Extended or Interconnected Grounding Systems.  Project grounding requirements shall also comply with the National Electrical Safety Code, ANSI/IEEE - 665 Guide for Generating Station Grounding, IEEE - 837 Standard for Qualifying Permanent Connections Used in Substation Grounding, IEEE - 487 Protection of Wire-Line Communication Serving Electric Power Stations, ANSI/IEEE 367-1987 IEEE Recommended Practice for Determining the Electric Power Station Ground Potential Rise and Induced Voltage from a Power Fault, and any applicable state and local codes.

### Insulation Coordination

Power system equipment is designed to withstand voltage stresses associated with expected operation.  Connection Reviews include the evaluation of the impact of the Project on equipment insulation coordination.  Duke ET identifies additions required to maintain an acceptable level of Duke ET System availability, reliability, equipment insulation margins, and safety.

Voltage stresses such as lightning surges, switching surges, temporary overvoltages, and normal 60Hz voltages may affect equipment duty.  Remedies depend on the equipment capability and the type and magnitude of the stress.  Below are the requirements that must be met to connect to the Duke ET System.  In general, stations shall be protected against lightning and switching surges.  Typically this includes station shielding against direct lightning strokes, surge arresters on all wound devices, and shielding on the incoming lines.

#### Lightning Surges

Lightning is the single largest cause of transmission line events in the Duke ET System service area and must be considered during the design and installations of transmission lines and substations.  Lightning related causes are not exempt from the requirements in the Performance Requirements section.  Although it is not always cost effective to design and build a power system to withstand every possible lightning stroke, it has been demonstrated that with proper design and installation procedures, the effects of lightning can be mitigated to achieve a reliability level equal to or exceeding the Project performance criteria defined in the Performance Requirements section.  Techniques used to help control lightning related events on transmission lines include proper use of shield wires, insulation levels, low resistance grounding, and surge arresters.  Techniques used to help control lightning related outages in substations include substation shielding, proper arrester applications, and shielding of incoming transmission lines.

If the Project proposes to tap a Duke transmission line that is shielded, the new tap line must also be properly shielded for at least one mile from the Duke ET System.  If any stations are within one mile of the Duke ET System, these also must be properly shielded from direct lightning strokes.  The Project Sponsor must be able to demonstrate proposed designs for any transmission lines and substations will perform within the limits for service interruptions as stated in the Performance Requirements section.

For transmission line design, an industry recognized lightning performance estimating algorithm may be used to demonstrate acceptable performance of the design.  The Project Sponsor must make reasonable assumptions based on the area that the transmission line will be installed including ground flash density and grounding conditions.  The Project Sponsor must be able to provide an alternative plan if the ground conditions required for acceptable performance are not achieved during construction of the transmission line.

For substation design, the Project Sponsor must be able to demonstrate their proposed designs will operate within the performance requirements.  The shielding designs and arrester applications shall adhere to applicable IEEE standards.  In addition, any normally open points that are subject to voltage “doubling” of incoming lightning surges must be considered and protected accordingly so the Performance Requirements are not violated.

#### Switching Surges

At voltages below 500-kV, modifications to protect the Duke ET System against Project-generated switching surges are not anticipated although the Connection Review identifies the actual needs.  At 500-kV, Duke ET may require that arresters be added at the line terminations of the substations if switching surge studies predict overvoltages that may otherwise cause a flashover at the Project’s facilities.

#### Temporary Overvoltages

Temporary overvoltages can last from cycles to minutes, and are not characterized as surges.  These overvoltages are usually present during faults and other abnormal system conditions.  The Duke ET System is typically considered Effectively Grounded at 100-kV and higher voltages.  However, the 44-kV system is not Effectively Grounded in all locations.  These systems may be impedance grounded and can have line to ground voltages approaching 1.73 times normal line to ground voltage during fault conditions on unfaulted phases.  It is not acceptable for the Project to supply any ground source for the transmission system unless specifically approved and coordinated with Duke ET.

A system study may be performed for each Project based on the point on the Duke ET System that is being connected.  The Project Sponsor will be supplied the system characteristics needed to calculate the temporary overvoltages that need to be considered.  Gapless metal-oxide surge arresters are especially sensitive to system temporary overvoltages and Duke ET may review the specification of arresters used on 44-kV systems to ensure proper application.

#### Normal Operating Voltages

The Duke ET System voltages are normally operated within the limits specified in the Performance Requirements section of this document.  Insulation Coordination usually does not need to consider this operating range once lightning and switching surge requirements are met; however, in highly contaminated areas, special consideration and additional insulation requirements may be required for proper insulation coordination.  The Project Sponsor is responsible for determining whether special insulation requirements are needed for its system.

### Inspection, Testing, Calibration and Maintenance

The Project Sponsor and Project Operator have full responsibility for the inspection, testing, calibration and maintenance of its equipment, up to the Connection Point, consistent with the power purchase, operating agreement or connection agreement.  Maintenance activities must be coordinated with the Project and TCC and/or SOC to ensure the Duke ET System is not adversely affected.

#### Preenergization Inspection and Testing

Before initial Project energization, the Project Sponsor or Project Operator shall develop an Inspection and Test Plan for preenergization and energization testing. This plan should include provisions for testing protective equipment that comply with the NERC Planning Standards, Section III A, Guide G9.  Duke ET will review and must approve the test plan prior to the test.  Duke ET may require additional tests; the costs of these tests are subject to negotiation.  The Sponsor shall make available to Duke ET all drawings, specifications, and test records of the Project equipment pertinent to connected operation.

#### Calibration and Maintenance

##### Revenue Metering

Revenue metering shall be tested and calibrated if necessary at least every two years.  More frequent test intervals may be negotiated.  All interested parties or their representatives may witness the calibration tests.  Calibration records shall be made available to all interested parties.  The Metering and Telecommunication Requirements section should be reviewed for further details.

##### All other equipment

The Project Sponsor or Project Operator shall implement a preventive maintenance program for the Project equipment.  The program shall be designed and executed in a manner to ensure the proper operation of the Project equipment. The program may be based on time or on other factors, including performance levels or reliability.  Appropriate equipment performance data will be collected and maintained by the Project Sponsor or Project Operator.  Duke ET reserves the right to review the preventive maintenance program for the Project.  Maintenance records of the Project equipment pertinent to connected operation shall be made available to Duke ET upon request.

### Station Service

Power provided for local use at a substation to operate lighting, heat and auxiliary equipment is termed Station Service and will be required at all Protection Stations.  Appropriate providers of Station Service are determined during the Project planning process.  Generally, the utility with a distribution service in the area will be the preferred provider of Station Service.  The Project Sponsor may need to provide metering for Station Service depending on the provider of Station Service.

Alternate Station Service is a backup source of power used only in emergency situations or during maintenance when primary Station Service is not available.  Alternate Station Service is usually only used in large stations.

## Performance Requirements

All Projects must be properly designed, constructed, operated, and maintained to avoid degrading the reliability of the Duke ET System.  A Project must comply with the Project performance criteria, listed below, and must be able to operate satisfactorily within the limits defined in the Duke ET System Characteristics section, below, in order to be considered properly connected.  The Project Sponsor or Project Operator is expected to demonstrate, through monitoring, that the Project meets the Performance Criteria.  It is required that the criteria of Sections 1.a, 1.b, and 1.c (below) be monitored.  The remaining criteria must be met and considered in the design and operation of the Project although these do not necessarily have to be monitored.  However, if problems are suspected at any time, Duke ET may require the Project Sponsor and/or Project Operator to demonstrate through monitoring the performance of the Project at the Connection Point meets these requirements.

If the requirements are not met, the Project Sponsor or Project Operator must demonstrate to Duke ET a plan to improve and meet the performance criteria.  Relay and control requirements may be developed and enforced by Duke ET after connection is made if these performance criteria are violated.  Enforcement of these performance criteria and penalties associated with them are beyond the scope of this document and will be in Project-specific contracts and operating agreements.

### Project Performance Criteria

To ensure the reliability and integrity of the supply system, all Projects must meet the Project performance criteria at the Connection Point.  The following section details the Project performance criteria.

#### Power Factor

Projects that serve primarily distribution load (retail stations, wholesale customers, etc.) must comply with the following power factor requirements measured at, or compensated to, the Connection Point:

Peak Periods - The Project must operate its electrical system in a manner resulting in a power factor not less than 96.5% lagging at the hour of transmission system peak load on an annual basis.

Valley Periods - The Project must operate its electrical system in a manner not resulting in a leading power factor at the hour of transmission system valley load on an annual basis.

#### Transmission System Interruptions

For Connection Points at 100kV and below, the Project shall not cause an interruption to any portion of the Duke ET System more than once in a 12-month period, more than three times in a five-year period, or more than five times in a ten year period.  For Connection Points at voltages higher than 100kV, requirements will be determined on a case-by-case basis.  An interruption is defined as a voltage zero condition lasting greater than 20 milliseconds.  Interruptions occurring within one minute of each other will be considered the same event.  Exemptions are not typically given, even for lightning or other weather related causes.  A Project is in violation of the Project performance criteria if these requirements are not met.

#### Temporary Undervoltages

For Connection Points at 100kV and below, the Project may not cause a temporary undervoltage at the Connection Point more than two times in a 12-month period, more than five times in a five-year period, or more than eight times in a ten year period.  For Connection Points at voltages higher than 100kV, requirements will be determined on a case-by-case basis.  A temporary undervoltage is defined as an oscillatory phase-to-ground or phase-to-phase voltage of 85% or less of nominal voltage lasting greater than 20 milliseconds occurring during fault conditions.  Undervoltages due to non-fault events are covered in the voltage flicker requirements.  Temporary undervoltages occurring within one minute of each other will be considered the same event.  A Project is in violation of the Project performance criteria if these requirements are not met.

#### Voltage Flicker

Per IEEE Standard 1453-2004, planning levels of Pst=0.8 and Plt=0.6 define the allowable voltage fluctuation limits at the Connection Point.  In unique cases, higher limits can be considered with the understanding that the customer operating the disturbing load will be required to mitigate the flicker that they cause, if significant customer complaints are generated.  Additionally, any single customer that creates disturbances for other customers will be required to mitigate the disturbance, regardless of the actual measured value.

Operation of the system or equipment in such a manner as to create a voltage fluctuation greater than 3% on the transmission system or on the primary of the distribution system is not allowed.

#### Harmonic Content/Harmonic Distortion

The maximum allowable harmonic current injections (percentage harmonic distortion at each frequency as a function of maximum load current) at the Connection Point for Projects connected at 230-kV or 500-kV, 100-kV, and 44-kV are defined in Table 1, Table 2, and Table 3, respectively.  Operation of the system or equipment in such a manner as to create a condition where the harmonic current injection at the Connection Point exceeds the limits provided for in Tables 1, 2, and 3 for a duration greater than or equal to one hour on any single day or exceeds 150% of the limits provided for the given connection voltage for a duration greater than five minutes on any two days during a six month period is in violation of the Project performance criteria.

# Table 1. Current Injection Harmonic Distortion Limits: 
Connection Point Voltage >161000 V

|  | Individual Harmonic Order (Odd Harmonics) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Isc/Iload | H<11 | 11(h<17 | 17(h<23 | 23(h<35 | h>35 | TDD |
| <50 | 2.0 % | 1.0 % | 0.75 % | 0.3 % | 0.15 % | 2.5 % |
| (50 | 3.0 % | 1.5 % | 1.15 % | 0.45 % | 0.22 % | 3.75 % |

# Notes:	Even harmonics are limited to 25% of the odd harmonic limits above

Current distortions that result in DC offset are not allowed

Iload is the maximum load current (fundamental frequency component) at the Connection Point

# Isc is the maximum short-circuit current at the Connection Point

TDD (Total Demand Distortion) is the total harmonic current distortion expressed in % of maximum demand load current

Table 2. Current Injection Harmonic Distortion Limits: 
Connection Point Voltage 69001 V to 161000 V

|  | Individual Harmonic Order (Odd Harmonics) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Isc/Iload | H<11 | 11(h<17 | 17(h<23 | 23(h<35 | h(35 | TDD |
| <20 | 2.0 % | 1.0 % | 0.75 % | 0.3 % | 0.15 % | 2.5 % |
| 20<50 | 3.5 % | 1.75 % | 1.25 % | 0.5 % | 0.25 % | 4.0 % |
| 50<100 | 5.0 % | 2.25 % | 2.0 % | 0.75 % | 0.35 % | 6.0 % |
| 100<1000 | 6.0 % | 2.75 % | 2.5 % | 1.0 % | 0.5 % | 7.5 % |
| >1000 | 7.5 % | 3.5 % | 3.0 % | 1.25 % | 0.7 % | 10.0 % |

Table 3. Current Injection Harmonic Distortion Limits: 
Connection Point Voltage 120 V to 69000 V

|  | Individual Harmonic Order (Odd Harmonics) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Isc/Iload | H<11 | 11(h<17 | 17(h<23 | 23(h<35 | h(35 | TDD |
| <20 | 4.0 % | 2.0 % | 1.5 % | 0.6 % | 0.3 % | 5.0 % |
| 20<50 | 7.0 % | 3.5 % | 2.5 % | 1.0 % | 0.5 % | 8.0 % |
| 50<100 | 10.0 % | 4.5 % | 4.0 % | 1.5 % | 0.7 % | 12.0 % |
| 100<1000 | 12.0 % | 5.5 % | 5.0 % | 2.0 % | 1.0 % | 15.0 % |
| >1000 | 15.0 % | 7.0 % | 6.0 % | 2.5 % | 1.4 % | 20.0 % |

#### Voltage Unbalance

The maximum Voltage Unbalance any Project is allowed to introduce on the Duke ET System at the Connection Point is 1%.  Any Voltage Unbalance condition greater than 1% that has a duration greater than or equal to one minute is in violation of the Project performance criteria.

#### Temporary Overvoltages

The Project may not operate its equipment or system in such a manner as to cause a temporary overvoltage at the Connection Point greater than or equal to 120% of the nominal system voltage.  A temporary overvoltage is defined as an oscillatory phase-to-ground or phase-to-phase overvoltage lasting greater than 20 milliseconds which is undamped or only weakly damped.  Any temporary voltage condition caused by the operation of the Project’s equipment that results in a temporary overvoltage greater than or equal to 120% of the nominal system voltage at the Connection Point is in violation of the Project performance criteria.

#### Transient Overvoltages

The Project may not operate its equipment or system in such a manner as to cause a peak transient voltage at the Connection Point greater than or equal to 140% of the nominal peak voltage.  A transient overvoltage is defined as the peak line-to-line or line-to-ground voltage during the transient conditions resulting from operation of a switching device.  Any transient voltage condition caused by the operation of the Project’s equipment that results in a peak transient voltage greater than or equal to 140% of the nominal peak voltage at the Connection Point is in violation of the Project performance criteria.

#### i.   	Standards for Degradation of Transmission System Reliability and Integrity by Customers

This section prescribes a comprehensive approach for limiting the degradation of transmission system Reliability and Integrity by customers while the sections immediately preceding address some specific areas of interest.  In any case, the more stringent limitation applies.

Customers shall not cause power disturbances on the Duke ET System that exceed any of the annual limits listed below.  Customers exceeding any of these annual limits shall be considered to have violated the Standards for Degradation of Transmission System Reliability and Integrity (R&I) by Customers.

- Creation of more than 0.0067 Sustained Outages per 1 MW of customer’s load (SAIFI of 0.0067 per MW load).

- Creation of more than 0.0333 Momentary Interruptions or Equivalent Faults per 1 MW of customer’s load (MAIFI of 0.0333 per MW load).

- Creation of more than 400 Customer Equivalent Incapacitating Disturbances (CEID) per 1 MW of customer’s load.

The Standards for Degradation of Transmission System Reliability and Integrity by Customers applies to future system changes and reconfigurations whether these changes are initiated by the customer or the utility.

The result of the calculations in limits 1, 2 and 3 above will change if the customers load changes.

The result of the calculation for limit 3 is also subject to change if the number of Customer Equivalent Incapacitating Disturbances changes.  This could result from a change in the number, size or location of other customers or changes in the utility facilities feeding other customers.  A customer may elect to pay for dedicated facilities, with utility approval, to limit the future risk of exposing other customers to Incapacitating Disturbances in limit number 3.

### Duke ET System Characteristics

All Project equipment connected to the Duke ET System should be designed to operate within the system conditions defined in this section.  These characteristics are typical to the Duke ET System during normal and contingency conditions, but may be exceeded for very short times or if exceptional circumstances prevail.

#### Frequency

The frequency of the Duke ET System shall be nominally 60 Hz and shall be controlled within the limits of 59.9 Hz - 60.1 Hz unless exceptional circumstances prevail.  System frequency could rise to 61 Hz or fall to 59 Hz under exceptional circumstances.

#### Steady-State Voltage Variations

The Duke Electric Transmission System Planning Guidelines for voltage regulation and range at the Connection Point are listed in Table 4.

Table 4. System Voltage Variations at the Connection Point

|  | Absolute Voltage | Voltage Regulation |
| --- | --- | --- |
| Nominal Voltage (kV) | Minimum | Maximum | Normal | Contingency |
| 44 | 94 % | 109% | 8.5% | 10% |
| 100 | 95 % | 107% | 6% | 7% |
| 230 | 95 % | 105% | * | * |
| 500 | 100 % | 110% | * | * |

* On 230kV and 500kV, maximum allowable contingency drop is 5%.

#### Harmonic Voltage Distortion

The maximum harmonic voltage distortion at the Connection Point for each transmission voltage level is defined in Table 5.

Table 5. System Harmonic Voltage Distortion Limits

| Nominal Voltage (kV) | Maximum Individual Harmonic Voltage Distortion (%) | Maximum Total Voltage Distortion (%) |
| --- | --- | --- |
| 44 | 3.0 | 5.0 |
| 100 | 1.5 | 2.5 |
| 230 | 1.0 | 1.5 |
| 500 | 1.0 | 1.5 |

The limits in Table 5 represent the maximum harmonic voltage distortion at a given connection voltage for a duration less than or equal to one hour on any single day.  The maximum harmonic voltage distortion will not exceed 150% of the limits for a given connection voltage for a duration greater than five minute on any two days during a six month period.

#### Voltage Unbalance

The maximum Voltage Unbalance on the Duke ET System at the Connection Point for a duration greater than or equal to one minute will be less than or equal to 2.0%.

#### Transient Overvoltages

The maximum peak transient overvoltage at the Connection Point will be less than or equal to 200% of the nominal system peak voltage.

#### Temporary Overvoltages

The maximum temporary overvoltage at the Connection Point will be less than or equal to 180% of the nominal system voltage.  For Effectively Grounded portions of the Duke ET System, the maximum may be significantly lower than 180%.

## Protection Requirements

This section establishes the minimum design objectives and recommended design philosophy for the protective systems associated with a load delivery from the Duke ET System.  A protective system is defined as those components used collectively to detect defective power system elements or conditions of an abnormal or dangerous nature, to initiate the appropriate control circuit action, and to isolate the appropriate system components in order to alleviate or minimize the harmful effect of the abnormality.

In analyzing the relaying practices to meet the broad objectives set forth, consideration must be given to the type of equipment to be protected, e.g., generators, lines, transformers, buses, etc., as well as the importance of the particular equipment to the integrity of the transmission system.  Thus, practices may vary for different equipment, and for different applications of the same type of equipment.  While it is recognized that the probability of failure should not negate the single contingency principle, the practices adopted may vary, based on judgment and experience as to the development of a workable and practical set of standards.  Special local conditions or considerations may necessitate the use of more stringent design criteria and practices.

### Protective Relaying Philosophy

#### Objectives

The basic design objectives of any protective scheme are to

- Insure safety of the general public

- Maintain dynamic stability;

- Prevent or minimize equipment damage;

- Minimize equipment outage time;

- Minimize the system outage area;

- Minimize system voltage disturbances;

- Allow the continuous flow of power within the ratings                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                         of equipment on the system.

#### Protective System Design Considerations

The philosophy in the implementation of any protection system should be to detect and isolate all failed or faulted components as quickly as possible, while minimizing disruption to the remainder of the electric system.  This objective implies that a protection system should be: (1) dependable - operate when required, (2) secure - not operate unnecessarily, (3) selective - only the minimum required number of devices should operate, and (4) fast - minimize hazards to personnel and damage to equipment.  In addition, backup protection should clear any fault upon failure of the protective equipment in the primary protection system.

#### Operation

Operation of the Project should not adversely affect the Duke ET System.  This includes switching operations as well as faults within the Project.  The Project Sponsor is responsible for providing protection for the Project and must demonstrate that their own equipment properly protects all of their facilities.  The Project should not be designed or operated with a ground source at the connected voltage unless specifically approved by Duke ET.

#### Fault Analysis

All operations of protective devices within the Project are to be reviewed and documented. This information will be available to Duke ET on request to assist in analyzing fault operations on the Duke ET System.  To facilitate the analysis of system disturbances and the evaluation of system operation, fault recorders may be required on certain types of complex substations and at all large unit generating stations connected to the Duke ET System.  Fault recording functions in microprocessor relays may provide the detailed data needed to perform the analysis.

#### System modifications beyond the Connection Point

System protection modifications to the Project are to be reviewed by Duke ET before changes are made.  These changes are defined as changes in interrupters, lines, transformers, protective devices and protective settings. This review is needed to insure proper operation of the power systems and coordination of protective devices.

#### Maintenance of Equipment

Project Operator will perform protection equipment maintenance on a regular schedule.  This is to include the following:

- Functional testing of trip circuit

- Functional testing of interrupter

- Calibration testing of protective devices settings

- Inspection and maintenance of power dc sources

- Inspection and maintenance of interrupter

### 100-kV Load Delivery (radial load at Connection Point)

- Duke ET will be responsible for providing protection for the Duke ET System.

- Protection beyond the Connection Point is the responsibility of the Project Sponsor and/ or Project Operator and must be coordinated with Duke ET System protective devices.

- The Project Sponsor may be required to provide a Protection Station immediately beyond the Connection Point to provide protection for the Project.

- Protection will include devices to detect and interrupt all types of faults.  This generally will include overcurrent protection for both phase and ground faults and a three phase interrupting device.

- The overcurrent protection should provide both instantaneous tripping for high value faults and time delay (Inverse) tripping for lower value faults.

- All protective relays will be in service at all times and not be blocked for automatic or manual testing of the Project.  When required for switching, ground relays may be blocked.

- One time delayed automatic reclose to the Project can be performed. Up to two time delayed automatic recloses may be allowed on 44-kV deliveries if fed directly from a tie station bus.  Reclosing intervals must be coordinated with the Duke ET System reclosing devices.

- Manual testing of the Project after a lockout is to be coordinated with Duke’s TCC before testing the line.

- Fault monitoring/location equipment is recommended at Protection Stations.

- Functional testing of protective circuits and interrupting device should be regularly performed.

- All protective device operations at transmission voltages will be analyzed and documented.

### 100-kV Load Delivery Requiring a New Duke ET -Owned Tap Line

Protection of any Duke ET -owned tap line will be reviewed to determine if additional protection is required.  If additional protection is required due to the addition of the Project, it will be to protect Duke ET -owned facilities and the Project Sponsor is still required to provide protection as defined in Section 2 (above) for the Project.  The length and location of the Duke ET -owned tap line will determine if Duke ET System requires additional protection.

- If Duke ET System’s standard protective devices can not detect faults at the end of the Duke ET -owned portion of the tap line, additional protection will be required.  This will either require a protective device and interrupter at the transmission line tap or additional protective devices on the transmission line.

- If additional protective devices are needed on the Duke ET System, then zone distance pilot relays at each end of the transmission line may be required. Also a communication channel between the two ends of the line may be required.  This scheme may be used to allow the reach of the distance relay to be extended to the end of the tap line without causing the transmission line to trip for remote faults not on the line.

### Dual Feeds to Project, 44-kV, 230-kV and Higher, etc.

These will be evaluated as needed.  The protection requirements for this type of station vary with the location and type of feeds.

## Metering and Telecommunication Requirements

All Projects that are connected to the Duke ET System will require revenue-accuracy-metering equipment (i.e. metering enclosure with meter and associated equipment, instrument transformers, and certain interface enclosures with associated isolation devices). This section states the minimum requirements for metering and telecommunication associated with a load delivery from the Duke ET System.

### Supervisory Control and Data Acquisition (SCADA)

Loads larger than 100 MVA may require SCADA depending on their location to ensure that the TCC has the information necessary for maintaining system reliability.

The following data may be required:

Connection Point isolation device(s) status

Load MW and MVAR measured at the Connection Point

Voltage at the Connection Point

MW and MVAR line flow on any transmission line coming into the substation

### Metering

Metering equipment should be installed, if possible, at the Connection Point.  If not installed at the Connection Point then power transformer and/or line losses will need to be considered.

#### Metering Equipment Requirements

A solid state meter shall be used to measure the real and reactive power interchange between the Duke ET System and the Project. Three-element, three-phase, four-wire meters shall be utilized on wye connected power systems. Two-element, three-phase, three-wire meters shall be utilized on delta connected power systems.

A bi-directional watt/var-hour meter may be necessary if there is power flow in and out of the Duke ET System.

For metering equipment located in the Project substation, the installation of a metering bypass is suggested, but not required. For the replacement of failed or malfunctioning equipment a metering bypass is necessary to maintain power flow to the Project. If a metering bypass is not installed, an outage will be required to replace the failed or malfunctioning equipment.

The metering devices must be fully compatible (approved meter type and communication media) with Duke ET System’s remote metering and data acquisition system.

#### Meter Accuracy

Meters shall be calibrated to 0.5% accuracy at unity power factor for both full load and light load. These meters shall be calibrated to 1.0% accuracy for 0.5 power factor at full load. Metering accuracy limits are stated in the following table.

| METER ACCURACY LIMITS |
| --- |
| Watt-hour Function | Var-hour Function |
| Full Load | Power Factor | Light Load | Power Factor |
| +/- 0.5 | +/- 1.0 | +/- 0.5 | +/- 1.0 |

# Notes:

- Watt-hour and var-hour functions should be tested in both directions of energy flow (In and Out).

- When compensating for transformer or line loss, utilize stated limits above or 5% of desired compensation, whichever is greater.

- The meter shall be tested with compensation applied to obtain a true test of the installation.

| Test Points | Volts | Amps | Power Factor |
| --- | --- | --- | --- |
| Full Load | 120 | 5 | 1.0 |
| Power Factor | 120 | 5 | 0.5 |
| Light Load | 120 | 0.5 | 1.0 |

#### Instrument Transformers

Voltage and current transformers shall be 0.3% metering accuracy class for both magnitude and phase angle over the burden range of the installed metering circuit.  Instrument transformer correction factors may be applied to the meter to adjust the meter for inaccuracies associated with the secondary burdens in the current transformer and voltage transformer circuits.  All instrument transformers shall comply with ANSI/IEEE Standard C57.13.

#### Loss Compensation

If the metering is not located at the Connection Point, then power transformer and/or line loss compensation will need to be considered. Duke ET approved power transformer and/or line loss compensation values should be applied to the meter to properly compensate for the losses in the power transformer and/or line.

#### Access to Metering Data

If access to the meter is required, proper security measures must be taken to ensure the integrity of the meter is not compromised. If data pulses are required from the revenue meter, then the appropriate interface box with associated equipment must be installed to properly protect the revenue meter.  If an additional information meter is requested, good engineering practices must be adhered to when terminating the connections in the meter circuit to ensure the integrity of the revenue-accuracy metering circuit is intact.

#### Station Service Power

Metering requirements for the Station Service Power, if any, will be determined on a case-by-case basis.

#### Calibration of Metering Facilities

Metering facilities shall be tested and calibrated if necessary every two years.  More frequent test intervals may be negotiated.  All interested parties or their representatives may witness the calibration tests.  Calibration records shall be made available to all interested parties.  The accuracy of the standard utilized for calibration purposes shall be traceable to the National Institute of Standards and Technology, (NIST).

### Voice Communication

Requirements, if any, will be determined on a case-by-case basis.

### Telecommunications for SCADA

Consist of either leased phone lines, microwave channels, or fiber-optics from the site to the TCC.  Factors involved in selecting a type of circuitry are availability, proximity to the site, and cost.  Fiber is preferred. These are dedicated channels and are not redundant.

### Telecommunications for Revenue-accuracy metering

A compatible and reliable communication media must be provided and maintained, to enable Duke ET to interrogate the meter, collect, merge, and store metering and usage data with Duke ET System’s remote metering and data acquisition system.

### Telecommunications for Protection Systems

Most Projects connected to the Duke ET System will not require any special communication devices/circuits for protection.  A local voice/alarm circuit is recommended when an interrupting device is installed.

If the Project can back-feed the Duke ET System either from a generator or alternate source, then the protection system may require communications with remote ends of Duke’s transmission line. These will be evaluated on a case-by-case basis.

# FACILITY CONNECTION REQUIREMENTS – GENERATION AND INTERCONNECTION FACILITIES

## Scope

The technical requirements contained herein generally apply to all generation facilities and Interconnections to the Duke ET System.  The location of the connection and the impacts on the Duke ET System, or another utility’s system, determine the specific requirements.  The Project must not degrade the safe operation, integrity, or reliability of the Duke ET System.

- Applicable Codes, Standards, Criteria and Regulations

To the extent that the Codes, Standards, Criteria and Regulations are applicable, the Project shall be in compliance with those listed in the References section of this document and others that are applicable.

- Safety, Protection, and Reliability

Duke ET, after consultation with the Project Sponsor and other relevant parties, shall make the sole and final determination as to whether the Duke ET System is properly protected from any problems that the Project might cause before a connection is closed.  The Project Sponsor is responsible for correcting such problems before connected operation begins. The Project Sponsor is responsible for safety, protection, and reliability on the Project side of the Connection Point.

- Non-Duke Responsibilities

Project Sponsors and Project Operators shall comply with NERC Planning Standards and Operating Policies.  The Project Sponsor is responsible for the planning, design, construction, reliability, protection, and safe operation of non-Duke-owned facilities.  The design and operation of the Project is subject to applicable local, state and federal statutes and regulations.

- Cost of Connection Reviews

The Project Sponsor requesting Duke ET to perform a Connection Review will reimburse Duke ET for its actual costs to perform the study.  This includes costs associated with verifying that all technical requirements in this document are properly addressed.

## Request for Generation and Interconnection Studies

Project Sponsors should contact Duke Electric Transmission as early as possible in the planning process for any potential new/modified utility Interconnection or generation connection to the Duke ET System.  The Project Sponsor should supply information about the location, voltage, and other pertinent connection requirements.  Certain areas within the Duke ET System can accept only limited amounts of additional generation without costly reinforcements.  Duke ET may have to add to or modify its transmission system substantially before connecting a new Project.  A Connection Review must be performed to determine the required connection facilities and modifications to accommodate the Project.  This study may also address the transmission system capability, transient stability, voltage stability, losses, voltage regulation, harmonics, voltage flicker, electromagnetic transients, ferroresonance, metering requirements, protective relaying, substation grounding, and fault duties.   If necessary, joint study with neighboring control areas may be performed to assess the impact of the Project.   The data that the Project Sponsor is required to provide to enable the completion of these studies is listed in the Project Sponsor Supplied Information section.

Proposals for Interconnection with other control areas will require a Connection Review.  The new Interconnection would require development of a new, or modification of an existing interchange or Interconnection agreement.  In addition to the technical aspects of the new Interconnection, a business case would have to be developed to examine the economics of the proposal.

### Connection Configuration

Projects may be connected to the Duke ET System by tapping an existing transmission line(s) or by connecting directly into an existing transmission station.  A new transmission switching station may be built in the middle of an existing transmission line.  Duke’s 500-kV and 230-kV transmission systems are typically reserved for the bulk transport of large amounts of electricity.

The number of available connection options is dependent upon many factors, including location of the desired Connection Point relative to existing Duke transmission facilities, the size of the Project’s generation, present transmission line loading, and other requirements of the Project.  The most feasible option(s) will be considered in the Connection Review, with the most economic option meeting all requirements being selected.

### Power Flow

The Project is incorporated into power flow models by Duke ET using the data provided by the Project Sponsor.  Power flow simulations are performed to determine the impact of the Project on the transmission system.  The Project Sponsor must provide the expected source and sink of energy related to the Project.  The primary intent is to determine if the Project causes any violations of the Duke Electric Transmission Planning Guidelines (Planning Guidelines), which is part of Duke’s annual FERC 715 filing, the SERC Planning Principles and Guides, or the NERC Planning Standards (collectively, Planning Standards).  A summary of these guidelines is provided below:

#### Thermal and Voltage Screening

The purpose of this study is to ensure that the connection of the Project does not create any thermal loading or voltage levels outside of the limits provided in the Planning Guidelines.  Project information obtained from the Project Sponsor is used to model the Project.  Power system simulation tools are used to model a wide range of transmission system operating conditions to determine the thermal loading and voltage level changes created by the Project on the Duke ET System.

#### Transfer Capability

The purpose of this study is to ensure that the connection of the Project does not reduce the ability of the transmission system to transport power over long distances between and among control areas.  Joint studies with other utilities may be necessary.  Transfer Capability requirements are detailed in the Planning Standards.  Power transfers are simulated across the Duke Electric Transmission System in various directions to determine how the Project affects Duke’s ability to transfer power across its system and to and from other control areas.

#### Fault Duty

The purpose of this study is to determine the changes in available fault duty caused by the Project.  Transformer, line and generator impedances, and the circuit configuration are needed to create the model for the study.  The data is inserted into the current Duke ET model.  The new generation buses and those local to it are faulted to allow comparison with fault conditions prior to the addition of the Project.  The study results are reviewed to ensure that no equipment ratings will be exceeded and are utilized for determining the type of grounds used for personnel protection for conducting de-energized line and station work.

#### Stability

Dynamics software is used to evaluate the impact of the new system configuration and additional generating capacity on system stability.  In addition to the normal steady state model data, generator impedances and time constants, turbine governor data, and voltage regulator data are needed to create a model for the study.  The new generation buses and those local to it are faulted to evaluate system stability with and without the Project.  Study results are evaluated to ensure system stability will be maintained and that any necessary changes to relaying or controls are identified. See the General Requirements section for more detail on generator controls.

### Protection

After studying the possible ways to connect the Project to the Duke ET System, the protective requirements will be determined.  This will include an impedance model at the Connection Point (short-circuit data), protective changes to the transmission system, protective requirements for the generation and any special protective needs for the Project.  See the General Requirements and Protection Requirements sections for more details on these requirements.

### Power Quality and Reliability

There is a very diverse set of users connected to the Duke ET System with differing system requirements.  In the past, most customers were only concerned with extended interruptions.  However, the increased use of highly sensitive power electronic devices within all customer sectors has changed the definition of reliability.  Due to the sensitivity of many industrial and commercial loads such as adjustable speed drives (ASDs) and computer controlled processes, reliability is no longer only defined by the frequency and duration of sustained interruptions.  There are many power quality variations other than sustained interruptions than may constitute inadequate service for the proper operation of customer equipment.  Variations such as Voltage Unbalance, voltage flicker, harmonic distortion, transient overvoltages, temporary overvoltages and steady-state voltage regulation can adversely affect customer processes.

The challenge for the transmission owner is to design and operate the transmission system such that it meets the requirements of this diverse set of users.  To meet this challenge, Duke Electric Transmission performs studies to determine the power quality and reliability impacts of any new Project on the Duke ET System at the Connection Point.  The intent of these studies is to ensure that the connection of the Project does not compromise the reliability and integrity of the Duke ET System.

The studies performed for each new Project may include:

#### Voltage Unbalance

The purpose of this study is to ensure that the operation of any new Project does not create a Voltage Unbalance condition in excess of the limits provided in the Performance Requirements section.  Project information obtained from the Project Sponsor is added to the power system model.  Using power system simulation tools, studies are performed over a wide range of transmission system operating conditions to determine the range of Voltage Unbalance created by the Project at the Connection Point.

#### Voltage Flicker

The purpose of this study is to ensure that the operation of any new Project does not create voltage fluctuations in excess of the limits provided in the Performance Requirements section.  Project information obtained from the Project Sponsor is added to the power system model.  Using power system simulation tools, studies are performed over a wide range of transmission system operating conditions to determine the range of voltage fluctuations created by the Project at the Connection Point.

#### Harmonic Distortion

The purpose of this study is to ensure that the operation of any new Project does not create harmonic current injections in excess of the limits provided in the Performance Requirements section.  Project information obtained from the Project Sponsor is added to the power system model.  Using power system simulation tools, studies are performed over a wide range of transmission system operating conditions to determine the range of harmonic distortion created by the Project at the Connection Point.

#### Transient Overvoltage

The purpose of this study is to ensure that the operation of any new Project does not create a transient overvoltage condition in excess of the limits provided in the Performance Requirements section.  Project information obtained from the Project Sponsor is added to the power system model.  Using power system simulation tools, studies are performed over a wide range of transmission system operating conditions to determine the range of transient overvoltages created by the Project at the Connection Point.

#### Temporary Overvoltage

The purpose of this study is to ensure that the operation of any new Project does not create a temporary overvoltage condition in excess of the limits provided in the Performance Requirements section.  Project information obtained from the Project Sponsor is added to the power system model.  Using power system simulation tools, studies are performed over a wide range of transmission system operating conditions to determine the range of temporary overvoltages created by the Project at the Connection Point.

#### Temporary Undervoltage

The purpose of this study is to ensure that the operation of any new Project does not create a temporary undervoltage condition in excess of the limits provided in the Performance Requirements section.  Project information obtained from the Project Sponsor is added to the power system model.  Using power system simulation tools, studies are performed over a wide range of transmission system operating conditions to determine the range of temporary undervoltages created by the Project at the Connection Point.

#### Insulation Coordination

The purpose of this study is to ensure that the operation of any new Project does not create a condition that will require intervention of Duke-owned transmission equipment in excess of the limits provided in the Performance Requirements section.  Project information obtained from the Project Sponsor regarding insulation coordination studies is reviewed and must be approved by Duke ET prior to connection.  Duke ET may perform independent studies verifying the models and assumptions used by the Project Sponsor are appropriate for their application.

### Changes to Project Sponsor-Supplied Information

If any data previously supplied pursuant to these connection requirements changes, the Project Sponsors or Project Operator will notify Duke ET in writing without delay.  Data changes may require additional studies to examine the impact.  This notification will include:

- the time and date at which the change became, or is expected to become, effective

- if the change is only temporary, an estimate of the time and date at which the data will revert to the previously supplied form.

A request for a change in Connection Point to the Duke ET System, level of generation, or expected sink must be submitted as a new request.  A new completion date will be negotiated with the Project Sponsor or Project Operator when Project data is changed.

### Required Project Sponsor-Supplied Information

Any Project Sponsor desiring a new connection or modification of an existing connection must provide the following applicable information:

- Company name and contact name

- Address

- Phone number, fax number, e-mail address of contact name

- Effective date of new connection or modification

- Proposed geographic location and Plot Plan providing orientation of the Project on the Site (USGS map)

- Electrical Connection Point

- Voltage level of Proposed Connection

- One-line diagram of Project

- Start-up Date

- Commercial Operation Date

- Contract Path & Source and Sink for the energy

- Duration of Contract

- Expansion Plans

- Number and Type of Units

- Plant Start-up Load

- Fuel Type

- Total Generation Capability (MW) – Summer and Winter ratings

- Power Factor

- Generator Data (for each generator)

- Manufacturer

- Base MVA

- Maximum MVA

- Rated MW (Summer & Winter)

- Rated kV

- Rated Power Factor

- % Reactance – Synchronous, Sub-Transient & Transient

- Capability Curve Data

- Auxiliary Load Data

- Dynamic Modeling Data – H, Ra, Xd, Xq, X’d, X’q, X”d, X”q, Xl, T’do, T’qo, T”do, T”qo, S(1.0), S(1.2)

- Governor & Excitation System Models – IEEE or PTI format

- Step-up Transformer Data

- Manufacturer

- Connection (Delta/Wye)

- KVA ratings of all windings

- H winding kV

- X winding kV

- Y winding kV

- Transformer neutral load (if wye connected on the high side) in ohms

- Impedance (%Z) and load losses (W) @kVA for all tap combinations of H-X, H-Y, & X-Y

- No load losses and magnetizing current

- Other transformer ratings, connections, voltage taps, impedances, and grounding

- Transmission line voltage, conductor rating, impedance, length

- Lightning protection designs for transmission lines and stations

- Special requirements (e.g. sensitive equipment, dual feeds, etc.)

- Preferred method of connection (ring bus, breaker and a half, etc.)

- Relay schemes, relay settings, protection equipment

- Maintenance schedules and procedures

## General Requirements

### Safety

All safety and operating procedures for joint use equipment shall be in compliance with the Occupational Safety and Health Administration (OSHA) standard 29 CFR 1910.269, the National Electrical Safety Code (NESC), the Duke Power Safe Work Practices Manual, the Duke Electric Transmission Operating Procedures Manual and the Project Sponsor’s safety manuals.

#### Isolation Requirements

The Project Operator shall not energize any Duke ET System line or equipment unless the Duke TCC specifically approves energization.  If, for any reason, a protective device operation separates the Project from the Duke ET System, the Project Operator will contact the Duke TCC before attempting to restore the connection to the Duke ET System.

At the Connection Point with the Duke ET System, a disconnect switch shall be provided for the purpose of physically and visibly isolating the Project from the Duke ET System.  With the consent of Duke ET and the Project Sponsor, the disconnect switch may be installed at another location, other than the Connection Point, provided that the purpose described herein is satisfied. The device:

- Must be accessible by Duke ET and under Duke TCC jurisdiction.

- If gang-operated, must be lockable in the open position by Duke ET.

- Must be suitable for safe operation under the conditions of use.

- Would not be operated without advance notice to either party, unless an emergency condition requires that the device be opened to isolate the Project.

Duke ET personnel may open the switch:

- If it is necessary for the protection of Duke ET maintenance crew personnel when working on de-energized circuits.

- If the Project or Duke ET System equipment presents a hazardous condition.

Consideration shall be given as to the design and capacity of the switch on a case-by-case basis.  The switch is required for safety and may not be required to interrupt load or energization (charging) current.  However, a suitable switch for the safety requirements herein described may also be used to provide for other operational purposes.

#### Cogeneration Served by the Project

The Project Sponsor shall maintain a record of all cogeneration customers served by the Project and such record shall be made available to Duke ET.  For the requirements of energized line maintenance or line construction on the Duke ET System, the Project Sponsor will ensure that all cogeneration customers served by the Project will disconnect their generation upon request by Duke ET.

### Connection Point Considerations

#### General Configurations and Constraints

Integration of  Projects into power systems usually falls into one of the following three categories:

1)	Connection into an existing 44-kV to 500-kV substation.

2)	Connection on the low-voltage side (typically 4-kV to 24-kV) of a new or existing customer service transformer that was originally designed to serve load.  Load Delivery Requirements apply to projects having generating capability of less than 25% of minimum load.

3)	Connection at 44-kV to 500-kV to a transmission line by building a new switching station in the vicinity of the Project.

#### Other Considerations

Below are some of the other issues considered when evaluating Project proposals:

##### Equipment

Existing electrical equipment, such as transformers, power circuit breakers, disconnect switches, and line conductors were purchased based on the duties and capacity limits expected in response to system additions identified in long-range plans.  However, with the connection of a new generating resource or large loads, some equipment may become overloaded and need to be replaced.

##### Outage Coordination & Maintenance

Duke ET operates and maintains its system to provide reliable customer service at all times.  Project integration requires that the equipment at the Point of Connection not restrict timely outage coordination, automatic switching or equipment maintenance scheduling.  Preserving reliable service to all Duke ET customers is essential and may require additional switchgear, equipment redundancy, or bypass capabilities at the Point of Connection for acceptable operation of the system.

##### Atmospheric & Seismic

The effects resulting from wind storms, floods, lightning, altitude, temperature extremes, and earthquakes must be considered in the design and operation of the Project.  The Project Sponsor is responsible for determining that the appropriate standards are met, including, but not limited to, the Uniform Building Code (UBC) and the National Electrical Safety Code (NESC).  Depending on Project location, size, type, and importance, Duke Energy may request that additional capabilities be designed into the Project.

### Substation Grounding

Each generation site and/or interconnecting substation must have a ground grid that solidly grounds all metallic structures and other non-energized metallic equipment.  This grid shall limit the ground potential gradients to such voltage and current levels that will not endanger the safety of people or damage equipment which are in, or immediately adjacent to, the station under normal and fault conditions.

If the Project is physically close to another substation, it is recommended that the two ground grids be connected.  The interconnecting cables must have sufficient capacity to handle fault currents and control ground grid voltage rises.  Duke ET must approve any connection to a Duke substation ground grid.  If the ground grids must be isolated for operational reasons, there must be no metallic ground connections between the two substation ground grids.  Cable shields, cable sheaths, station service ground sheaths, and overhead transmission shield wires can all inadvertently connect ground grids.  Fiber-optic cables are an excellent choice for telecommunications and control between two substations to maintain isolated ground grids. In the case where the Project is physically close to another substation but the ground grids are isolated, the Project Sponsor must demonstrate that the ground grids are properly isolated and in compliance with all applicable codes and standards.  Duke ET prefers to connect static wires on incoming transmission lines to the station ground grid.  If the Project Sponsor prefers not to connect static wires on incoming transmission lines to the station ground grid; the Project Sponsor must notify Duke ET in writing and demonstrate that relay performance, lightning protection, and personnel safety are not compromised by isolating the static wires from the station ground grid.

The Project ground grid should be designed to ANSI/IEEE Std. 80-1986, IEEE Guide for Safety in AC Substation Grounding, and should be measured in accordance with IEEE - 81 Part 1: Guide for Measuring Earth Resistivity, Ground Impedance, and Earth Potentials and Part 2: Measurement of Impedance and Safety Characteristics of Large, Extended or Interconnected Grounding Systems.  Project grounding requirements shall also comply with the National Electrical Safety Code, ANSI/IEEE - 665 Guide for Generating Station Grounding, IEEE - 837 Standard for Qualifying Permanent Connections Used in Substation Grounding, IEEE - 487 Protection of Wire-Line Communication Serving Electric Power Stations, ANSI/IEEE 367-1987 IEEE Recommended Practice for Determining the Electric Power Station Ground Potential Rise and Induced Voltage from a Power Fault, and any applicable state and local codes.

### Insulation Coordination

Power system equipment is designed to withstand voltage stresses associated with expected operation.  Connection Studies include the evaluation of the impact of the Project on equipment insulation coordination.  Duke ET identifies additions required to maintain an acceptable level of Duke ET System availability, reliability, equipment insulation margins, and safety.

Voltage stresses such as lightning surges, switching surges, temporary overvoltages, and normal 60Hz voltages may affect equipment duty.  Remedies depend on the equipment capability and the type and magnitude of the stress.  Below are the requirements that must be met to connect to the Duke ET System.  In general, stations shall be protected against lightning and switching surges.  Typically this includes station shielding against direct lightning strokes, surge arresters on all wound devices, and shielding on the incoming lines.

#### Lightning Surges

Lightning is the single largest cause of transmission line events in the Duke ET System service area and must be considered during the design and installations of transmission lines and substations.  Lightning related causes are not exempt from the Performance Requirements section.  Although it is not always cost effective to design and build a power system to withstand every possible lightning stroke, it has been demonstrated that with proper design and installation procedures, the effects of lightning can be mitigated to achieve a reliability level equal to or exceeding the requirements of the Project performance criteria section.  Techniques used to help control lightning related events on transmission lines include proper use of shield wires, insulation levels, low resistance grounding, and surge arresters.  Techniques used to help control lightning related outages in substations include substation shielding, proper arrester applications, and shielding of incoming transmission lines.

If the Project proposes to tap a Duke transmission line that is shielded, the new tap line must also be properly shielded for at least one mile from the Duke ET System.  If any stations are within one mile of the Duke ET System, these also must be properly shielded from direct lightning strokes.  The Project Sponsor must be able to demonstrate proposed designs for any transmission lines and substations will perform within the limits for service interruptions as stated in the Performance Requirements section.

For transmission line design, an industry recognized lightning performance estimating algorithm may be used to demonstrate acceptable performance of the design.  The Project Sponsor must make reasonable assumptions based on the area that the transmission line will be installed including ground flash density and grounding conditions.  The Project Sponsor must be able to provide an alternative plan if the ground conditions required for acceptable performance are not achieved during construction of the transmission line.

For substation design, the Project Sponsor must be able to demonstrate their proposed designs will operate within the performance requirements.  The shielding designs and arrester applications shall adhere to applicable IEEE standards.  In addition, any normally open points that are subject to voltage “doubling” of incoming lightning surges must be considered and protected accordingly so the Performance Requirements are not violated.

#### Switching Surges

At voltages below 500-kV, modifications to protect the Duke ET System against Project-generated switching surges are not anticipated although the Connection Review identifies the actual needs.  At 500-kV, Duke ET may require that arresters be added at the line terminations of the substations if switching surge studies predict overvoltages that may otherwise cause a flashover at the Project’s facilities.

#### Temporary Overvoltages

Temporary overvoltages can last from seconds to minutes, and are not characterized as surges.  These overvoltages are usually present during faults and other abnormal system conditions.  The Duke ET System is typically considered Effectively Grounded at 100-kV and higher voltages.  However, the 44-kV system is not Effectively Grounded in all locations.  These systems may be impedance grounded and can have line to ground voltages approaching 1.73 times normal line to ground voltage during fault conditions on unfaulted phases.  It is not acceptable for the Project to supply any ground source for the transmission system unless specifically approved and coordinated with Duke ET.

When generation is connected to the low-voltage side of a delta-grounded wye (D-YG) transformer, remote end breaker operations initiated by the detection of faults on the high-voltage side can cause overvoltages that can affect personnel safety and damage equipment.  In these instances, Duke ET will require the Project to rapidly separate the generator from the step-up transformer by tripping a breaker using either remote relay detection with pilot scheme (transfer trip) or local relay detection of overvoltage condition.

A system study may be performed for each Project based on the point on the Duke ET System that is being connected.  The Project Sponsor will be supplied the system characteristics needed to calculate the temporary overvoltages that need to be considered.  Gapless metal-oxide surge arresters are especially sensitive to system temporary overvoltages and Duke ET may review the specification of arresters used on 44-kV systems to ensure proper application.

#### Normal Operating Voltages

The Duke ET System voltages are normally operated within the limits specified in the Performance Requirements section of this document.  Insulation Coordination usually does not need to consider this operating range once lightning and switching surge requirements are met; however, in highly contaminated areas, special consideration and additional insulation requirements may be required for proper insulation coordination.  The Project Sponsor is responsible for determining whether special insulation requirements are needed for its system.

### Inspection, Testing, Calibration and Maintenance

The Project Sponsor and Project Operator have full responsibility for the inspection, testing, calibration and maintenance of its equipment, up to the Connection Point, consistent with the power purchase, operating agreement or interconnection agreement.  Maintenance activities must be coordinated with the Project and TCC and/or SOC to ensure the Duke ET System is not adversely affected.

#### Preenergization Inspection and Testing

Before initial Project energization, the Project Sponsor or Project Operator shall develop an Inspection and Test Plan for preenergization and energization testing. This plan should include provisions for testing protective equipment that comply with the NERC Planning Standards, Section III A, Guide G9.  Duke ET will review and must approve the test plan prior to the test.  Duke ET may require additional tests; the costs of these tests are subject to negotiation.  The Sponsor shall make available to Duke ET all drawings, specifications, and test records of the Project equipment pertinent to interconnected operation.

#### Calibration and Maintenance

##### Revenue Metering

Revenue metering shall be tested and calibrated if necessary at least every two years.  More frequent test intervals may be negotiated.  All interested parties or their representatives may witness the calibration tests.  Calibration records shall be made available to all interested parties.  The Metering and Telecommunication Requirements section should be reviewed for further details.

##### All other equipment

The Project Sponsor or Project Operator shall implement a preventive maintenance program for the Project equipment.  The program shall be designed and executed in a manner to ensure the proper operation of the Project equipment. The program may be based on time or on other factors, including performance levels or reliability.  Appropriate equipment performance data will be collected and maintained by the Project Sponsor or Project Operator.  Duke ET reserves the right to review the Project’s preventive maintenance program.  Maintenance records of the Project equipment pertinent to interconnected operation shall be made available to Duke ET upon request.

### Station Service

Power provided for local use at a substation to operate lighting, heat and auxiliary equipment is termed Station Service.

Alternate Station Service is a backup source of power, used only in emergency situations or during maintenance when primary Station Service is not available usually only in large switching stations.

Appropriate providers of Station Service and alternate Station Service are determined during the Project planning process, including Project diagram development and review.  Generally, the utility with a distribution service will be the preference provider of primary Station Service unless 1) it is unable to serve the load, or 2) costs to connect the local utility are prohibitive.

The Project Sponsor must provide metering for Station Service and alternate Station Service, as specified by the metering section of this document.

### Isolating, Synchronizing and Black Starts

#### Isolation

The Project Sponsor is responsible for ensuring that proper current-interrupting, isolating equipment is acquired and installed at the facility.  This equipment will be installed for the purposes of protecting the Project from faults or other undesirable conditions on the transmission system, and to protect the transmission system from faults internal to the Project.

During emergency conditions, the Project Operator’s first duty is to ensure safety guidelines are achieved and to protect station

equipment.  The Project Operator should have a Duke approved set of procedures on file at the Duke System Operating Center (SOC) and at the Project that are to be followed when separating from and reconnecting to the transmission system.  These procedures, jointly developed by the Project Operator and Duke ET, typically include:  1) a frequency limit duration table, 2) a circuit breaker operation procedure, 3) a generator loading/circuit protection procedure, and 4) a set of unit operating conditions that should be maintained to prevent damage to the unit(s) and/or the transmission system.

The Project Operator should NOT energize any equipment, connect to any energized equipment unless instructed to do so by the Duke TCC, or parallel any generation to the system unless instructed to do so by the Duke SOC System Coordinator.  If, for any reason, the Duke Electric Transmission System is disconnected from the Project (through a fault condition, line switching, etc.), the protective equipment connecting the Project to the system must open and not reclose until approved by the TCC.

#### Synchronization

The Project Operator shall be responsible for synchronizing its equipment to the Duke ET System.  If the Project is a participant in the Duke Emergency Guidelines for Capacity Shortages, then the Project Operator should follow those procedures during the event of a system emergency.  During all other conditions, the generator should have Duke ET approved procedures in place when connecting to the system.  For automatic synchronization, a synchronizing relay shall be installed to assure that the unit is not connected to the energized power system out of synchronization.

#### Blackstart

Blackstart is the condition when a unit of a generation Project starts up under local power, in isolation from the Duke ET System.  Blackstart capability is needed in the rare event of a system restoration emergency.  Depending on the size and location of a Project, this service may be needed from that Project.  It is generally not needed for small generators or for Projects in close proximity to other major generation.  If the Project is supplying blackstart capability to the Duke ET System, then it will be a participant in the Duke Emergency Guidelines for Capacity Shortages.  In the event of a local or wide-spread blackout, those guidelines should be followed to aid in the restoration of the system.  If for any event, generation is not running and the Project becomes completely de-energized, the Project Operator should advise the Duke System SOC Coordinator of its status and await further Coordinator instruction.

Some issues Duke ET considers when determining whether to request the capability of a Project to provide blackstart capability include the following:

- Proximity to other generation (i.e. Can blackstart capability be provided more efficiently from another Project?)

- Location of the Project on the transmission system (i.e. Is the Project near major load centers and far from other generation?)

- Cost of on-site start-up; and

- Periodic testing to ensure personnel training and capability.

## Performance Requirements

All Projects must be properly designed, constructed, operated, and maintained to avoid degrading the reliability of the transmission network.  A Project must comply with the Project performance criteria, listed below; and must be able to operate satisfactorily within the limits defined in the Duke ET System Characteristics section, below, in order to be considered properly connected.  The Project Sponsor or Project Operator is expected to demonstrate, through monitoring, that the Project meets the performance criteria.  It is required that the criteria of Sections 1.a and 1.b be continuously monitored.  The remaining criteria must be met and considered in the design and operation of the Project although these do not necessarily have to be continuously monitored.  However, if problems are suspected at any time, Duke ET may require the Project Sponsor and/or Project Operator to demonstrate through monitoring the performance of the Project at the Connection Point meets these requirements.

If the requirements are not met, the Project Sponsor or Project Operator must demonstrate to Duke ET a plan to improve and meet the performance criteria.  Additional relay and control requirements may be developed and enforced by Duke ET after connection is made if these performance criteria are violated.  Enforcement of these performance criteria and penalties associated with them are beyond the scope of this document and will be in Project-specific contracts and operating agreements.

### Project Performance Criteria

To ensure the reliability and integrity of the supply system, all Projects must meet the Project performance criteria at the Connection Point.  The following section details the Project performance criteria.

#### Transmission System Outages

The Project may not operate its equipment or system in such a manner as to cause the unplanned outage of any Duke ET System components more than once in any twelve month period, more than three times in any five year period, or more than five times in any ten year period.  An unplanned outage is defined as the electrical isolation of equipment from the electrical system, without scheduling and notification of Duke ET, such that the equipment is unable to perform its intended function for the duration of the isolation.

#### Temporary Undervoltages

The Project may not operate its equipment or system in such a manner as to cause temporary undervoltages at the Connection Point more than twice in any twelve month period, more than five times in any five year period, or more than eight times in any ten year period.  A temporary undervoltage is defined as an oscillatory phase-to-ground or phase-to-phase voltage of 85% or less of nominal voltage lasting greater than 20 milliseconds, occurring during fault conditions.  Undervoltages due to non-fault events are covered in the in the Voltage Fluctuations and Flicker requirements.  Multiple temporary undervoltage conditions occurring within one minute will be considered the same event.

#### Transient Overvoltages

The Project may not operate its equipment or system in such a manner as to cause a peak transient voltage at the Connection Point greater than or equal to 140% of the nominal peak voltage.  A transient overvoltage is defined as the peak line-to-line or line-to-ground voltage during the transient conditions resulting from operation of a switching device.  Any transient voltage condition caused by the operation of the Project’s equipment or system that results in a peak transient voltage greater than or equal to 140% of the nominal peak voltage at the Connection Point is not allowed.

#### Temporary Overvoltages

The Project may not operate its equipment or system in such a manner as to cause a temporary overvoltage at the Connection Point greater than or equal to 120% of the nominal system voltage.  A temporary overvoltage is defined as an oscillatory phase-to-ground or phase-to-phase overvoltage lasting greater than 20 milliseconds which is undamped or only weakly damped.  Any temporary voltage condition caused by the operation of the Project’s equipment or system that results in a temporary overvoltage greater than or equal to 120% of the nominal system voltage at the Connection Point is not allowed.

#### Voltage Fluctuations and Flicker

Per IEEE Standard 1453-2004, planning levels of Pst=0.8 and Plt=0.6 define the allowable voltage fluctuation limits at the Connection Point.  In unique cases, higher limits can be considered with the understanding that the customer operating the disturbing Project will be required to mitigate the flicker that they cause, if significant customer complaints are generated.  Additionally, any single customer that creates disturbances for other customers will be required to mitigate the disturbance, regardless of the actual measured value.

Operation of the Project’s system or equipment in such a manner as to create a voltage fluctuation greater than 3% on the transmission system or on the primary of the distribution system is not allowed.

#### Harmonic Content/Harmonic Distortion

The maximum allowable harmonic current injections (percentage harmonic distortion at each frequency as a function of load current) at the Connection Point for Projects connected at 230-kV or 500-kV, 100-kV, and 44-kV are defined in Table 1, Table 2, and Table 3, respectively.  Operation of the Project’s system or equipment in such a manner as to create a condition where the harmonic current injection at the Connection Point exceeds the limits provided for in Tables 1, 2, and 3 for a duration greater than or equal to one hour on any single day or exceeds 150% of the limits provided for the given connection voltage for a duration greater than five minutes on any two days during a six month period is not allowed.

# Table 1. Current Injection Harmonic Distortion Limits: 
Connection Point Voltage >161000 V

|  | Individual Harmonic Order (Odd Harmonics) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Isc/Iload | h<11 | 11(h<17 | 17(h<23 | 23(h<35 | h>35 | TDD |
| <50 | 2.0 % | 1.0 % | 0.75 % | 0.3 % | 0.15 % | 2.5 % |
| (50 | 3.0 % | 1.5 % | 1.15 % | 0.45 % | 0.22 % | 3.75 % |

# Notes:	Even harmonics are limited to 25% of the odd harmonic limits above

Current distortions that result in DC offset are not allowed

Iload is the maximum load current (fundamental frequency component) at the Connection Point

Isc is the maximum short-circuit current at the Connection Point

TDD (Total Demand Distortion) is the total harmonic current distortion expressed in % of maximum demand load current

Table 2. Current Injection Harmonic Distortion Limits: 
Connection Point Voltage 69001 V to 161000 V

|  | Individual Harmonic Order (Odd Harmonics) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Isc/Iload | h<11 | 11(h<17 | 17(h<23 | 23(h<35 | h(35 | TDD |
| <20 | 2.0 % | 1.0 % | 0.75 % | 0.3 % | 0.15 % | 2.5 % |
| 20<50 | 3.5 % | 1.75 % | 1.25 % | 0.5 % | 0.25 % | 4.0 % |
| 50<100 | 5.0 % | 2.25 % | 2.0 % | 0.75 % | 0.35 % | 6.0 % |
| 100<1000 | 6.0 % | 2.75 % | 2.5 % | 1.0 % | 0.5 % | 7.5 % |
| >1000 | 7.5 % | 3.5 % | 3.0 % | 1.25 % | 0.7 % | 10.0 % |

Table 3. Current Injection Harmonic Distortion Limits: 
Connection Point Voltage 120 V to 69000 V

|  | Individual Harmonic Order (Odd Harmonics) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Isc/Iload | h<11 | 11(h<17 | 17(h<23 | 23(h<35 | h(35 | TDD |
| <20 | 4.0 % | 2.0 % | 1.5 % | 0.6 % | 0.3 % | 5.0 % |
| 20<50 | 7.0 % | 3.5 % | 2.5 % | 1.0 % | 0.5 % | 8.0 % |
| 50<100 | 10.0 % | 4.5 % | 4.0 % | 1.5 % | 0.7 % | 12.0 % |
| 100<1000 | 12.0 % | 5.5 % | 5.0 % | 2.0 % | 1.0 % | 15.0 % |
| >1000 | 15.0 % | 7.0 % | 6.0 % | 2.5 % | 1.4 % | 20.0 % |

#### Phase Unbalance

Unbalanced phase voltages and currents can affect protective relay coordination and cause high neutral currents and thermal overloading of transformers.  To maintain the reliability and integrity of the Duke ET System, the Project shall not operate its system or equipment in such a manner as to cause a Voltage Unbalance greater than 1% nor a current unbalance greater than 5% at the Connection Point.  Any unbalance condition in excess of the specified limits for a duration greater than or equal to one minute is not allowed.  Phase unbalance is defined as the percent deviation of one phase from the average of all three phases.

### Duke ET System Characteristics

All Project equipment connected to the Duke ET System should be designed to operate within the system conditions defined in this section.  These characteristics are typical to the Duke ET System during normal and contingency conditions, but may be exceeded for very short times or if exceptional circumstances prevail.

#### Frequency

The frequency of the Duke ET System shall be nominally 60 Hz and shall be controlled within the limits of 59.9 Hz - 60.1 Hz unless exceptional circumstances prevail.  System frequency could rise to 61 Hz or fall to 59 Hz under exceptional circumstances.

#### Steady-State Voltage Variations

The transmission system planning guidelines for voltage regulation and range at the Connection Point is listed in Table 4.

Table 4. System Voltage Variations at the Connection Point

|  | Absolute Voltage | Voltage Regulation |
| --- | --- | --- |
| Nominal Voltage (kV) | Minimum | Maximum | Normal | Contingency |
| 44 | 94 % | 109% | 8.5% | 10% |
| 100 | 95 % | 107% | 6% | 7% |
| 230 | 95 % | 105% | * | * |
| 500 | 100 % | 110% | * | * |

* On 230kV and 500kV, maximum allowable contingency drop is 5%.

#### Harmonic Voltage Distortion

The maximum harmonic voltage distortion at the Connection Point for each transmission voltage level is defined in Table 5.

Table 5. System Harmonic Voltage Distortion Limits

| Nominal Voltage (kV) | Maximum Individual Harmonic Voltage Distortion (%) | Maximum Total Voltage Distortion (%) |
| --- | --- | --- |
| 44 | 3.0 | 5.0 |
| 100 | 1.5 | 2.5 |
| 230 | 1.0 | 1.5 |
| 500 | 1.0 | 1.5 |

The limits in Table 5 represent the maximum harmonic voltage distortion at a given connection voltage for a duration less than or equal to one hour on any single day.  The maximum harmonic voltage distortion will not exceed 150% of the limits for a given connection voltage for a duration greater than five minute on any two days during a six month period.

#### Voltage Unbalance

The maximum Voltage Unbalance on the Duke ET System at the Connection Point for a duration greater than or equal to one minute will be less than or equal to 2.0%.

#### Transient Overvoltages

The maximum peak transient overvoltage at the Connection Point will be less than or equal to 200% of the nominal system peak voltage.

#### Temporary Overvoltages

The maximum temporary overvoltage at the Connection Point will be less than or equal to 180% of the nominal system voltage.  For Effectively Grounded portions of the Duke ET System, the maximum may be significantly lower than 180%.

### Switchgear

#### All Voltage Levels

Duke ET’s facilities ratings methodology was submitted to SERC in February 1999 for NERC Planning Standards compliance.  Circuit breakers, disconnect switches, and all other current carrying equipment connected to Duke’s transmission facilities shall be capable of carrying normal and emergency load currents, as defined in the SERC submittal, without damage.  For Interconnections, the equipment shall not become a limiting factor (bottleneck) in the ability to transfer power on the Duke ET System.

All circuit breakers and other fault-interrupting devices shall be capable of safely interrupting fault currents for any fault that they may be required to interrupt.  Application shall be in accordance with ANSI/IEEE C37 Standards.  These requirements apply to the generation site, the interconnecting substation, the Connection Point as well as other locations on the Duke ET System.  Minimum fault-interrupting requirements are supplied by Duke ET as part of the coordinating study, and are based on the greater of the fault duties at the time of the connection request or those projected in long-range plans.

#### Circuit Breaker Operating Times

Table 6 specifies the component operating times typically required of circuit breakers on the Duke ET System.  These times also apply to equipment at the generation site and the Connection Point.  System stability considerations may require very fast opening and reclosing times.  The total automatic recloser times would be the the summation of the breaker interrupt and close time plus intentionally added delay to allow for deionization and subsequent extinction of the fault arc (referred to as the dead timer delay), and the protective relay requirements. The following table shows Duke’s required interrupting time of the breaker and the dead “timer” delay at system voltages.

Table 6. Circuit Breaker Operating Times

| Voltage Class | Rated Interrupting Time (Cycles) | Dead “Timer” Delay (Cycles) |
| --- | --- | --- |
| 500-Kv | 2 | 30 |
| 230-kV | 3 | 22 |
| 69-kV – 100-kV | 5 | 20 |
| Below 69-kV | 8 | 20 |

#### Other Fault-Interrupting Device Operating Times

Depending on the application, the use of other fault-interrupting devices such as circuit switchers may be allowed.  Trip times of these devices are generally slower, and current interrupting capabilities are often lower than those of circuit breakers. Often circuit switchers are utilized to isolate generator step-up transformers from the transmission breakers. The dead “timer” delay on circuit switchers is typically 15 seconds and consequently, these devices usually are not reclosed.

### Excitation System and Power System Stabilizers

The excitation system shall operate in the automatic-terminal-voltage regulation mode.  For planned operation in manual mode, the plant operators shall obtain the approval of the Duke SOC in advance.  For unplanned, forced operation in manual mode, the plant operators shall notify the SOC within 1 hour of switching to manual mode.  Operation in the manual mode for extended periods shall only be permitted when approved by the SOC.

All new or replacement voltage regulators are required to have a load compensation circuit.  Based on system conditions, it may become necessary to add load compensation to existing systems.  In applications where needed, load compensation is used to control voltage at a point beyond the generator terminals (line-drop or transformer-drop compensator).  The compensator is typically set to account for 50% to 80% of the transformer impedance.  Generators whose terminals are tied directly together (cross-compound, hydro, etc.) require operation in a droop compensation mode to ensure stability.  Droop compensation effectively regulates the voltage at a point behind the generator terminals (within the generator).  In general, no two generators should be set to regulate the same point on the electric system.

A Power System Stabilizer (PSS) uses auxiliary stabilizing signals to control the excitation system to improve power system dynamic performance.  For generators that have a PSS, Duke ET will determine if the PSS needs to be put into service and will work with the generator operator to calculate appropriate settings. Based on system conditions, it may become necessary to add the PSS prior to the installation of new or replacement systems.

The latest IEEE Std. 421.4, Guide for the Preparation of Excitation System Specifications, should be consulted in designing the excitation system.  Additional requirements or a change in technical specification may be identified as a result of system studies.

The excitation system is critical to the overall system performance.  Therefore, Duke ET shall have control over and final approval of the settings for these systems (gains, time constants, limiters, etc.).  Duke ET reserves the right to specify these settings initially or revise the settings at any time during the life of the generator as warranted by system conditions.

Projects shall have a maintenance and testing program for excitation systems in compliance with applicable NERC Operating & Planning Standards and Policies.

### Governor Speed and Frequency Control

A speed governor system is required on all generators.  The governor regulates the output of the generator as a function of system frequency and desired MW output.  This function is called the governor’s ‘droop’ characteristic and must be coordinated with the governors of other generators located within the same control area, to assure proper system response to frequency variations.  All speed governor systems must respond to system frequency changes to help maintain the stability of the power system.  The speed governor system shall have a droop characteristic settable between three and seven percent and typically set to five percent.  Droop equals change in frequency or speed, in per unit of nominal, divided by change in generator load, in per unit of full load.  An example equation is: 0.05 = (0.1/60)/0.0333; where if a generator has a 5% droop setting, a system frequency change of 0.1 Hz, will cause the generator load to change by 3.33% (ignoring deadbands and other non-linearities).

See NERC Operating Policy 1 – Generation Control and Performance for additional information on speed governor operation.

Projects shall have a maintenance and testing program for the governor control systems in compliance with applicable NERC Operating & Planning Standards and Policies.

### Voltage Regulation and Reactive Power Requirements

#### Duke Transmission System Voltages

Duke ET operates its transmission system within the voltage guidelines defined below.  Projects shall have the capability to operate within the full voltage range at the Connection Point so as not to restrict the operational range of the transmission system.  Explanation of the meaning of the terms Absolute Voltage Limits, Contingency Voltage Drop, and Voltage Regulation are available in the Definitions section.

# Bulk Transmission System Voltage Guidelines

| Nominal Voltage (kV) | Absolute Voltage Limits Minimum Maximum | Maximum Allowable Contingency Voltage Drop |
| --- | --- | --- |
| 230 | 95% 105% | 5% |
| 500 | 100% 110% | 5% |

44 & 100 kV Transmission System Voltage Guidelines

| Nominal Voltage (kV) | Absolute Voltage Limits Minimum Maximum | Voltage Regulation Normal Contingency |
| --- | --- | --- |
| 100 | 95% 107% | 6% 7% |
| 44 | 94% 109% | 8.5% 10% |

#### Voltage Schedules and Operation of the Project

Major generators (as determined by Duke ET) are provided voltage schedules by the SOC.  Voltage schedules are necessary for efficient and reliable electric power transmission and for adequate service to loads.  The voltage schedules establish operating requirements for generators and may be set for seasons, holidays, days of the week, and time of day.  These schedules may be changed at any time by the SOC coordinator to meet transmission system requirements.  When requested by the SOC, Project Operators shall provide the date, duration and reason for a generator not maintaining the established voltage schedule.

Generator step-up (GSU) transformers (unit transformers) must have taps that cover the entire range of possible transmission system voltages given in the previous section, with less than or equal to 2.5% difference between adjacent taps.  The GSU tap must be set to allow the generator to produce or absorb reactive power between 0.95 leading and 0.90 lagging power factor to meet the voltage schedule.  At the same time, the plant electrical system must be designed so that all modes of unit operation are not restricted by transmission system operation within the voltage range given in the previous section.  In the project design phase, the Project Sponsor shall demonstrate to Duke ET that the Project meets these requirements.

Dynamic sources of reactive power, such as synchronous generators, are necessary to operate a reliable power system.  Therefore synchronous generators are required to participate in voltage regulation by meeting voltage schedules.  Operating requirements for each Project are determined by facility studies and/or operating experience with similar projects.  Operating requirements may be refined based on actual Project operating experience or future system changes.

1)  Synchronous generators and projects with solid-state inverters are required to produce or absorb reactive power up to the temporary thermal capability of the generator during disturbances.

The voltage regulator is set to maintain constant voltage rather than constant power factor.  The regulator set point is coordinated with voltage schedules in the area.  The Project generators are not required to operate at more than 105% or less than 95% of the nominal voltage rating of the generators under steady state conditions.  However, seasonal adjustment of the transformer tap settings may be required when voltage schedules are changed by the SOC coordinator.  It is the Project Sponsor/Operator’s responsibility to ensure that the voltage regulator is initially set up correctly to allow the full range of adjustability.  If the midpoint of the range of adjustability  (or operating range “window”) is not set correctly the ability of the regulator to be adjusted may be significantly reduced in either the raise or lower position.

Projects using induction generators (without solid-state inverters) are usually not required to participate in voltage regulation, however they must not adversely affect voltage schedules.  The facility studies determine the reactive power capability necessary to insure that these voltage schedules are maintained.

#### Reactive Power and Voltage Regulator Requirements

Each generating facility shall supply at least 0.395 Mvars (0.93 lagging power factor) of dynamic reactive power for each MW supplied at the Connection Point.  The facility shall have the capability to supply this reactive power on a continuous basis at rated MW and the transmission voltage stated below:

100 kV and below	1.00 pu

230 kV			1.00 pu

500 kV			1.05 pu

Each generating facility shall absorb at least 0.251 Mvars (0.97 leading power factor) of dynamic reactive power for each MW supplied at the Connection Point.  The facility shall have the capability to absorb this reactive power on a continuous basis at rated MW and the transmission voltage stated below:

100 kV and below	1.05 pu

230 kV			1.04 pu

500 kV			1.09 pu

1)  Synchronous generators and projects with solid state inverters.  Each Project of this type must also have a voltage regulator capable of maintaining stable voltage at the generator terminal, within 0.5 percent of any set point.  The operating range of the regulator shall be at least plus or minus five percent of the rated voltage of the generator.

The generator continuous reactive capability between 0.95 leading and 0.90 lagging power factor shall not be restricted by any main or auxiliary equipment, e.g. main or auxiliary transformer settings, hydrogen cooling system, stator water cooling system, equipment voltage or current ratings, control, protection and so on.  The generator step-up transformer shall be chosen so as not to limit the real or reactive power output of the generator.  IEEE Standard. C57.116, IEEE Guide for Transformers Directly Connected to Generators, should be consulted when specifying the step-up transformer turns ratio, impedance, etc.

Projects shall have a program to verify the gross and net reactive power capability in compliance with applicable NERC Planning Standards.

2) Projects using induction generators (without solid-state inverters) shall provide at a minimum, sufficient reactive power capability or the ‘equivalent’ to deliver the Project output at unity power factor at the Connection Point.  ‘Equivalent’ reactive power includes adding shunt capacitors at locations other than at the Connection Point or the Generation Site or acquiring sufficient reactive power from Duke or another utility.  Duke ET determines the acceptable locations for ‘equivalent’ reactive using facility studies.

Power factor correction capacitors added to the Project to meet the unity power factor requirement may need to be switchable (while energized).  Depending on the size of the Project and location on the system, these capacitors may need to be switched to participate in voltage regulation.  The control methods and set points for switching these capacitors will be coordinated by Duke ET with voltage schedules in the area.

### Voltage and Frequency Operation During Disturbances

Power system disturbances initiated by faults, forced equipment outages, etc., expose connected generators to oscillations in voltage and frequency.  It is important that generators remain in service while the oscillations are damped and the system returns to a stable operating point.  Therefore each generator must be capable of continuous operation at 0.95 to 1.05 pu voltage and 59.5 to 60.5 Hz and limited time operation for larger deviations.  Nearly all generators have inherent capability for off-nominal operation.  Over/under voltage and over/under frequency relays are normally installed to protect the generators from extended off-nominal operation.  To insure that the Project generator is not tripped prematurely, the required time delays for setting these relays are presented in the Protection Requirements section.

To avoid large-scale blackouts that can result from the excessive generation loss during a disturbance, underfrequency load shedding has been implemented throughout the Eastern Interconnection.  When system frequency declines, loads are automatically interrupted in discrete steps, with most of the interruptions between 59.3 and 58.5 Hz.  Load shedding attempts to stabilize the system by balancing the generation and load.  It is imperative that generators remain connected to the system during frequency declines, both to limit the amount of load shedding required and to help the system avoid a complete collapse.  This need, as well as the restricted ability of some generators to withstand off-nominal frequency operation, has been taken into account in the relay-setting delays provided in this document.

To avoid voltage collapse within the Duke ET System, undervoltage load shedding may be implemented in the future.  If required in the future, the Project may be required to add undervoltage relaying and coordinate undervoltage relay settings with the Duke undervoltage load shedding program.

For those generators connected to Duke through a tapped transmission line, a ‘local island’ is created when the breakers at the ends of the transmission line open.  This leaves the generator and any other loads that also are tapped off this line isolated from the power system.  Delayed fault clearing, overvoltages, ferroresonance, extended undervoltages, etc. can result from this ‘local island’ condition and are therefore not allowed to persist on Duke transmission facilities.  For protection, special relaying and settings are used to disconnect the generator(s) in the ‘local island.’  (See also Protection Requirements section.)

## Protection Requirements

The protection requirements identified in this document are intended to achieve the following objectives:

- Insure safety of the general public, Duke ET personnel, and Project personnel.

- Maintain dynamic stability.

- Prevent or minimize equipment damage.

- Minimize system voltage disturbances.

- Minimize adverse operating conditions on the Duke ET System and to Duke’s customers.

- Permit the Sponsor to operate the Project in parallel with the Duke ET System in a safe and efficient manner.

To achieve these objectives, certain protective equipment (relays, circuit breakers, etc.) must be installed.  These devices ensure that faults or other abnormalities initiate prompt and appropriate disconnection of the Project from the Duke ET System.  Protective equipment requirements depend on a number of issues.  Significant issues that could affect these requirements include:

- The configuration of the Project.  See Figures 1 and 2 below for examples

- The Connection Point to the power system.

- The level of existing service and protection to adjacent facilities (including those of other Duke ET customers and potentially those of other utilities).

In addition, certain modifications and/or additions to the Duke ET System may be required for Project connection.  Each individual connection will require a protection system consistent with these technical requirements.  Duke ET will have final approval of the protective devices required by the Project.  Duke ET works with Project Sponsors to achieve an installation that meets the Project Sponsor’s and Duke’s requirements.

Duke ET cannot assume any responsibility for protection of the Project.  Project Sponsors are solely responsible for protecting their equipment in such a manner that faults, imbalances, or other disturbances on the Duke ET System do not cause damage to the Project facilities.  The sponsor is also expected to provide proper protective systems to ensure Project Sponsor’s equipment does not adversely impact the Duke transmission system.  Sponsor should follow IEEE guide for Utility-Consumer connections (IEEE C37.95) and IEEE guide for AC generator protection (IEEE C37.102-1995).

### Protection Criteria

The protection system must be designed such that the Project generating equipment or connection point is automatically isolated for the following situations:

- Internal faults within the Project.

- External faults within the Duke ET System

- Conditions that indicate abnormal operation, including islanding of the Project.

The information below is provided to identify general protection practices as applied to Duke ET System transmission lines and connections thereto.  The protection schemes necessary to integrate the Project must be consistent with these practices and the equipment used to implement them.

#### All voltages

- A generator may interconnect to an existing transmission line only if the line protection can be coordinated without compromising reliability, system stability, or quality of service to Duke ’s existing customers.

- Relays, breakers, etc. are required at the Connection Point or the Interconnecting Substation to isolate Duke ET equipment from the Project (or the distribution system containing the Project) during faults or other system abnormalities.

- The Project is to be synchronized to the power system.  An automatic synchronizing function must supervise all closures of the breaker connecting the generator to the power system.

- Any breaker dedicated for the sole purpose of isolating the interconnecting power system or generator shall open all three phases.

- Breaker automatic reclose supervision will be required at the Interconnecting Substation and/or electrically ‘adjacent’ stations; e.g., hot bus/dead line check, synchronization check, etc.

#### 500-kV

- Two independent sets of directional line protection schemes with separate pilot communication for each relay set shall be installed at each line terminal to trip the line terminal breakers.

- Total fault clearing time with a pilot scheme must not be more than four cycles, including relay and breaker time.

- Relays shall provide back-up directional distance protection for loss of communication channel.

- Line protection may be required to be compatible with Duke ET equipment.

- Breaker failure relay (BFR) protection at the Project Sponsor’s facilities is required. Total time for BFR scheme fault-clearing must not exceed stability limits as defined for safe operation of the transmission system.

- System reliability and stability studies shall determine reclosing requirements of the transmission line/tap line.

#### 230-kV

- Two independent sets of directional line protection shall be installed at each line terminal to trip the line breakers.

- One of the protection schemes shall use pilot communications for fast clear of all line faults.

- Total fault clearing time with a pilot scheme must not be more than four cycles, including relay and breaker time.

- Pilot scheme must be compatible with existing Duke equipment.

- Relays shall provide backup directional distance protection.

- Breaker failure relay (BFR) protection at the Project Sponsor’s facilities is required. Total time for BFR scheme fault-clearing must not exceed stability limits as defined for safe operation of the transmission system.

- System reliability and stability studies shall determine reclosing requirements of the transmission line/tap line.

#### 44 & 100-kV

- Directional distance line protection with back up overcurrents shall be installed at each line terminal to trip the line terminal breakers.

- A pilot communication scheme may be required.  A scheme common to both relay sets is acceptable.

- Total fault-clearing times, with or without a pilot scheme, must be provided for Duke ET review and approval.  Breaker operating times, relay models, and relay settings must be identified specifically.

- If a pilot scheme is necessary, it must be compatible with existing Duke equipment.

- If a pilot scheme is necessary, relays shall provide backup protection for loss of channel.

- Breaker failure relay (BFR) protection at the Project Sponsor’s facilities is required. Total time for BFR scheme fault-clearing must not exceed stability limits as defined for safe operation of the transmission system.

- System reliability and stability studies shall determine reclosing requirements of the transmission line/tap line.

### Implications for Project Connection to an Existing Customer Service Substation

Many generation projects are proposed for integration into utility power systems through a transformer that is designed only to serve loads; e.g., connection at voltages normally at 24-kV or below.

Existing facilities may have protection only on the high-voltage side of the transformer; other installations may use a circuit switcher or breaker with relay control.  The device and associated relays (if any) at these sites are provided to isolate the Duke ET System from faults within the transformer and act as backup to the customers’ (feeder) protective devices.  The existing protection at these installations was applied under the assumption that there was not a source from the low-voltage side to feed faults in the transmission system.

Responsible and thorough protective relaying strategies are necessary when generation is connected into these sites.  Some issues to consider are:

- ‘Neutral shift’ can be attributed to connection into stations with a primary (high-voltage) side delta, secondary (low-voltage) side wye-grounded (D-YG) transformer.

- Ferroresonance is also cause of concern, regardless of transformer connection.

- Equipment damage, relay performance, and saturation of measuring devices are only a few of the issues.

Primary and/or backup relays used for detection of faults in the power system may be required at the Project as well as the Connection Point.  Usually, changes to existing protection and reclosing schemes are not limited to those at the Connection Point.

### Protection Measures

Under all circumstances, generators Infeed current and/or voltage effects to faults within the transmission system.  The duration of this Infeed varies with generator size, type, and excitation.  The magnitude of this Infeed depends on the fault type, system configuration, and fault location.  The discussion below describes how relaying works and identifies the conditions under which relay schemes must operate:

- Infeed detection to phase and ground faults

- Islanding

- Synchronizing and reclosing

- Unique problems related to system configuration

#### Phase fault detection

Normally, phase overcurrent (type 50/51) and neutral overcurrent (type 51TN) relays are provided to detect abnormally high currents. These non-directional relays may not be able to sense generator Infeed in the power system.

Infeed detection for faults within the power system usually requires directional current-sensing or directional power relays to remove the Project’s contribution to the fault.  Zone-distance relays (type 21) can also serve this need.  However, some generation projects (generally ‘small-capacity’) may not contribute sufficient Infeed to power system phase faults to make distance-relay detection feasible.  In these cases, relays at the Project need to provide the necessary detection and fault isolation.

#### Ground fault detection

Ground fault detection has varying requirements.  The most significant consideration in ability to detect ground faults on the utility power system is the winding configuration of the transformer connecting the Project to the transmission system.  The scenarios below assume that the Project is connected to the low-voltage side of this transformer.

##### Transformer grounded wye connection on the transmission side

If the transformer is connected in grounded-wye on the primary (high-voltage) side and delta on the secondary (low-voltage) side (YG-D), then a ground overcurrent relay (type 51TN) connected in the neutral of the wye is used to provide detection.  This relay also protects the integrating transformer.  This arrangement also applies to a grounded- wye primary, grounded-wye secondary connected (YG-YG) transformer with delta tertiary.  Either of these connections provide what is often referred to as a ‘ground source’ for the wye grounded terminal(s).  The measured quantity in the transformer grounded-wye neutral is caused by zero-sequence circulating currents in the delta winding during ground faults.

If the generator/grounded-wye transformer contributes over 30% of the total ground current for a line phase to ground fault, then additional line protection may be required to safely isolate faults on the transmission system.

##### Transformer Delta Connection on the Transmission Side

Under the second common scenario (the most common configuration used at Duke ET customer service substations), the connecting transformer is D-YG.  For ground faults on the high voltage system, protective relaying cannot detect zero sequence current at this location unless a ground source (grounding bank) is connected to the high-voltage side of the transformer.  Protective relay operation at the remote transmission line terminal(s) will isolate the line.  However, the generator Infeed (voltage effect) will continue to energize the transmission line and, with one phase grounded, can result in significant overvoltages (neutral shift).  Thus a voltage protection scheme must be applied to this situation to detect the fault and trip the generator and/or the Project as rapidly as possible.

A detection method for this situation uses voltage sensing devices on the primary side of the transformer connected phase-to-ground.  The voltage sensing shall monitor all three phases in an open delta connection or monitor one phase in an over/under voltage scheme.

Pilot trip from the end(s) of the transmission line is an acceptable alternative.  A grounding bank connected to the high side (delta side) of the interconnecting power transformer is another acceptable alternative.

#### Islanding

Islanding describes a condition where the power system splits into isolated load and generation groups, usually when breakers operate for fault clearing or system stability remedial action.  Generally, the ‘islanded groups’ do not have a stable load to generation resource balance.  However, it is possible that, under unique situations, generator controls can establish a new equilibrium in an islanded group.

When Duke ET customer loads are being served over the utility’s transmission system, where generation is also interconnected, implications of islanding must be addressed to minimize adverse impacts on these loads.  If a generator can be islanded, then additional protection is required to prevent this.  Based on protection studies either a transfer trip scheme will be required or additional relays at the Project will be required to monitor voltage and frequency. The additional relays are applied as necessary to protect Duke ET customer loads from damage: over/under voltage (type 59/27), and over/under frequency (type 81).  These relays are intended to trip the generator for the large voltage and frequency deviations that would tend to occur during a ‘local’ island condition.  However, they are also set so the generator does not trip for the less severe deviations that could occur during most major disturbances on the interconnected power system.

#### Synchronizing and Reclosing

The Project generator(s) shall be synchronized to the power system.  The point of synchronism depends on the configuration of the Project’s connection.  All closes of the breaker synchronizing the Project generator to the power system must be supervised by an automatic synchronizing function.  The breaker used to synchronize the generator to the power system is usually the dedicated generator breaker.

#### Line Reclosing

If the Project includes a synchronous machine and connects to an existing line, automatic reclosing schemes at the remote line breakers may include either time delay or instantaneous reclosing. The reclosing time intervals are based on system requirements.  Typical reclosing times are instantaneous (approximately 20-30 cycles) and/or voltage supervised reclosing (1.5 seconds).  Even if an existing line is set up for time delay reclosing Duke ET reserves the right to change the reclosing to instantaneous reclosing if the system requirements change.

If Duke ET’s line reclosing is instantaneous and no other customers are on that line then Duke ET may elect to delay reclosing for the Project’s generators.  Duke ET reserves the right to change the reclosing back to instantaneous if the system requirements change.  The Project Sponsor/Operator should be notified well in advance of any changes in the reclosing times to allow the Project Sponsor/Operator to make any necessary adjustments.  If the instantaneous reclosing still presents a problem then the Project Sponsor/Operator may want to consider some other options to insure that the system will not reclose back until their generators are off line.  There are two options the Project Sponsor/Operator may want to consider:

Option #1.  Transfer Trip.  The transfer trip signal can be transmitted via a carrier channel or by transmitting over a leased phone line. In addition transfer reclose can be added at an additional cost.  This will help insure that the Project has received a trip signal before Duke ET closes back.  If the signal is not received then the source breaker will close time delay regardless of the situation.  The time delay reclose will be voltage supervised.

Option #2.  Voltage Supervision On Instantaneous Reclosing.  A potential device along with an undervoltage relay can be installed to help insure that Duke ET will only reclose if the relay senses a dead line.  The voltage sensing devices can be installed on one phase, two phases or even all three phases depending on what the Project Sponsor/Operator desires.

#### Disturbance Monitoring

Unique and unanticipated protection problems can result from the changed system configuration due to connection with the Project.  Duke ET may, at its discretion, install monitoring equipment to identify possible protection scheme problems and to provide power quality measurements of the new configuration.  If relay performance indicates inadequate protection of the Duke ET  System, the owner of the Project will be notified of additional protection requirements.  The monitor provides information similar to that of an oscillograph or fault recorder.  The availability of current and voltage measurements determines the number of channels for the device.  Monitoring equipment is also installed to aid in the understanding of the electrical phenomena, such as overvoltages and ferroresonance, that can be associated with these projects.  (Duke ET plans to use the information acquired to update future editions of this document.)  Remote access to monitored quantities is often accomplished using communication equipment.

### Protective System Coordination

A relay coordination study will need to be performed to insure proper operation of the generator and/or transmission line protection equipment.  The Project Sponsor shall provide all requested protective relay drawings, protection settings, setpoint calculation studies, and associated equipment data for protective relays that will detect faults on the Duke ET System for a coordination study and design review.  Any Project settings that will not coordinate or will adversely affect the proper operation of the transmission system will need to be adjusted.

Adequate protection scheme redundancy should be considered to ensure local isolation of faults.  In addition, protection scheme modifications should be considered to remove any single points of protection scheme failure identified that could require remote station devices to isolate local faults.

### Protective System Maintenance

The Project Operator will perform Project equipment maintenance on a regular schedule.  This is to include the following:

- Functional testing of trip circuit

- Functional testing of interrupter

- Calibration testing of protective devices settings

- Inspection and maintenance of power dc sources

- Inspection and maintenance of interrupter

### Protective System Fault Analysis

All operations of protective devices within the Project should be reviewed and documented. This information should be available to Duke ET on request to assist in analyzing fault operation on the Duke ET System.  To facilitate the analysis of system disturbances and the evaluation of system operation, fault recorders may be required on certain types of complex substations and at all major generating stations connected to the Duke ET System.  Fault recording functions in microprocessor relays may provide the detail data needed to perform the analysis.

### System Modifications Beyond the Connection Point

System modifications to the Project must be reviewed by Duke ET before changes are made.  These changes are defined as changes in interrupters, lines, transformers, protective devices and protective settings. This review is needed to insure proper operation of the power systems and coordination of protective devices.

Figure 1  Integration of Generation into an Existing Customer Service

# Figure 2  Integration of Generation into a Transmission Line

## System Dispatching, Operation & Control, Power Scheduling, and Reserves

### General

All Project Operators are required to contact the Duke SOC prior to starting generation and connecting the generation to the transmission system.  In addition, metering that is telemetered to the Duke SOC is required for all Projects.

### Scheduling

Projects may be required to submit energy schedules to the Duke SOC prior to the hour of operation.  This requirement is dependent on the size of the generation output, the service that the Project is supplying and the location of the Project’s delivery.  If the Project is delivering its output outside the Duke Control Area, an hourly schedule must be submitted.  All schedules must be submitted in accordance with Duke Power’s scheduling standard.  In addition, for deliveries outside of the Duke Control Area, transmission reservations and access must be acquired through the Duke OASIS in accordance with the Duke’s Open Access Transmission Tariff.

### Load Following

If Duke has entered into a contract for the Project to provide Load Following service, then an agreement between the parties will be developed that specifies the terms and conditions of that service.  At a minimum, telemetry will be required from the Project to the Duke SOC.

### Regulation

In order for a Project to provide regulation service to Duke, the Project must be under the Duke System Operating Center’s Automatic Generation Control (AGC).  Pulsing capability of the unit must be provided to the SOC, and the Project must be operating under the terms and conditions of the contract that will be established for the Project to provide Regulation Service.

### Reserves

If Duke has entered into a contract for the Project to provide operating reserves to the Duke Control Area, then an agreement between the parties will be developed that specifies the terms and conditions of that service.  At a minimum, the capacity of the Project must be under contract to the Duke SOC for its use as specified in the agreement.

## Metering and Telecommunication Requirements

All Projects that are connected to the Duke ET System will require revenue-accuracy-metering equipment (i.e. metering enclosure with meter and associated equipment, instrument transformers, and certain interface enclosures with associated isolation devices).  This section states the minimum requirements for metering and telecommunication associated with a generation connection or Interconnection to the Duke ET System.

### Supervisory Control and Data Acquisition (SCADA)

Requirements will be determined on a case-by-case basis depending on the location of the generating facility, the number and size of the units, and the extent to which the SOC will control the generators.

Normally, all generators larger than 10 MVA or sites with greater than 50 MVA aggregate capacity must be equipped with SCADA to ensure that the SOC has the information necessary for monitoring response to SOC operating instructions and for maintaining system reliability.

The following data may be required:

- Generator breaker(s) status (if not installed, then the status of the generator isolation device(s) shall be provided instead

- Generator step-up transformer high voltage breaker status

- Status of any other high voltage breaker at the site

- Status of the Connection Point isolation device(s)

- Generator MW and MVAR output

- Voltage of the bus controlled by the generator(s) (may be its own low voltage bus or the bus at the high voltage terminals of the step-up transformer

- Generators providing Automatic Generation Control (AGC) service will require additional SCADA capability

### Metering

Metering equipment should be installed, if possible, at the Connection Point.  If not installed at the Connection Point, then power transformer and/or line losses will need to be considered.

#### Metering Equipment Requirements

A solid state meter shall be used to measure the real and reactive power interchange between the Duke ET System and the Project. Three-element, three-phase, four-wire meters shall be utilized on wye connected power systems. Two-element, three-phase, three-wire meters shall be utilized on delta connected power systems.

A bi-directional watt/var-hour meter should be utilized to measure the power flow in and out of the Duke ET System.

For metering equipment located in the Project substation, the installation of a metering bypass is suggested, but not required. For the replacement of failed or malfunctioning equipment a metering bypass is necessary to maintain power flow to the Project. If a metering bypass is not installed, an outage will be required to replace the failed or malfunctioning equipment.

The metering devices must be fully compatible (approved meter type and communication media) with Duke ET System’s remote metering and data acquisition system.

#### Meter Accuracy

Meters shall be calibrated to 0.5% accuracy at unity power factor for both full load and light load. These meters shall be calibrated to 1.0% accuracy for 0.5 power factor at full load. Metering accuracy limits are stated in the following table.

| METER ACCURACY LIMITS |
| --- |
| Watt-hour Function | Var-hour Function |
| Full Load | Power Factor | Light Load | Power Factor |
| +/- 0.5 | +/- 1.0 | +/- 0.5 | +/- 1.0 |

# Notes:

- Watt-hour and var-hour functions should be tested in both directions of energy flow (In and Out).

- When compensating for transformer or line loss, utilize stated limits above or 5% of desired compensation, whichever is greater.

- The meter shall be tested with compensation applied to obtain a true test of the installation.

| Test Points | Volts | Amps | Power Factor |
| --- | --- | --- | --- |
| Full Load | 120 | 5 | 1.0 |
| Power Factor | 120 | 5 | 0.5 |
| Light Load | 120 | 0.5 | 1.0 |

#### Instrument Transformers

Voltage and current transformers shall be 0.3% metering accuracy class for both magnitude and phase angle over the burden range of the installed metering circuit. Instrument transformer correction factors may be applied to the meter to adjust the meter for inaccuracies associated with the secondary burdens in the current transformer and voltage transformer circuits.  In bi-directional situations where there are significant differences in the magnitude of capacity delivered to the Duke ET System compared to the load supplied by it; good engineering practices should be in place to accurately meter power flow in both directions.  All instrument transformers shall comply with ANSI/IEEE Standard C57.13.

#### Loss Compensation

If the metering is not located at the Connection Point, then power transformer and/or line loss compensation will need to be considered. Duke ET approved power transformer and/or line loss compensation values should be applied to the meter to properly compensate for the losses in the power transformer and/or line.

#### Access to Metering Data

If access to the meter is required, proper security measures must be taken to ensure the integrity of the meter is not compromised. If data pulses are required from the revenue meter, then the appropriate interface box with associated equipment must be installed to properly protect the revenue meter.  If an additional information meter is requested, good engineering practices must be adhered to when terminating the connections in the meter circuit to ensure the integrity of the revenue-accuracy metering circuit is intact.

#### Station Service Power

Metering requirements for the Station Service Power, if any, will be determined on a case-by-case basis.

#### Calibration of Metering Facilities

Metering facilities shall be tested and calibrated if necessary every two years. More frequent test intervals may be negotiated. All interested parties or their representatives may witness the calibration tests. Calibration records shall be made available to all interested parties. The accuracy of the standard utilized for calibration purposes shall be traceable to the National Institute of Standards and Technology, (NIST).

### Voice Communications

Voice communication is required between the Duke SOC and the Project Operator.   A typical phone line at the Project may be sufficient to supply this communication path.  In the event that the Project is supplying additional services (AGC, load following, reserves, system restoration, etc.) or if the Project is in excess of a specified generation capacity, back-up communication with the Project may be necessary and can be specified by Duke Energy.

Independent voice communications for coordination of system protection, control, and maintenance activities between Duke and the Project may be required in addition to the voice communications specified above.

### Data Communications

All generating facilities and transmission facilities are required to have in place, a means of transmitting monitoring, accounting, and control data where appropriate to the Duke Energy control center(s).

a)  SCADA requirements consist of either leased phone lines, microwave channels, or fiber-optics from the site to the SOC or the TCC.  Factors involved in selecting a type of circuitry are availability, proximity to the site, and cost.  Fiber is preferred. These are dedicated channels and are not redundant.

b)  Data for AGC calculations and control is transferred to both of the above centers at a telecommunications rate of 2400 baud.

c)  Accounting data is transferred from the site through an on-site Remote Terminal Unit (RTU) to the centers in a. above through any one of the above mentioned data communication circuits.

### Telecommunications for Revenue-accuracy Metering

A compatible and reliable communication media must be provided and maintained, to enable Duke ET to interrogate the meter, collect, merge, and store metering and usage data with Duke ET System’s remote metering and data acquisition system.

### Telecommunications for Control & Protection

Telecommunication channels may be used for Pilot Relay Protection or Direct Transfer Trip if performance of the channel and the equipment meets the Control and Protection requirements of the connection.

Communications for Protection must function at the full performance level before, during, and after any power system fault condition (Service Performance Objective Class A per IEEE Standard 487).

#### Speed of Operation

Throughput operating times of the telecommunications system must not add unnecessary delay to the clearing or operating times of protection or remedial action schemes. Maximum permissible clearing times for faults are specified in Protection Requirements section of this standard. The throughput operating times of the telecommunications system is only a portion of that total clearing time.

#### Equipment Compatibility

In order to provide maintainability and operability between the Project and the Duke ET System, teleprotection terminal equipment such as transfer trip units shall be functionally compatible.  'Tone' equipment must be of the same manufacturer and type.  The need or implementation of peripheral capabilities such as signal counters, test switches, etc. are not required to be identical to those used at Duke ET facilities.  Duke ET prefers the use of terminal equipment that is the current Duke standard for the control application.  Duke ET will consider the use of alternative equipment and/or technologies as proposed by the Project Sponsor as long as the equipment is suitable for the purposes of the control application required.

## Exceptions

The requirements specified in this section, Facility Connections Requirements – Generation and Interconnection Facilities, apply to all generators.  New contracts should be written to comply with this document.  Existing contracts take precedence over these requirements.  Existing non-compliant generators must submit a plan and schedule for meeting the requirements.  Under rare circumstances the Project Sponsor/Operator may be granted an exemption from meeting one or more of the requirements.

# REFERENCES

Occupational Safety and Health Administration (OSHA) standard 29 CFR 1910.269

# National Electrical Safety Code (NESC)

# Duke Power Safe Work Practices Manual

# Duke Electric Transmission Operating Procedures Manual

# Uniform Building Code (UBC)

# ANSI/IEEE Std. 80, IEEE Guide for Safety in AC Substation Grounding

IEEE - 81 Part 1: Guide for Measuring Earth Resistivity, Ground Impedance, and Earth Potentials

IEEE - 81 Part 2: Measurement of Impedance and Safety Characteristics of Large, Extended or Interconnected Grounding Systems.

IEEE – 837, Standard for Qualifying Permanent Connections Used in Substation Grounding

# IEEE – 487, Protection of Wire-Line Communication Serving Electric Power Stations

ANSI/IEEE 367, IEEE Recommended Practice for Determining the Electric Power Station Ground Potential Rise and Induced Voltage from a Power Fault

# North American Electric Reliability Council (NERC) Planning Standards

# NERC Operating Policy 1 – Generation Control and Performance

# ANSI/IEEE – 665, Guide for Generating Station Grounding

# IEEE – Std. 421.4, Guide for Preparation of Excitation System Specifications

# IEEE Std. C57.116, IEEE Guide for Transformers Directly Connected to Generators

IEEE Std. C37, IEEE Standards for Circuit Breakers, Switchgears, Substations, and Fuses Standards Collection.