| Transmission line & substation Projects |
| --- |
| Company: EnterGy Services, INC. |
| Customer: AFS 2012-002 |
| Facilities study |
| ejo # F4PPMS0282 |
| AFS 2012-002 |
| AFFECTED SYSTEM FACILITIeS STUDY |
| Revision: 2 |
| Rev | Issue Date | Description of Revision | Prepared By | Approved By |
| 0 | 01/10/13 | Submitted to PD | KC | RT |
| 1 | 02/04/13 | Updated based on setting evaluation | IK/KC | RT |
| 2 | 02/04/13 | TPD Approval | RB | BW |
| * Note: All required JET approvals and other stakeholder concurrences are shown in the voting polls in eRoom. |

table of contents

1.	PROJECT SUMMARY	3

1.1.	Background and Project Need	3

1.2.	Scope Summary	3

1.2.1.	Financial Rights for Supplemental Upgrades	3

1.2.2	Entergy System Modeling and Relay Settings	4

1.3.	Cost Summary	4

1.4.	Schedule Summary	4

1.5.	Automatic Generation Control	5

2.	SAFETY Requirements	5

3.	GENERAL ASSUMPTIONS	5

4.	SCOPE of work	5

4.1	Entergy System Modeling and Relay Settings	5

5.	COST	6

6.	UPGRADE CLASSIFICATION	6

7.	SCHEDULE	7

8.	RISK ASSESSMENT	7

9.	Confirmed Reservations	7

10.	Attachments	7

# PROJECT SUMMARY

## Background and Project Need

This Affected System Impact Study is based on the AFS 2012-002 request for interconnection of 150MW of wind generation on CLECO’s transmission system located on the Coughlin – Plaisance 138kV transmission line for commercial operation by 31 December, 2013.

The generator will be connected to a new CLECO Substation called Napoleon.

Napoleon Substation will be connected to the CLECO 138kV line between Coughlin and Plaisance.

Plaisance Substation is connected to Entergy Champagne Substation through L636 (Entergy Gulf Louisiana – EGSL).

The purpose of this Facilities Study is to determine if there are any impacts to Entergy’s system due to this generator interconnection.

The previously completed System Impact Study performed by Southwest Power Pool ICT (PID-AFS-2012-002) indicated that a short circuit and stability study were unnecessary due to the low short circuit contribution and use of a non-synchronous tie.

Since the generator is interconnecting on CLECO system, Entergy is not required to develop the scope of work for the interconnection. Instead, Entergy will determine the required relay setting changes needed on their system.

## Scope Summary

## Financial Rights for Supplemental Upgrades

Not applicable

## Entergy System Modeling and Relay Settings

Entergy Relay Setting group has performed evaluation of system model for connecting 150 MW wind generator on Cleco system and lines connecting to Entergy.  In compliance with Entergy policy PRC-001, the following actions are recommended as a prerequisite to connecting the generator to the grid:

- No need to revise settings on over current relays at Entergy owned Champagne substation since the change in fault current due to the proposed DEGS wind farm is negligible.  However,

- Changes to settings on Plaisance line panel at Entergy owned Champagne substation would be required.  
This is due to fact that 61% change would incur in the impedance of CLECO’s Plaisance-Coughlin 138kV line.  This will result in the need to reduce the reach of zone 2 and zone 3 at Entergy’s Champagne 138 kV substation for the Plaisance line panel.

## Cost Summary

The estimated total cost of performing the study to determine required relay setting changes is $25,494. This does not include Tax Gross Up which may apply if and where applicable (Tax Gross Up rate at this time is 27.15%).

Approval to commence work should be provided by no later than 6/1/13.

The ICT has assigned $______ as Base Case upgrades and $_______ as Supplemental Upgrade based on Attachment T of Entergy’s Open Access Transmission Tariff (“OATT”).

## Schedule Summary

The proposed commercial operation date of this interconnection is December 31, 2013.

The schedule for the study and implementation of settings, should they be required, would be as follows:

- Approval from customer to proceed with revision of settings by 06/01/13;

- Completion of calculations for revision of relay settings and issuance to the field by 09/06/13;

- Completion of implementation of revised relay settings in the filed by 11/25/13.

Notes:

1)  Revision of settings may require line outage.  Some outages are required to be reserved a year ahead of time.  Therefore, earlier completion of evaluation and issuance of revised relay settings would minimize the risk.  Nonetheless, this risk could result in delay of interconnection of generators by 12/31/13.

## Automatic Generation Control

- Not applicable

# SAFETY Requirements

- None identified for scope described in this document

# GENERAL ASSUMPTIONS

- Communicate the project and protection coordination with nuclear, generation plants, load customers and other interconnected utilities as appropriate.

- Comply with PRC-001, PRC-023 and relevant procedures, standards and guidelines as appropriate.

- Modify the Webtop Folders according to the project.

# SCOPE of work

## Entergy System Modeling and Relay Settings

See section 1.2.2 above

# COST

The ICT has reviewed and determined whether each required upgrade will be considered a Base Plan Upgrade or a Supplemental Upgrade.  For more information on cost responsibility for Base Plan and Supplemental Upgrades, see Attachment T to Entergy’s OATT.

The costs shown in the table include all applicable overheads but do not include tax gross up. Entergy incurs a tax liability proportional to the amount of customer contributions.

|  | 2013 | Total |
| --- | --- | --- |
| Direct | $ 21,280 | $ 21,280 |
| Indirect | $ 4,214 | $ 4,214 |
| Total | $ 25,494 | $ 25,494 |

Note – this estimate is only for performing calculations for revising line relay settings and to apply them in the field.

# UPGRADE CLASSIFICATION

The ICT has reviewed and determined whether each required upgrade will be considered a Supplemental Upgrade. For more information on cost responsibility for Base Plan and Supplemental Upgrades, see Attachment T to Entergy’s OATT.

| Task | Total Cost | Base Plan | Supplemental | FFR Payment | Section |
| --- | --- | --- | --- | --- | --- |
| Perform study to determine changes to relay settings | $25,494 |  |  |  |  |
| Total | $25,494 |  |  |  |  |

# SCHEDULE

- The proposed commercial operation date of this interconnection is December 31, 2013.  See details in section 1.4.

# RISK ASSESSMENT

| Risk | Comment | Impact |
| --- | --- | --- |
| Outages may not be available | See notes in section 1.4 | ** |

** - moderate impact to schedule for work described in this document

# Confirmed Reservations

Not applicable

# Attachments

- Generator Interconnection (attached)

- Champagne Substation Oneline (attached)

- Table of Acronyms

| ACSR | Aluminum Conductor Steel Reinforced |
| --- | --- |
| ACSS | Aluminum Conductor Steel Supported |
| ADEQ | Arkansas Department of Environmental Quality |
| AFUDC | Allowance for Funds Used During Construction |
| ATC | Available Transfer Capability |
| EES | Entergy Control Area |
| EHV | Extra-High Voltage |
| ERIS | Energy Resource Interconnection Service |
| ICT | Independent Coordinator of Transmission |
| IPO | Independent Pole operated |
| kV | Kilo-Volt |
| MCM | (M) Thousand Circular Mils |
| MVA | Mega-Volt Amp |
| MW | Mega-Watt |
| NPDES | National Pollution Discharge Elimination System |
| NOI | Notice of Intent |
| NRIS | Network Resource Interconnection Service |
| OASIS | Online Access and Same-time Information System |
| OATT | Open Access Transmission Tariff |
| POD | Point of Delivery |
| POR | Point of Receipt |
| SES | Steam Electric Station |
| SOC | System Operations Center |
| SHV | Super High Voltage |
| SW | Switch Station |
| TOC | Transmission Operations Center |