Summary Orange Cogen Event on October 7, 2008

According to FPSC Rule 25-17.086, “Periods During Which Purchases are Not Required”, Progress Energy Florida (PEF) is providing notice to the Florida Public Service Commission that PEF reduced the output of the Orange Cogen facility by 20 MW on 10/07/08 from 1409 hours until 1939 hours.  The Orange Cogen facility is interconnected to the PEF transmission system at PEF’s Orange Switching substation.  PEF took this action in its capacity as Transmission Operator in order to ensure the reliability of the transmission system and prevent equipment damage.

The incident began at 14:00 hours on 10/07/08 when the 69 kV line from Homeland substation to Mulberry substation tripped out of service due to a fault caused by an Osprey nest falling onto the conductors.  This line is one of two lines that transport Orange Cogen’s output south from the plant.  A single line carries the plant’s output to the north; the Orange Switching substation to North Bartow substation 69 kV line.

Neither of the two lines going south is capable of carrying the full load output of Orange Cogen alone.  When one of these two lines are forced out of service, for the loss of the line going north (first contingency) the remaining line would be forced to carry the full output of the Orange Cogen and would be overloaded beyond its emergency rating.  This line, Homeland substation to Ft Meade substation, has the City of Ft Meade and Pembroke substations tapped to it.  There are significant customer loads fed from these two substations.

Prudent operating practice as well NERC standards require that PEF mitigate first contingency System Operating Limit Violations (SOLVs), such as the one for this event on a pre-contingency basis.  After executing contingency studies and identifying the constraining parameters, at 14:09 PEF contacted Orange Cogen and requested that the unit reduce output by 20 MW.  After execution of the request, post contingency loading of the monitored element (remaining line) was reduced to 100% of its normal operating limit.

Crews were dispatched immediately to locate the fault on the 69 kV line from Homeland substation to Mulberry substation, isolate it, and perform repairs.  At 19:34 the fault was cleared and the line was switched back in service.  At 19:39 PEF contacted Orange Cogen and released their 20 MW constraint.