FPL Available Transfer Capability Implementation Document

Revision History

| Rev | Changes | Author | Approver | Date |
| --- | --- | --- | --- | --- |
| 0 | Initial Draft | JCR/DAM | DAMc | 3/24/11 |
| 1 | Modified TRM section to reflect change in TRM methodology and application | DAMc | DAMc | 6/14/12 |
| 2 | Modified to address requirement R3.6.3 | DAMc | DAMc | 9/8/2012 |
| 3 | Revised Communications/Coordination section page 13. Revised rollover language to clearly indicate rollovers will be continued if status is indeterminate Revised algorithms to conform to MOD-028 terminology for TRMs and CBMs Modification of counter flow language to incorporate treatment of long term firms | DMcI | DAMc | 4/11/2013 |
| 4 | Modified counterflow language to include non-firm and Florida Southern exception Modified Other services to change “ may” to “will” and remove distribSution factor criterion | DMcI |  | 7/29/2013 |
| 5 | Clarified counterflow language to specify where counterflow is applied. | BMB |  | 8/9/2013 |
| 6 | Removed Appendix B. Added language to page 9 to specify that for FPL the counterflowF term is zero | DMcI |  | 10/11/2013 |
| 7 | Formatting Changes | BMB | MY | 7/23/2014 |
| 8 | Adding Powersouth Cooperative as coordinating entity for attachment 1 | AM | AM | 07/13/2022 |
| 9 | Implement NAESB WEQ standards after retirement of MOD-001, 004, 008, 028, 029, and 030 | AC |  | 1/30/2024 |

FPL ATC Implementation Document (ATCID) 
Algorithms and Formulae

This document serves as FPL’s Available Transfer Capability Implementation Document (“ATCID”) and describes the methodology that Florida Power and Light (“FPL”) uses to calculate Total Transfer Capability (“TTC”) and Available Transfer Capability (“ATC”).  FPL, along with other Florida Reliability Coordinating Council (“FRCC”) members, uses an ATC/TTC calculation software program that is provided and hosted by Open Access Technology International, Inc. (“OATI”). This calculator software program along with OATI’s WebTrans product is collectively known as the “Engine”. Members of the FRCC, including FPL, have formed the Florida Transmission Capability Determination Group (“FTCDG”) in an effort to provide ATC values to the regional electric market that are transparent, coordinated, timely, and accurate.  The methodology and criteria conform to the applicable North American Electric Reliability Corporation (“NERC”) Reliability Standards, as approved by the Federal Energy Regulatory Commission (“FERC”).

- Methodology (WEQ-23-1.1, WEQ-23-1.1.1)

FPL has elected to use the Area Interchange Methodology as described in WEQ-23-1.1 to calculate ATC for all paths.  If in the future a different methodology is selected for other paths this document will be modified accordingly.

- Calculation Frequencies (WEQ-23-1.2)

Calculations of TTC along with the subsequent ATC calculation for each individual path are performed at the following frequencies.  Additionally, ATC values are continuously updated when reservations are processed.

- Hourly TTC values are calculated for Hours 1-72 with an hourly update frequency.

- Hourly TTC values are calculated for Hours 73-168 with a daily update frequency.

- Daily TTC values for Days 1-7 are determined by the most restrictive of the hourly values for that day.

- Daily TTC values are calculated for Days 8-31 with a weekly update frequency.

- Daily TTC values are calculated for Months 2 -13 with a weekly update frequency.  Monthly values are derived from these calculations based on the most restrictive day of the month.

In the event of an unexpected outage of a 500kV transmission facility or a transformer with a low side voltage of 200kV or higher, TTC numbers will be recalculated within 24 hours, accounting for the outage provided that the outage is expected to last longer than 24 hours.

FPL functions as both a Transmission Operator and a Transmission Service Provider.  Through integrated software, calculated TTC values are immediately delivered for use in ATC calculations at intervals equal to or better than the specified times of WEQ-023-2.1.2.

  - Horizon Definitions

Based on the FERC definitions:

The Scheduling Horizon refers to the same day and real-time.
The Operating Horizon refers to the day ahead and pre-schedule.
The Planning Horizon refers to the time beyond the operating horizon.

Within the calculation software, FPL defines the following time intervals:

  - Scheduling Interval

This is a moving window extends from the current hour through the next eight hours.

  - Operating Interval

This is a moving window that extends from the end of the Scheduling Interval to hour 24:00 of the next day.  At hour 10:00 the Operating Interval expands to include all of the current day through hour 24:00 of the following day. On Fridays at 10:00 this expands to include all of the weekend and Monday until hour 00:00 of Tuesday.  If the following day is a holiday the window expands further to include the entire holiday.  This concept also applies if a holiday occurs anytime in the week.

  - Planning Interval

This window begins at the end of the Operating Interval and extends 13 months from the current date.

- Process Flow Diagram

Following is a process flow diagram illustrating the various steps through which TTC/ATC is calculated.

- Total Transfer Capability (TTC) Calculation

  - Definition of TTC:

The amount of electric power that can be moved or transferred reliably from one area to another area of the interconnected transmission systems by way of all transmission lines (or paths) between those areas under specified system conditions. <From NERC Glossary of terms>

  - Contractual Obligations

FPL’s limits its TTC to the lower of physical limitations, the sum of its tie facility ratings with the other entity participating in the transfer or any contractual limitations including allocated share.

  - ATC Paths

FPL calculates ATC for commercially viable paths and to all control areas to which it is directly connected.  The source used for ATC is obtained from the Point of Receipt (POR) field of the transmission reservation. The sink used for ATC calculations is obtained from the Point of Delivery (POD) field of the transmission service reservation.  Each POR/POD corresponds to an “area” within the model and physically represents a Balancing Authority (BA), a specific generation site, or a subset of generation within a BA.  The TTC calculated for each path is based on an area to area transfer.  In the specific case of Florida Municipal Power Pool, the BA is represented by multiple POR/PODs which have TTC that is obtained by determining the percentage participation of that particular group of generation in the total transfer of the area.

For merchant generation sites less than a cumulative total of 75MW located within the FPL Balancing Area (BA) individual paths are not provided.  For sales to external BA’s these merchants reserve capacity on the direct FPL ATC paths but with a different Source identifier.  For sales to FPL a single path designated as 
F/FPL/FPL-FPL/EMBED-FPL is used.

Non-native network loads embedded within the FPL BA reserve capacity on the direct FPL ATC paths but with a different Sink identifier.  For sales from FPL to these non-native network loads a single path designated as F/FPL/FPL-FPL/FPL-EMBED_LD is used.

  - TTC Calculation Methodology (WEQ-23-1.1.1.2, WEQ-23-1.3.2, WEQ-23-1.4, WEQ-23-1.4.1, WEQ-23-2.1.1, WEQ-23-1.1.1.1)

OATI creates base case load flow models for each TTC calculation period by taking the base topology model to which it makes the adjustments described in steps i-vii below.  The loads, outages, topology, interchange, generation dispatch and other assumptions used to perform these calculations are either the same or less limiting than the assumptions used in planning of operations for the corresponding time period studied.

    - Beginning with this base case model, the First Contingency Incremental Transfer Capability ("FCITC") for each transmission path is calculated.  The generation is increased in the source area and decreased in the sink area, according to the merit order.  The transfer capability increases until either a base or contingency System Operating Limit (SOL) violation occurs, provided the transaction has at least a 5% Outage Transfer Distribution Factor (OTDF).  The value of the transfer calculated when the violation is reached is listed as the FCITC.

If the source area’s generation is fully dispatched and a SOL violation has not been reached, a limited amount of artificial generation is added to that area and dispatched until a SOL violation occurs; otherwise the FCITC equals the value at which the maximum adjustment was applied.  If the sink area‘s generation is fully reduced to zero before a SOL violation occurs, the flow to the sink area is increased through the use of an artificial negative generator until a SOL violation occurs; otherwise the FCITC equals the value at which the maximum adjustment was applied.

The final value of TTC is the lower of the sum of Facility Ratings of all ties comprising the ATC Path, contractual limitations for the path, or the FCITC added to the “impacts of firm transmission services.”  The value for this “impact of firm transmission service” is based on the transmission services modeled in the study case.

FPL monitors the loading of the system facilities in the pre-contingency and post-contingency state and limits ATC on a given path if the transfers on that path result in the loading of the monitored facility to exceed its rating. Identified system voltage, transient stability, voltage stability limits and other SOL’s are less limiting than those of facility ratings.

    - Base models are derived from the current FRCC Transmission Working Group (“TWG”) seasonal models and represent the network topology for the entire FRCC region as well as the Sub-region of the South East Reliability Council (SERC) region immediately adjacent to the FRCC.  The remainder of the SERC is an equivalent representation in the models. These models contain detailed generation and transmission facilities and their associated ratings as specified by the Generator and Transmission Owners, including planned additions.  Some equivalent representation of transmission facilities rated lower than 115 kV may be used in the study models. FTCDG members collaborate to provide periodic updates to the model to reflect system changes, including the addition and retirement of facilities.

    - Long-term firm and network interchange schedules are included in the calculation through a compiled FRCC list of transactions.  The Source/Sink information provided for these transactions maps to the model using the following priorities as available:

      - Discretely Modeled Point

      - Equivalence/ Aggregate Representation

      - Adjacent Balancing Authority

    - The model topology is adjusted to reflect scheduled FRCC generation and transmission outages that will be active for the period.  Future facilities that are included within the model are taken out of service for the time periods prior to which they are scheduled to be commissioned. Specific outages within the SERC region that have been identified as impacting the TTC are also reflected in the model. The following criteria describe the consideration of outages for the different time periods of calculation. As a member of the FTDCG FPL uses contingencies identified by the group as being relevant. If an outage cannot be mapped to the model it is assumed as not having a significant impact. If studies indicate that a specific outage does create restrictions not seen by the program, depending on the length of the outage, a change to the model would be considered through collaboration with the other members of the FTCDG or other affected Transmission Providers.

      - Outages scheduled for a part of a day impact hourly calculations only for the hours during which they are scheduled.  Daily ATC calculations for Days 1-7 are based on the most restrictive hour of the day; therefore these outages are accounted for if they are active for the hour that is determined to be most restrictive for these days.

      - Outages impact daily calculations for Days 8-395 if they are scheduled to be out during the hour starting at16:00 EPT for that particular day.

      - Outages scheduled for a part of a month impact monthly calculations by impacting the associated daily calculations.  Each day of the month has its own calculation and will account for the outage if scheduled on that day.  The monthly calculation is posted as lowest daily number for each specific path

    - The model includes all adjacent utilities and the firm interchange transactions between them; therefore the model is capturing parallel path (loop flows) adjustments and their impacts on the system.

    - Adjust load levels to the forecasted load provided per Control Area.

      - Hourly loads supplied for Hours 1 – 168

      - Daily loads supplied for Days 8 – 395 (used to provide monthly calculations)

      - The base case load flow models include all customer loads.  Interruptible demands are not utilized in determining ATC values.

    - Dispatch generation per area to meet the sum of the forecasted load and the net interchange of the area.  This dispatch is based on a unit block dispatch order (Merit Order) supplied by each FTCDG member to reflect the expected run order of generation based on economics or any other commitment or legal obligation for the unit. FTCDG members collaborate to provide periodic updates to the merit order to reflect generation changes, including the addition and retirement of generators.

TTC Calculation Databases (WEQ-23-1.1.1.2)

The Engine builds the model for calculating the FCITC using the following databases:

- Topological Transmission model of FRCC and parts of SERC

- Generator Dispatch Merit Order

- Expected Interchange (Transmission Services to be modeled)

- Monitored elements and facility ratings

- Contingencies

- Load Forecast

- Generator and Line Outages (From FTMS)

Coordination of Constraints (WEQ-23-1.1.1.3, WEQ-23-1.1.1.3.1, WEQ-23-1.1.1.3.2, WEQ-23-1.1.1.3.3)

Contingency Outages and Monitored Branches are established by the individual FRCC participants and combined into a single list. These constraints that are identified, and which have a Distribution Factor greater than or equal to 5 percent, are accounted for in FPL’s determination of TTC.

FPL includes tie lines, lines 230kV and above, transformers with a high side winding of 230kV and above, and additional voltage level branches that create constraints for specific paths. For FPL, this is a reduced set of contingencies and monitored branches from those used in operation planning studies ensuring that it is no more limiting.  Facilities for which mitigation measures have been identified may be excluded or accommodated by modeling the mitigation.  FPL’s 500kV and 230kV branches were chosen because these are the most heavily impacted by transfers.  The additional voltage level branches are those that have been identified through offline transfer studies in which all lines are analyzed as having an impact or being impacted by transfers.

- ATC Methodology (Mathematical Algorithm)

FPL uses the following specific algorithms to calculate ATC, according to the Area Interchange Methodology described in the WEQ-023-2 standard.  The algorithms are applied to each horizon as described below.  Details of each component are found in later sections.

  - Firm ATC (WEQ-023-2.1.5)

In calculating its firm ATC FPL applies the following algorithm. Firm ATC is made available as a daily, weekly, and monthly product within the operating and planning horizon. FPL does not offer hourly firm but reserves the right to do so at any time.

ATCF = TTC – ETCF – CBM – TRM + PostbacksF + CounterflowsF

Where:

ATCF is the firm Available Transfer Capability for the ATC Path for that period.

TTC is the Total Transfer Capability of the ATC Path for that period.

ETCF is the sum of existing firm Transmission commitments for the ATC Path during that period.

CBM is the Capacity Benefit Margin for the ATC Path during that period.

TRM is the Transmission Reliability Margin for the ATC Path during that period.

PostbacksF are changes to firm ATC due to a change in the use of Transmission Service for that period, as defined in Business Practices.

CounterflowsF are adjustments to firm ATC as determined by the Transmission Service Provider and specified in the ATCID. For FPL the CounterflowF term is zero for all paths for all horizons.

  - Non-Firm ATC (WEQ-023-2.1.6)

In calculating its firm ATC FPL applies the following algorithm as specified in WEQ-023-2.1.5. Non-firm is made available as an hourly, daily, weekly, and monthly product within the scheduling, operating, and planning horizon.

ATCNF = TTC – ETCF - ETCNF – CBMS – TRMU + PostbacksNF + CounterflowsNF

Where:

ATCNF is the non-firm Available Transfer Capability for the ATC Path for that period.

TTC is the Total Transfer Capability of the ATC Path for that period.

ETCF is the sum of existing firm Transmission commitments for the ATC Path during that period.

ETCNF is the sum of existing non-firm Transmission commitments for the ATC Path during that period.

CBMS is the Capacity Benefit Margin for the ATC Path that has been scheduled without a separate reservation during that period.

TRMU is the Transmission Reliability Margin for the ATC Path that has not been released for sale (unreleased) as non-firm capacity by the Transmission Service Provider during that period.

PostbacksNF are changes to non-firm ATC due to a change in the use of Transmission Service for that period, as defined in Business Practices.

CounterflowsNF are adjustments to non-firm ATC as determined by the Transmission Service Provider and specified in the ATCID.

- ETC (WEQ-023-2.1.3, WEQ-023-2.1.4)

Definition of ETC: Committed uses of a Transmission Service Provider’s Transmission system considered when determining ATC or AFC. <From NERC Glossary of terms>

  - Firm ETC

ETCF = NITSF + GFF + PTPF + RORF + OSF

Where:

NITSF is the firm capacity set aside for Network Integration Transmission Service (including the capacity used to serve bundled load within FPL’s area with external sources) on ATC Paths that serve as interfaces with other Balancing Authorities.

GFF is the firm capacity set aside for Grandfathered Firm Transmission Service and contracts for energy and/or Transmission Service, where executed prior to the effective date of FPL’s Open Access Transmission Tariff or safe harbor tariff on ATC Paths that serve as interfaces with other Balancing Authorities.

PTPF is the firm capacity reserved for confirmed Point-to-Point Transmission Service.

RORF is the capacity reserved for roll-over rights for Firm Transmission Service contracts granting Transmission Customers the right of first refusal to take or continue to take Transmission Service when the Transmission Customer’s Transmission Service contract expires or is eligible for renewal.

OSF is the firm capacity reserved for any other service(s), contract(s), or agreement(s) not specified above using Firm Transmission Service, including any other firm adjustments to reflect impacts from other ATC Paths.

  - Non-Firm ETC

ETCNF = NITSNF + GFNF + PTPNF + OSNF

Where:

NITSNF is the non-firm capacity set aside for Network Integration Transmission Service (i.e. secondary service, including the capacity used to serve bundled load within FPL’s area with external sources) on ATC Paths that serve as interfaces with other Balancing Authorities.

GFNF is the non-firm capacity set aside for Grandfathered Non-Firm Transmission Service and contracts for energy and/or Transmission Service, where executed prior to the effective date of FPL’s Open Access Transmission Tariff or safe harbor tariff on ATC Paths that serve as interfaces with other Balancing Authorities.

PTPNF is the non-firm capacity reserved for confirmed Point-to-Point Transmission Service.

OSNF is the non-firm capacity reserved for any other service(s), contract(s), or agreement(s) not specified above using Non-Firm Transmission Service, including any other non-firm adjustments to reflect impacts from other ATC Paths.

- Network Integration Transmission Service

FPL native and network customer loads are incorporated within the Transmission Model used to develop the FCITC; therefore, the transmission capacity set aside to serve this load is inherently present in the determination of FCITC but is not explicitly counted as ETC.

Generation resources for FPL and other network customers which are located external to FPL’s control area are included as either NITSF or NITSNF, and are explicitly counted as ETC.

Non-OATT customers only have capacity set aside through ETC when there is a place holder network service reservation or transmission service reservation on the FPL OASIS system.

  - Point to Point Transmission Service

Point-to-Point Transmission service requests are accounted for in ETC through the use of reservations in OASIS.  Long term firm point-to-point requests (i.e. greater than a year) are included as interchange (impact of firm transmission service) in which case they are added to the FCITC to arrive at TTC and then subtracted by the appropriate ETC reservation.

  - Grandfathered Transmission Service

FPL grandfathered customer loads are incorporated within the Transmission Model used to develop the FCITC.  The transmission capacity set aside to serve this load is inherently present in the determination of FCITC but is not explicitly counted as ETC.

Other Grandfathered Transmission Service is counted as ETC through the use of Set Aside reservations.

- Rollover Rights

Generally a decision regarding the “roll-over” of a firm transmission service is settled prior to the ATC Planning Interval. This is now always the case given new FERC requirements that rollover rights only extend to transactions five year or longer and that a year’s notice must be given. For any periods when the rollover status may be indeterminate FPL will include the transaction as if it was continuing as this is the most conservative assumption.

- Other Transmission Services

FPL uses an OS component referred to as Committed Use (CU) that is used to account for the impacts of seams issues in the treatment of transactions between two BA. Specifically FPL uses CU to account for transactions included within the ATC engine but for which FPL has no corresponding reservation on its system but needs to subtract the transaction from TTC to correctly calculate the path ATC.  A companion posted document “Paths with CU Applied” contains the paths where FPL applies a CU component. This list is updated quarterly or upon request

- TRM

  - Definition of TRM

The amount of transmission transfer capability necessary to provide reasonable assurance that the interconnected transmission network will be secure. TRM accounts for the inherent uncertainty in system conditions and the need for operating flexibility to ensure reliable system operation as system conditions change. <From NERC Glossary of terms>

  - TRM Usage

The specifics of the FPL TRM methodology and usage can be found in FPL’s Transmission Reliability Margin Implementation Document (TRMID. The TRM is applied to all horizons and is released as non-firm.

- CBM

  - Definition of CBM

The amount of firm transmission transfer capability preserved by the transmission provider for Load-Serving Entities (LSEs), whose loads are located on that Transmission Service Provider’s system, to enable access by the LSEs to generation from interconnected systems to meet generation reliability requirements. Preservation of CBM for an LSE allows that entity to reduce its installed generating capacity below that which may otherwise have been necessary without interconnections to meet its generation reliability requirements. The transmission transfer capability preserved as CBM is intended to be used by the LSE only in times of emergency generation deficiencies: The amount of transmission transfer capability necessary to provide reasonable assurance that the interconnected transmission network will be secure. CBM accounts for the inherent uncertainty in system conditions and the need for operating flexibility to ensure reliable system operation as system conditions change.  <From NERC Glossary of terms>

  - CBM Application

Neither FPL nor any of its network customers currently reserve CBM; therefore the CBM component for Firm and Non-Firm ATC is zero.

- Counter flows

  - Definition of Counter flows

Counterflows are adjustments to ATC to reflect the impact of transactions on the inverse path.

  - Counter flows Application

FPL does not include the effect of counter flows from non-firm ATC reservations.  The inclusion of non-firm TSR as counterflow that are reserved but not scheduled artificially creates ATC that, if sold, could potential create SOL violations. Firm transactions both short and long term are included as counterflows if they are included in the in the ATC interchange tables which are used by the ATC engine model. In determining its ATC for paths with SOCO as the POD FPL does not apply counterflows to its allocated export share.

- ATC Path Allocation

FPL has a contractual allocated share of the total Southern Company to Florida TTC.  The FRCC Region, including the FPL transmission system, is connected to the Eastern Interconnection solely through the Southern/Florida Transmission (SO/FL) Interface.  All flows into or out of the FRCC Region flow on this interface; therefore, the modeling of scheduled interchange within the ATC models accounts for the total power flow on this transmission interface.  The FCITC and TTC values for the entire SO/FL Interface are determined using the methodology given in the link below.  The TTC values for FPL’s portion of the SO/FL Interface are determined by applying the contractual allocation percentage to the calculated TTC for the entire interface.  The full allocated amount is applied to all of FPL’s Southern paths and is granted on a first-come first-serve basis until the entire allocation is used.  FPL’s share of this TTC is a fixed percentage derived from its ownership share of the interface facilities.

TTC Methodology for the Southern Interface

- Communication/Coordination

  - Clarification of Methodology (WEQ-23-1.7, WEQ-23-1.7.1)

FPL will provide a written response within 45 calendar days of receiving a written request for clarification of its TTC methodology, ATCID, CBMID, or TRMID, as long as the request is not contrary to its confidentiality, regulatory, or security requirements. If the request does create any concern of violating these requirements, then a written response will be provided by FPL that explains what clarifications were not able to be provided, and options for resolving those concerns.

  - Data Exchange

FPL coordinates with and exchanges data with other Florida’s BAs, TOPs, TSP, and PA as well as the Southern PA and TOP. Base topology and facility ratings are exchanged through the Florida Transmission Working Group (TWG) including the model for the Southern Companies and system adjacent to Southern. As a working member of the Florida Transmission Capability Determination Group FPL shares its generation merit order, firm long term interchange information and unit and line outage information through the Florida Transaction Management System (FTMS). A listing of the specific entities with which FPL shares data is contained as Attachment 1.

  - Notification for ATCID updates

Before implementing a new or revised ATCID FPL will notify the FRCC Reliability Coordinator, Southern Reliability Coordinator, and all of the Planning Coordinators, Transmission Operators, and Transmission Service Providers associated with and adjacent to FPL.  This includes all those within the FRCC as well as those immediately adjacent to FPL within the SERC.  FPL functions as its own Planning Coordinator and Transmission Operator and will also perform internal notifications through email of implementation and revision of its ATCID.  This ATCID will be posted on FPL’s OASIS website and also to the FRCC site “FRCC Operating Entities Posting Area- BAs/TOPs” for access by all of the above entities.

https://www.frcc.com/BATOPPosting/default.aspx

  - Data Requests (WEQ-23-1.8, WEQ-23-1.8.1, WEQ-23-1.8.2, WEQ-23-1.8.3)

FPL will make available any of the following data, in the format maintained by FPL, within 45 calendar days of receiving a request for said data from any Transmission Service Provider, Planning Coordinator, Reliability Coordinator, or Transmission Operator for use in the requestor’s ATC or AFC calculations.  The data, for up to 13 months into the future, will be made available on the schedule specified by the requestor up to once per hour. If the request raises any concerns of violating FPL’s confidentiality, regulatory, or security requirements, then a written response will be provided by FPL within 45 calendar days that explains what data cannot be provided, and any options for resolving those concerns.

    - Expected generation and Transmission outages, additions, and retirements.

    - Load forecasts.

    - Unit commitments and order of dispatch, to include all designated network resources and other resources that are committed or have the legal obligation to run, as they are expected to run, in the following format: Block Dispatch

    - Aggregated firm capacity set-aside for Network Integration Transmission Service and aggregated non-firm capacity set aside for Network Integration Transmission Service (i.e. Secondary Service).

    - Firm and non-firm Transmission reservations.

    - Aggregated capacity set-aside for Grandfathered obligations.

    - Firm roll-over rights.

    - Any firm and non-firm adjustments applied by FPL to reflect parallel path impacts.

    - Power flow models and underlying assumptions.

    - Contingencies, provided in the following format: A list of Elements

    - Facility Ratings.

    - Any other services that impact Existing Transmission Commitments (ETCs).

    - Values of Capacity Benefit Margin (CBM) and Transmission Reliability Margin (TRM) for all ATC Paths.

    - Values of TTC and ATC for all ATC Paths.

    - Source and sink identification and mapping to the model.

Appendix A

WEQ-23-1 and WEQ-23-2 Index References

WEQ-23-1.1.1	2

WEQ-23-1.1.1	2

WEQ-23-1.1.1.1	2

WEQ-23-1.1.1.2	6

WEQ-23-1.1.1.3	8

WEQ-23-1.1.1.3.1	8

WEQ-23-1.1.1.3.2	8

WEQ-23-1.2	2

WEQ-23-1.3	2

WEQ-23-1.3.1	2

WEQ-23-1.3.2	6

WEQ-23-1.3.3	8

WEQ-23-1.4	6

WEQ-23-1.4.1	6

WEQ-23-1.5	9

WEQ-23-1.6	9

WEQ-23-1.7	15

WEQ-23-1.7.1	15

WEQ-23-1.8	15, 16

WEQ-23-1.8.1	15, 16

WEQ-23-1.8.2	15, 16

WEQ-23-1.8.3	15, 16

WEQ-023-2.1	2, 3

WEQ-023-2.1.1	6

WEQ-023-2.1.2	2, 3

WEQ-023-2.1.3	10

WEQ-023-2.1.4	10, 11

WEQ-023-2.1.5	9

WEQ-023-2.1.6	9

Attachment 1 
Entities with whom FPL shares ATC modeling data
effective as of 3/28/2013

| Shared Data Entities List |  |
| --- | --- |
| (revised 3/28/2013) |  |
| Below is the list of entities with which FPL both provides and receives information for calculation of ATC's. Information shared includes such items as: generation and transmission outages, firm long term interchange schedules, transmission projects, network topology, facilities ratings, and generation merit orders. This list will be updated on an annual basis based on the NAESB functional entities registration, and a concatenation of the FRCC Operating Reliability Subcommittee membership, the FRCC PC Regional Representatives membership, and the FRCC Operating Committee Regional Entities membership |
| City of Tallahassee |  |
| Gainesville Regional Utility |  |
| Orlando Utility Commission Powersouth Electric Cooperative |  |
| Southern Company Services |  |
| Seminole Electric Cooperative |  |
| Ready Creek Improvement District (through Progress Energy Florida) |  |
| Progress Energy Florida (Duke) |  |
| Florida Municipal Power Agency |  |
| Jacksonville Electric Authority |  |
| Lee County Electric Cooperative |  |
| Utility Commission for City of New Smyrna Beach |  |
| TECO Energy |  |
| City of Homestead |  |
| Florida Keys Electric Cooperative |  |

# Text boxes

FPL PROCESS FLOW DIAGRAM

START

FPL Data Provided to FRCC for retrieval by OATI

-

System Topology       -Generator Dispatch Merit Order

-Expected Interchange (Transmission Commitments)

-Facility Ratings          -Monitored Elements

-Contingencies            -Load Forecast*

-Generator Outages*    -Line Outages*

*Provided through FTMS

Applies to Firm and Non-Firm:

-Monthly

-Weekly

-Daily

-Hourly (Non-Firm)

OATI TTC Calculator Determines:

-FCITC

-"Impact of Firm Transmission"

-TTC (Segment) = FCITC + Impact of

Firm Trans

-TRM based on facility ratings

Data Passed to OATI

Webtrans Application

Additional Data in Webtrans:

-FPL TRM     -Existing Reservations

-Existing Schedules

(Tags)

-Contractual limits on TTC / Sum of Facility

Ratings of Ties

Provider's Webtrans Calculates

-TTC (Path)   - ETC

-TRM             -ATC

Data Passed from Webtrans

To FPL OASIS

On Going Process #1:

Changes in

-Schedules (Tags)     -Reservations

Continuously update ETC & ATC

On Going Process #2:

Revise TTC & TRM

Based on predetermined frequency or on

Demand due to major events.

Data Posted on

Oasis

Data Input

Calculation

Data Transfer

Ongoing Process

KEY

Termination