Interconnection Request for a Generating Facility

    - The undersigned Interconnection Customer submits this request to interconnect its Generating Facility with Transmission Provider's Transmission System pursuant to a Tariff.

    - This Interconnection Request is for (check one):

A proposed new Generating Facility.

An increase in the generating capacity or a Material Modification of an existing generating facility.

    - The type of interconnection service requested (check one):

Energy Resource Interconnection Service

Network Resource Interconnection Service

    - If you are an Interconnection Customer requesting Network Resource Interconnection Service, do you also seek to have your Generating Facility studied for Energy Resource Interconnection Service?

Yes	 No

    - The Interconnection Customer should provide the following information:

      - Address or location or the proposed new Generating Facility site including a United States Geological Survey map of the proposed plant site  (to the extent known) or, in the case of an existing Generating Facility, the name and specific location of the existing Generating Facility.

      - Maximum summer at 95° Fahrenheit  and winter at 50-70°   Fahrenheit  gross and net megawatt electrical output of the proposed new Generating Facility or the amount of megawatt increase in the generating capacity of an existing Generating Facility.

      - General description of the equipment configuration.

      - Estimated In-Service Date, Initial Synchronization Date and Commercial Operation Date (Day, Month, and Year).

      - Name, address, telephone number, and e-mail address of Interconnection Customer's contact person.

      - Approximate location of the proposed Point of Interconnection (optional).

      - Interconnection Customer Data (set forth in Attachment A); and Running Station Service Load       MW:       Mvar, and connection location (i.e. attach single-line diagram).

        - Applicable deposit amount as specified in the GIP.

          - Evidence of Site Control as specified in the GIP (check one):

Is attached to this Interconnection Request

Will be provided at a later date in accordance with this GIP

- This Interconnection Request shall be submitted to the representative indicated below:

Inter-connect Transmission Contract Administrator

Imperial Irrigation District

P.O. Box 937

Imperial, CA 92251

- Representative of Interconnection Customer to contact:

[To be completed by Transmission Provider]

This Interconnection Request is submitted by:

| Name of Interconnection Customer: |  |
| --- | --- |
| Signature: |  |
| Print Name: |  |
| Title: |  |
| Date: |  |

ATTACHMENT A

A typical System Impact Study includes Power Flow, Transient Stability, Post-Transient Stability, and Short Circuit Analysis. If the size and/or technology type of the project is different than typical size and/or technology type, IID System Planning group can recommend expanding or reducing the scope of the study.

IID normally uses the last version of G.E. PSLF software approved by WECC to perform Power Flow, Transient Stability and Post-Transient Stability analyses. For the Short Circuit analysis uses the last version of ASPEN software.

A) Power Flow (Project’s data)

Please provide the following information. (Additional sheets or documents can be added)

1) Project Name

What is the name of the project?

(Please provide 3 different alternatives)

Alternative 1:

Alternative 2:

Alternative 3:

Note: If the name of your project represents a potential confusion issue for the IID’s Planning Group personnel since your project has the same name or similar name as the assigned to another project involved in the same study, IID will suggest a new project’s name for your project to prevent the subject potential confusion. This does not intend to create any legal or commercial issues on the development of your project.

2) Project One-Line Diagram

Please provide a simplified one-line diagram of the facility (ies) to be studied.

3) Provide a map with geographical location of the new generation project. The map should contain a scale to be able to determine the distance between your generation project and other important elements in the area as streets, roads, IID transmission lines, etc..

4) Will this project be completed in phases?    Yes            No

5) Provide the in-service date for the total completion of the project or per phase.

6) Provide the commercial operation date for the total completion of the project or per phase.

7) The System Planning group usually studies the Heavy Summer (PEAK) and Light Winter (OFF-PEAK) conditions to determine the most critical operating conditions for the IID System. Do you consider the need for studying another season or year for your project?

No

Yes      Which Season or Year:                           Reason:

Note: Notice that any additional season or year to be studied for a new generation project would potentially represent additional costs for the study.

8) Propose Point of Interconnection (POI) to the IID System. The POI is the electrical point where you propose to connect your project to the existing IID grid. Provide the Station’s Name or Line’s Name and kV.

Note: According to the OATT regulations for Cluster System Impact Studies, IID has the right to propose change of the POI for a new generation project requesting interconnection to the transmission grid to improve costs of common network upgrades.

9)  Propose Point of Delivery (POD). The POD represents the electrical point on the interconnected system where the energy produced by your project will be delivered. Provide the Receiving Balancing Authority’s Name, Substation’s Name and kV Bus to describe the POD

10) Is your project a peaking or base load generation?

11) Provide the company owner’s name of this generator:

12) Should internal IID generation be reduced to offset project in the post project condition?

Yes           No

13) Should this project energy be exported to other Control Area (other Balancing Authority)?

Yes        No

13a) If yes, please provide the Control Area’s or Balancing Authority’s Name

15) From the total MW output of your project, how many MW will be for export?

16) Will the power to serve load for the generator be provided by IID?

Yes        No

17) EQUIPMENT DATA. (Nameplate data is acceptable also)

Generator A:

| ANNUAL |
| --- |
| Type of Technology (PV, Geothermal, Gas Turbine, Solar-Thermal, etc..): |
|  | H. SUMMER | L.WINTER |
| Generator Data | Peak Min. | Peak Max. | Off- Peak Min. | Off- Peak Max. |
| MW (at POI) |  |  |  |  |
| MVAR (at POI) |  |  |  |  |
| Power Factor |  |

Generator B:

| ANNUAL |
| --- |
| Type of Technology (PV, Geothermal, Gas Turbine, Solar-Thermal, etc..): |
|  | H. SUMMER | L.WINTER |
| Generator Data | Peak Min. | Peak Max. | Off- Peak Min. | Off- Peak Max. |
| MW (at POI) |  |  |  |  |
| MVAR (at POI) |  |  |  |  |
| Power Factor |  |

Load 1:

| ANNUAL |
| --- |
|  | H. SUMMER | L. WINTER |
| Generator Data | Peak Min. | Peak Max. | Off- Peak Min. | Off- Peak Max. |
| MW |  |  |  |  |
| MVAR |  |  |  |  |
| Power Factor |  |

Load 2:

| ANNUAL |
| --- |
|  | H. SUMMER | L. WINTER |
| Generator Data | Peak Min. | Peak Max. | Off- Peak Min. | Off- Peak Max. |
| MW |  |  |  |  |
| MVAR |  |  |  |  |
| Power Factor |  |

Generator Step-up Transformer 1:

| Low Side Voltage (kV) |  | High Side Voltage (kV) |  |
| --- | --- | --- | --- |
| MVA Base (MVA) |  | Reactance (p.u.) or % |  |
| Continuous Normal Rating (MVA) |  | Emergency Rating (MVA) |  |
| Number of Transformers |  | Winding Config. (Delta, Y, etc.) |  |

Generator Step-up Transformer 2:

| Low Side Voltage (kV) |  | High Side Voltage (kV) |  |
| --- | --- | --- | --- |
| MVA Base (MVA) |  | Reactance (p.u.) or % |  |
| Continuous Normal Rating (MVA) |  | Emergency Rating (MVA) |  |
| Number of Transformers |  | Winding Config. (Delta, Y, etc.) |  |

System Step-up Transformer:

| Low Side Voltage (kV) |  | High Side Voltage (kV) |  |
| --- | --- | --- | --- |
| MVA Base (MVA) |  | Reactance (p.u.) or % |  |
| Continuous Normal Rating (MVA) |  | Emergency Rating (MVA) |  |
| Number of Transformers |  | Winding Config. (Delta, Y, etc.) |  |

18) INTERCONNECTING LINE.

The project owner has the option of providing the following line characteristics. If it is not provided in this template, IID will apply the current engineering design standards to determine the characteristics of the interconnection line. It is also optional for the customer to provide the data in the gray cells area.

ACSR

| Conductor Type |  | Length | Feet | Miles |
| --- | --- | --- | --- | --- |
| Single Circuit | Yes | No | Double Circuit | Yes | No |
| Single Conductor | Yes | No | Bundled Conductor | Yes | No |
| Voltage (kV) |  |
| Optional: |  |  |  |
| Resistance (R), p.u. |  | Reactance (X), p.u. |  |
| MVA Rating |  | Susceptance (B), p.u. |  |

Provide the contact person name, telephone number and email address for questions on the Power Flow analysis data provided.

ATTACHMENT B Transient Stability Study Data Synchronous Generators For your reference, IID provides the following Machine, Governor, Excitation System and Power System Stabilizer Models List for synchronous generators. Each generator requesting interconnection to the IID System should select the name of each of the appropriate dynamic model that would represent the elements of the generation equipment for your project. If your generator is not a synchronous generator please provide the parameters associated with your generator in PSLF format. Once you select the model’s name for each of the elements of the generation equipment for your project, you are to provide the parameters associated with each model in a General Electric (PSLF) format. The subject data can be obtained from your generator manufacturer or other reliable source. If you do not have the parameters associated with your generator, default values can be used upon confirmation. IID will not take a guess or determine the dynamic models for your project: Check the box below that best applies: I will be providing parameters in PSLF Format Use default parameters for all models MACHINE MODELS Model Name Description Gencc Generator represented by uniform inductance ratios rotor modeling to match WSCC type F model; shaft speed effects are neglected. Intended to model cross-compound machines represented as one generator in the load flow. Gencls Synchronous machine represented by "classical" modeling or Thevenin Voltage Source to Play Back known voltage/frequency signal Genrou Solid rotor generator represented by equal mutual inductance rotor modeling Gensal Salient pole generator represented by equal mutual inductance rotor modeling Gensdo Generator with stator d.c. current represented Gentpf Generator represented by uniform inductance ratios rotor modeling to match WSCC type F model; shaft speed effects are neglected Genwri Wound-rotor induction generator model (with variable external rotor resistance) Gewtg Generator/converter model for GE wind turbines Motor1 "Two-cage" or "one-cage" induction machine Shaft5 Call GE Genind "Two-cage" or "one-cage" induction generator Gentpj Generator represented by uniform inductance ratios rotor modeling to match WSCC type F model with modified saturation model; shaft speed effects are neglected

EXCITATION MODELS Model Name Description Esac1a IEEE (1992/2005) type AC1A excitation system Esac2a IEEE (1992/2005) type AC2A excitation system Esac3a IEEE (1992/2005) type AC3A excitation system Esac4a IEEE (1992/2005) type AC4A excitation system Esac5a IEEE (1992/2005) type AC5A excitation system model with optional speed multiplier Esac6a IEEE (1992/2005) type AC6A excitation system with optional speed multiplier Esdc1a IEEE (1992/2005) DC1A excitation system model with optional speed multiplier Esdc2a IEEE (1992/2005) DC2A excitation system model with optional speed multiplier Esdc3a IEEE DC3A (1992/2005) excitation system model with added speed multiplier Esdc4b IEEE (1992/2005) DC4B excitation system model with optional speed multiplier Esst1a IEEE (1992/2005) type ST1A excitation system. Esst2a IEEE (1992/2005) type ST2A excitation system with added lead-lag block Esst3a IEEE (1992/2005) type ST3A excitation system. Esst4b IEEE (2005) type ST4B excitation system Esst5b IEEE (2005) type ST5B excitation system Esst6b IEEE (2005) type ST6B excitation system Esst7b IEEE (2005) type ST7B excitation system Esac7b IEEE (2005) type AC7B excitation system Esac8b IEEE (2005) type AC8B with added speed multiplier. Exac1 IEEE type AC1 excitation system Exac1a Modified IEEE type AC1 excitation system Exac2 IEEE type AC2 excitation system Exac3 IEEE type AC3 excitation system Exac3a IEEE type AC3 excitation system Exac4 IEEE type AC4 excitation system Exac6a IEEE type AC6A excitation system Exac8b Brushless exciter with PID voltage regulator Exbbc Transformer fed static excitation system Exdc1 IEEE type 1 excitation system model Represents systems with d.c. exciters and continuously acting voltage regulators, such as amplidyne-based excitation systems Exdc2 IEEE type 2 excitation system model Represents systems with d.c. exciters and continuously acting voltage regulators, such as amplidyne-based excitation systems Exdc2a IEEE type 2 excitation system model Represents systems with d.c. exciters and continuously acting voltage regulators, such as amplidyne-based excitation systems Exdc4 IEEE (1968) type 4, DC3 (1980), and DC3A (1992, 2005) excitation system model with added speed multiplier Exeli Static PI transformer fed excitation system Exeli2 VATECH (ELIN) excitation system model with PSS Exivo IVO excitation system Expic1 Proportional/Integral Regulator Excitation System Model Exst1 IEEE type ST1 excitation system Exst2 IEEE type ST2 excitation system Exst2a IEEE type ST2 excitation system Exst3 IEEE type ST3 excitation system Exst3a IEEE type ST3 excitation system Exst4b IEEE type ST4b excitation system Exwtg1 Excitation system model for wound-rotor induction wind-turbine generator Extwge Excitation (converter) control model for GE wind-turbine generators Ieeetl "Old" IEEE type 1 excitation system model. Represents systems with d.c. exciters and continuously acting voltage regulators, such as amplidyne-based excitation systems Mexs Manual excitation control with field circuit resistance Pfqrg Power factor / Reactive power regulator Rexs General Purpose Rotating Excitation System Model Scrx Simple excitation system model representing generic characteristics of many excitation systems; intended for use where negative field current may be a problem Sexs Standard excitation system model representing generic characteristics of many excitation systems; intended for use where details of the actual excitation system are unknown and/or unspecified

PRIME MOVER MODELS Model Name Description Ccbtl Steam plant boiler / turbine and governor Ccst3 Combined Cycle Plant Steam Turbine Model Crcmgv Cross compound turbine governor model G2wscc Double derivative hydro governor and turbine. (Represents WECC G2 governor plus turbine model.) Gast Single shaft gas turbine Gegt1 General Electric Frame 6, 7, 9 Gas Turbine Model Ggov1 General governor model Ggov2 General governor model with frequency-dependent fuel flow limit Ggov3 General governor model with GE gas turbine control features Hygovr Fourth order lead-lag governor and hydro turbine. Hyst1 Hydro turbine with Woodward Electro-hydraulic PID Governor, Penstock, Surge Tank, and Inlet Tunnel Gpwscc PID governor and turbine. (Represents WECC GP governor plus turbine model.) Hyg3 PID governor, double derivative governor and turbine. (Represents WECC GP governor, WECC G2 governor plus turbine model.) Hygov Hydro turbine and governor. Represents plants with straight forward penstock configurations and electro-hydraulic governors that mimic the permanent/temporary droop characteristics of traditional dashpot-type hydraulic governors. Hygov4 Hydro turbine and governor. Represents plants with straight forward penstock configurations and hydraulic governors of traditional 'dashpot' type. Ieeeg1 IEEE steam turbine/governor model (with deadband and nonlinear valve gain added) Ieeeg3 IEEE hydro turbine/governor model. Represents plants with straightforward penstock configurations and hydraulic-dashpot governors. (Optional deadband and nonlinear gain added.) 1cfb1 Turbine Load Controller model 1m6000 LM6000 Aero-derivative gas turbine governor Pidgov Hydro turbine and governor. Represents plants with straight forward penstock configurations and "three term" electro-hydraulic governors (i.e. Woodard electronic) Stag1 Single Shaft Combined-Cycle Plant Model Tgov1 Basic steam turbine and governor Tgov3 Turbine/governor model with fast valving W2301 Woodward 2301 governor and basic turbine model Wndtge Wind turbine and turbine control model for GE wind turbines Wndtrb Wind turbine control model

STABILIZER MODELS Model Name Description ieeest Power system stabilizer pss2a Dual input Power System Stabilizer (IEEE type PSS 2A) pss2b Dual input Power System Stabilizer (IEEE type PSS 2A) withVoltage Boost signal Transient Stabilizer and Vcutoff pss1a Single input power system stabilizer pss3b IEEE (2005) type PSS3B dual-input power system stabilizer psssb Dual input Power system stabilizer (IEEE type PSS2A) +Voltage Boost Signal Transient Stabilizer and Vcutoff psssh Model for Siemens “H infinity” power system stabilizer with generator electrical power input wsccst WSCC Power System Stabilizer

Stability Model for Photovoltaic Generators

If your project technology will be Photovoltaic generation, you need to provide IID an electronic file with the dynamic model representing the inverter to be used in your project. The model should use a G.E. PSLF format. The subject data can be obtained from your generator manufacturer or other reliable source. IID will not determine the dynamic models for your project.

Provide the contact person name, telephone number and email address for questions on the Transient Stability data provided.

ATTACHMENT C

Short Circuit Study Data

SYNCHRONOUS GENERATOR DATA

FOR SHORT CIRCUIT STUDIES

Total Number of Generators:

| Generator Information |
| --- |
|  | Machine Base used for per unit impedances |
|  | Voltage rating of machine |
|  | Winding Configuration (i.e. Delta, Grounded Wye, etc) |
|  | Neutral Impedance (If applicable) |
|  | Direct-axis Sub-transient Reactance (Xd”), per unit |
|  | Quadrature-axis Sub-transient Reactance (X”q), per unit |
|  | Direct-axis Transient Reactance (X’d), per unit |
|  | Quadrature-axis Transient Reactance (X’q), per unit |
|  | Synchronous Reactance (Xs), per unit |
|  | Negative Sequence Reactance (X2), per unit |
|  | Zero Sequence Reactance (X0), per unit |

Total Number of Transformers:

| Generator Step-up Transformer Information |
| --- |
|  | Voltage Ratings of Primary & Secondary Windings |
|  | Winding Configurations (i.e. Delta, Grounded Wye, etc) |
|  | MVA Rating |
|  | Positive Sequence Impedance (R+jX) (Identify if in pu or (. If in pu, list base) |
|  | Zero Sequence Impedance (R+jX) |

Total Number of Transformers:

| Generator Step-up Transformer Information |
| --- |
|  | Voltage Ratings of Primary & Secondary Windings |
|  | Winding Configurations (i.e. Delta, Grounded Wye, etc) |
|  | MVA Rating |
|  | Positive Sequence Impedance (R+jX) (Identify if in pu or (. If in pu, list base) |
|  | Zero Sequence Impedance (R+jX) |

Total Number of Transformers:

| System Step-up Transformer Information |
| --- |
|  | Voltage Ratings of Primary & Secondary Windings |
|  | Winding Configurations (i.e. Delta, Grounded Wye, etc) |
|  | MVA Rating |
|  | Positive Sequence Impedance (R+jX) (Identify if in pu or(. If in pu, list base) |
|  | Zero Sequence Impedance (R+jX) |

Total Number of Transformers:

| System Step-up Transformer Information |
| --- |
|  | Voltage Ratings of Primary & Secondary Windings |
|  | Winding Configurations (i.e. Delta, Grounded Wye, etc) |
|  | MVA Rating |
|  | Positive Sequence Impedance (R+jX) (Identify if in pu or(. If in pu, list base) |
|  | Zero Sequence Impedance (R+jX) |

Note 1: All values provided above must clearly state per unit value. If the values are provided as per unit values, the base must be provided also.

Note 2: If you have more than one generator and/or unit transformer please attach additional copies of this template.

PHOTOVOLTAIC INVERTER DATA

FOR SHORT CIRCUIT STUDIES

Total Number of Inverters:

| Inverter Information |
| --- |
|  | Maximum Continuous Output Power (kW) |
|  | Nominal Output Voltage (volts) |
|  | Number of PV Units per inverter |
|  | Nominal Output Current (Amps) |
|  | Maximum Output Fault Current (Amps) |

Total Number of Transformers:

| Generator Step-up Transformer Information |
| --- |
|  | Voltage Ratings of Primary & Secondary Windings |
|  | Winding Configurations (i.e. Delta, Grounded Wye, etc) |
|  | MVA Rating |
|  | Positive Sequence Impedance (R+jX) (Identify if in pu or (. If in pu, list base) |
|  | Zero Sequence Impedance (R+jX) |

Total Number of Transformers:

| Generator Step-up Transformer Information |
| --- |
|  | Voltage Ratings of Primary & Secondary Windings |
|  | Winding Configurations (i.e. Delta, Grounded Wye, etc) |
|  | MVA Rating |
|  | Positive Sequence Impedance (R+jX) (Identify if in pu or (. If in pu, list base) |
|  | Zero Sequence Impedance (R+jX) |

Total Number of Transformers:

| System Step-up Transformer Information |
| --- |
|  | Voltage Ratings of Primary & Secondary Windings |
|  | Winding Configurations (i.e. Delta, Grounded Wye, etc) |
|  | MVA Rating |
|  | Positive Sequence Impedance (R+jX) (Identify if in pu or(. If in pu, list base) |
|  | Zero Sequence Impedance (R+jX) |

Total Number of Transformers:

| System Step-up Transformer Information |
| --- |
|  | Voltage Ratings of Primary & Secondary Windings |
|  | Winding Configurations (i.e. Delta, Grounded Wye, etc) |
|  | MVA Rating |
|  | Positive Sequence Impedance (R+jX) (Identify if in pu or(. If in pu, list base) |
|  | Zero Sequence Impedance (R+jX) |

Note 1: All values provided above must clearly state per unit value. If the values are provided as per unit values, the base must be provided also.

Note 2: If you have more than one type of inverter and/or unit transformer, please attach additional copies of this template for each different type of equipment.

Provide the contact person name, telephone number and email address for questions on the Short Circuit data provided.

A hard copy or scanned document of the completed template should be provided back to IID including data, and signed by the person (s) responsible for the data provided.

Responsible Person Signature:                                                                Date: