## Gen
DATA PROVIDED BY IID
Field | Value | Description | Requirements | Measure
PSLF Bus Number |  | Number of the Bus to which the generator is attached.
· See “Data Requirements (Buses)”
Unit ID |  | Two -character Generator identifier
Status |  | Generator status 1 = in-service 0 = out-of-service | G1. Out-of-service units shall have status set to zero. G2. Retired units shall be deleted rather than having status set to zero.
G2. Retired units shall be deleted rather than having status set to zero.
Area |  | Generator Area in which located | G13.Refer to “Appendix 2 – Area, Zone, and Bus Number Assignments” for designated Area.
Zone |  | Generator Zone in which located | G14.Refer to “Appendix 2 – Area, Zone, and Bus Number Assignments” for designated ranges of Zones used by Area
Planning Coordinator |  | Planning Coordinator Area in which Generator is located | G18.Refer to “Appendix 2 – Area, Zone, and Bus Number Assignments” for designated Planning Coordinator Areas.
DATA PROVIDED BY OWNER
Field | Value | Description | Requirements | Measure
Gen Bus Number
Gen Bus Name
Pgen |  | Real power output (gross MW) | G3. Pgen shall be at or within the unit Pmax and Pmin parameters for units that are in-service. | If Status = 1: Pmin ≤ Pgen ≤ Pmax
Qgen |  | Reactive power output (MVAr)
Pmax |  | Maximum real power output (MW) | G4. Pmax shall reflect the maximum real power output of the unit, also known as ‘gross’ capability. | Pmax ≤ Governor Max
G5. Pmax shall not be greater than the maximum capability of the unit represented by the governor model.
Pmin |  | Minimum real power output (MW) | G6. Pmin shall reflect the minimum real power output of the unit. | Pmin ≤ Pmax
G7. Pmin shall be less than or equal to Pmax
Qmax |  | Maximum reactive power output (MVAr) | G8. Qmax shall reflect the appropriate maximum reactive power output of the unit.
Qmin |  | Minimum reactive power output (MVAr) | G9. Qmin shall reflect the appropriate minimum reactive power output of the unit. | Qmin ≤ Qmax
G10.Qmin shall be less than or equal to Qmax
Q Alloc Factor |  | Reactive power regulating assignment factor
Q Table Flag |  | Reactive capability curve flag | G11.Q-Table data used for internal studies shall be included in WECC Base Case submittals.
Base load |  | types:
Non base load, Base load unit (cannot respond to low frequency with additional mechanical power), or Base load unit (cannot respond to low and high frequency with mechanical power)
Turbine Type |  | types:
non-reheat steam, reheat steam,steam cross-compound, steam in combined cycle (separate shaft), hydro, diesel non turbo charged, diesel turbo charged, industrial GT (single shaft), aero derivative GT, single shaft combined cycle, Synchronous condenser (no turbine), type 1 wind turbine, type 2 wind turbine, type 3 wind turbine, type 4 wind turbine, photovoltaic,DC tie (generators representing DC ties)
Reg Bus |  | Bus whose voltage is controlled by this Generator | G12. Regulation of a remote Bus that does not represent actual system operation shall be avoided.
Vsched |  | Generator scheduled voltage (pu)
Base MVA |  | Generator base (MVA) | G15.Unit Base MVA shall be equal to the MVA Base parameter of the unit’s Dynamic machine model. | Base MVA = Machine Base
Owner |  | Owner Number | G16.Owner Number shall be the Generator Owner.
|  | · Up to 8 owners allowed | G17.WECC staff shall assign Owner Number to required entities.
G tap |  | Tap ratio of generator step up transformer | G19.G tap shall be set to 1. | G tap = 1
R TR |  | Resistance of generator step up transformer | G20.R TR shall be set to 0. | R TR = 0
XTR |  | Reactance of generator step up transformer | G21.X TR shall be set to 0. | X TR = 0
R Sub transient |  | Sub transient resistance of generator
X Sub transient |  | Sub transient reactance of generator | G22.X Sub transient shall be equal to the sub transient reactance represented in the unit Dynamic machine model. | X Sub transient = Xdpp (or Ldpp)
One line drawing provided
| New facility, | expected in-service date:
Data provided by
Title
Date
Section to be completed by IID
Data reviewed by:
Title
Date
Technical Concerns: | yes | no
Requested clarification/comments or more data to owner on:
Accepted: | yes | no
| Template Revision: | Revision 0
| Revision Date: | 2015-07-01
Generator Owner
Other: