## Power Flow Results
Year of Study = 2008 | Idaho Control Area (Import) NAI | Idaho Control Area Load & Losses | Idaho Control Area Generation | 'First Contingency Incremental Transfer Capability (FCITC) | SIL = FCITC - NAI | Idaho-Northwest Total | ID-NW (LaGrande - BPA) | ID-NW (Imnaha - AVA) | ID-NW (Huricane - PACW) | ID-NW (Summer Lake - PACW) | Brownlee East | Hells Canyon Generation | Upper Snake Generation | Jim Bridger West | Jim Bridger Generation | Borah West | Midpoint West | Idaho-Sierra | Idaho-Montana | Path C (Utah-Idaho)
Path | [5 empty] | 14 W-E |  |  |  | 75 W-E | 55 W-E |  |  | 19 E-W |  | 17 E-W | E-W | 16 S-N | 18 N-S | 20 S-N
Winter |  |  |  |  | 2235
Winter Seasonal Path Ratings | [5 empty] | -1200 | -350 | -450 | -400 | -400 | 1850 |  |  | 2200 |  | 2557 | 1100 | -262 | -337 | 850
08hw2a_ipc_ca (reference base case) | -1230 | 2701 | 1471 |  |  | 250 | -69 | -212 | -22 | 549 | 1147 | 882 | 205 | 2048 | 2056 | 1279 | 52 | 142 | -184 | -105
08hw2a_ipc_ca_sil (benchmark case) | -2235 | 2714 | 479 | 1005 |  | -309 | -181 | -330 | -212 | 422 | 883 | 259 | 200 | 2128 | 2114 | 1559 | 614 | -24 | -216 | 72
Spring |  |  |  |  | 2040
Spring Seasonal Path Ratings | [5 empty] | -1150 | -350 | -400 | -400 | -400 | 1850 |  |  | 2200 |  | 2557 | 1100 | -262 | -337 | 850
08hsp2b_ipc_ca (reference base case) | -1440 | 2848 | 1408 |  |  | -298 | -127 | -285 | -102 | 204 | 1194 | 756 | 253 | 1493 | 1502 | 872 | 24 | -15 | -265 | -275
08hsp2b_ipc_ca_sil (benchmark case) | -2040 | 2855 | 815 | 600 |  | -503 | -170 | -327 | -201 | 187 | 1093 | 468 | 225 | 1620 | 1558 | 1198 | 384 | -62 | -254 | -33
Summer |  |  |  |  | 2225
Summer Seasonal Path Ratings | [5 empty] | -1090 | -350 | -340 | -400 | -400 | 1915 |  |  | 2200 |  | 2557 | 1100 | -262 | -337 | 850
08hs4a_ipc_ca (reference base case) | -1795 | 3565 | 1770 |  |  | -593 | -140 | -314 | -119 | -31 | 1570 | 1096 | 220 | 1877 | 1998 | 905 | 8 | 68 | -301 | -309
08hs4a_ipc_ca_sil (benchmark case) | -2225 | 3559 | 1334 | 430 |  | -534 | -157 | -332 | -149 | 96 | 1392 | 851 | 238 | 2039 | 2098 | 1231 | 349 | -94 | -293 | -120
Fall |  |  |  |  | 2045
Fall Seasonal Path Ratings | [5 empty] | -1090 | -350 | -340 | -400 | -400 | 1915 |  |  | 2200 |  | 2557 | 1100 | -262 | -337 | 850
08hs4a_ha_ipc_ca (reference base case) | -1240 | 2530 | 1290 |  |  | -346 | -110 | -281 | -106 | 135 | 1165 | 748 | 234 | 1839 | 2024 | 768 | -9 | 115 | -285 | -476
08hs4a_ha_ipc_ca_sil (bemchmark case) | -2045 | 2534 | 489 | 805 |  | -422 | -155 | -338 | -214 | 276 | 824 | 192 | 180 | 2000 | 2094 | 1268 | 520 | -95 | -303 | -161
SIL

## Summer
FERC 2010 Idaho Power Control Area Simultaneous Import Limit Study for Market Share Screening Analysis
VOLTAGE DEVIATIONS
|  |  | Seasonal Emergency Rating |  |  | Maximum
|  |  | *****OVERLOADS (%) ***** |  | Min | Relative
|  |  | Highest O/L |  | Absolute | Voltage
Case | Contingency | RAS | Line/Xfmr | Loading | Volt (p.u.) | Change | COMMENTS
08hs4a_ipc_ca_sil | MIDPOINT T341 700 MVA 345/230 kV Xfmr | None | MIDPOINT T342 500 MVA 345/230 kV Xfmr | 102.8% | None <- 5%
08hs4a_ipc_ca_sil | BROWNLEE-HELLS CANYON 230 kV | Trip 1 Hells Cyn Unit (115 MW) | Oxbow-Lolo 230 kV | 102.6% | None <- 5%
08hs4a_ipc_ca_sil | BROWNLEE-HELLS CANYON 230 kV | Trip 1 Hells Cyn Unit (115 MW) | Oxbow-Lolo 230 kV | 88.8% | None <- 5%
|  | Insert CRFD 2 x 10 Ohm Series Reactors |  |  |  |  | With RAS
08hs4a_ipc_ca_sil | BROWNLEE-HELLS CANYON 230 kV OXBOW-LOLO 230 kV | Trip 1 Hells Cyn Unit (115 MW) | McNary-Roundup 230 kV | 106.1% | LaGrande 69 - 0.928 | -7.8%
[5 empty] | Ukiah/Pilot Rk 69 - 0.894 | -7.7%
[5 empty] | Athena 69 - 0.882 | -7.8%
[5 empty] | Pendelton 69 - 0.900 | -7.5%
[5 empty] | Buckaroo 69 - 0.903 | -7.5%
08hs4a_ipc_ca_sil | BROWNLEE-HELLS CANYON 230 kV OXBOW-LOLO 230 kV | Trip 1 Hells Cyn Unit (115 MW) | McNary-Roundup 230 kV | 99.2% | LaGrande 69 - 0.937 | -6.9%
|  | Open Quartz 101A Breaker |  |  | Ukiah/Pilot Rk 69 - 0.904 | -6.7% | With Post-Disturbance Remediation
[5 empty] | Athena 69 - 0.892 | -6.8%
[5 empty] | Pendelton 69 - 0.910 | -6.5%
[5 empty] | Buckaroo 69 - 0.913 | -6.4%

## Winter
FERC 2010 Idaho Power Control Area Simultaneous Import Limit Study for Market Share Screening Analysis
VOLTAGE DEVIATIONS
|  |  | Seasonal Emergency Rating |  |  | Maximum
|  |  | *****OVERLOADS (%) ***** |  | Min | Relative
|  |  | Highest O/L |  | Absolute | Voltage
Case | Contingency | RAS | Line/Xfmr | Loading | Volt (p.u.) | Change | COMMENTS
08hw2a_ipc_ca_sil | MIDPOINT T341 700 MVA 345/230 kV Xfmr | None | MIDPOINT T342 500 MVA 345/230 kV Xfmr | 101.3% | None <- 5%

## Spring
FERC 2010 Idaho Power Control Area Simultaneous Import Limit Study for Market Share Screening Analysis
VOLTAGE DEVIATIONS
|  |  | Seasonal Emergency Rating |  |  | Maximum
|  |  | *****OVERLOADS (%) ***** |  | Min | Relative
|  |  | Highest O/L |  | Absolute | Voltage
Case | Contingency | RAS | Line/Xfmr | Loading | Volt (p.u.) | Change | COMMENTS
08hsp2b_ipc_ca_sil | MIDPOINT T341 700 MVA 345/230 kV Xfmr | None | MIDPOINT T342 500 MVA 345/230 kV Xfmr | 100.3% | None <- 5%

## Fall
FERC 2010 Idaho Power Control Area Simultaneous Import Limit Study for Market Share Screening Analysis
VOLTAGE DEVIATIONS
|  |  | Seasonal Emergency Rating |  |  | Maximum
|  |  | *****OVERLOADS (%) ***** |  | Min | Relative
|  |  | Highest O/L |  | Absolute | Voltage
Case | Contingency | RAS | Line/Xfmr | Loading | Volt (p.u.) | Change | COMMENTS
08hs4a_ha_ipc_ca_sil | MIDPOINT T341 700 MVA 345/230 kV Xfmr | None | MIDPOINT T342 500 MVA 345/230 kV Xfmr | 99.9% | None <- 5%