## Sheet1
ANCILLARY SERVICES PROVIDED BY POWER PLANT FOR FISCAL YEAR 2014-2015
DRAFT
(Abbreviated terms are defined below Table)
|  | Voltage Level (kV) | PERCENT |  | DATE FIRST | GENERATION |  | RATING |  | ANCILLARY SERVICES |  |  |  | AGC Yes/No | AVC Yes/No | PARTICIPATING |  |  |  |  | VOLTAGE CONTROL CAPABILITY
|  |  | GENERATING |  | CARRIED | NAMEPLATE |  | CAPABILITY (MW) |  | PROVIDED BY SCHEDULES | [5 empty] | AGC UNITS |  |  | Q.S.C | B.A.A |  | IF YES ON VOLTAGE CONTROL (V.C.)
NAME OF | UNIT |  | UNIT | UNIT | SYSTEM |  |  |  |  | Please check one or more | [5 empty] | A.G.C. UNITS | IF YES ON A.G.C. |  |  |  | V.C. |  | PMAX |  | PMIN |  | Notes
PLANT | NO. |  | OWNERSHIP | TYPE | LOAD | MVA | MW | SUMMER | WINTER | S2 | S3 | S5 | S6 |  |  | YES/NO | A.P.T. on AGC | R.O.H. | YES/NO | YES/NO | YES/NO | EXCITER (kW) | MAX(MVAR) | MIN(MVAR) | MAX(MVAR) | MIN(MVAR)
HYDRO
San Francisquito Power Plant 1 | 1A | 115 | 100% | Hydro | 1983-12-10 | 25 | 25 | 46.5 | 13 | X |  |  |  | No | Yes | NO | N/A | AGI | Yes | Yes | Yes | 167 | 9 | -14 | 14 | -19
| 3 | 115 | 100% | Hydro | 1917-04-16 | 11.719 | 9.375 |  |  | X |  |  |  | No | Yes | NO | N/A |  | Yes | Yes | Yes | 25 | 4.5 | -6 | 6 | -11.7
| 4 | 115 | 100% | Hydro | 1923-05-21 | 12.5 | 10 |  |  | X |  |  |  | No | Yes | NO | N/A |  | Yes | Yes | Yes | 25 | 5 | -7.5 | 6.6 | -12.5
| 5A | 115 | 100% | Hydro | 1987-04-09 | 25 | 25 |  |  | X |  |  |  | No | Yes | NO | N/A |  | Yes | Yes | Yes | 167 | 9 | -14 | 14 | -19
San Francisquito Power Plant 2 | 1 | 115 | 100% | Hydro | 1919-07-06 | 17.5 | 14 | 18 | 5.7 | X |  |  |  | No | Yes | NO | N/A |  | Yes | Yes | Yes | 75 | 0 | 0 | 0 | 0
| 2 | 115 | 100% | Hydro | 1919-08-07 | 17.5 | 14 |  |  | X |  |  |  | No | Yes | NO | N/A |  | Yes | Yes | Yes | 75 | 10.5 | -10.5 | 13.2 | -17.5
| 3 | 115 | 100% | Hydro | 1932-09-26 | 17.5 | 14 |  |  | X |  |  |  | No | Yes | NO | N/A |  | Yes | Yes | Yes | 75 | 8 | -1 | 13 | -14
San Fernando Power Plant | 1 | 34.5 | 100% | Hydro | 1922-10-22 | 3.5 | 2.8 | 6 | 2.1 |  |  |  |  | No | No | NO | N/A |  | Yes | Yes | Yes | 60 | 0 | 0 | 0 | 0
| 2 | 34.5 | 100% | Hydro | 1922-10-22 | 3.5 | 2.8 | [6 empty] | No | No | NO | N/A |  | Yes | Yes | Yes | 60 | 0 | 0 | 0 | 0
Foothill Power Plant | 1 | 34.5 | 100% | Hydro | 1971-10-06 | 11 | 11 | 9.9 | 2.9 |  |  |  |  | No | No | NO | N/A |  | Yes | Yes | Yes | 105 | 0 | 0 | 0 | 0
Franklin Power Plant | 1 | 34.5 | 100% | Hydro | 1921-06-03 | 2.5 | 2 | 2 | 0.4 |  |  |  |  | No | No | NO | N/A |  | Yes | Yes | No | 28 | N/A | N/A | N/A | N/A
Sawtelle Power Plant | 1 | 34.5 | 100% | Hydro | 1986-06-05 | 0.711 | 0.64 | 0.65 | 0.13 |  |  |  |  | No | No | NO | N/A |  | Yes | Yes | Yes | 7 | 0 | 0 | 0 | 0
Haiwee Power Plant | 1 | 34.5 | 100% | Hydro | 1927-07-18 | 3.5 | 2.8 | 11.83 | 0 |  |  |  |  | No | No | NO | N/A |  | Yes | Yes | Yes | 32 | 0 | 0 | 0 | 0
| 2 | 34.5 | 100% | Hydro | 1927-07-18 | 3.5 | 2.8 | [6 empty] | No | No | NO | N/A |  | Yes | Yes | Yes | 32 | 0 | 0 | 0 | 0
Cottonwood Power Plant | 1 | 34.5 | 100% | Hydro | 1908-11-13 | 0.937 | 0.75 |  | 0.4 |  |  |  |  | No | No | NO | N/A |  | Yes | Yes | No | 45 | N/A | N/A | N/A | N/A | Single Exciter for both Units
| 2 | 34.5 | 100% | Hydro | 1909-10-13 | 0.937 | 0.75 | [6 empty] | No | No | NO | N/A |  | Yes | Yes | No
Division Creek P. P. | 1 | 34.5 | 100% | Hydro | 1909-03-22 | 0.75 | 0.6 |  | 0.4 |  |  |  |  | No | No | NO | N/A |  | Yes | Yes | No | 20 | N/A | N/A | N/A | N/A
Big Pine Power Plant | 1 | 34.5 | 100% | Hydro | 1925-07-29 | 4 | 3.2 |  | 0.4 |  |  |  |  | No | No | NO | N/A |  | Yes | Yes | Yes | 32 | 0 | 0 | 0 | 0
Pleasant Valley P. P. | 1 | 34.5 | 100% | Hydro | 1958-02-05 | 4 | 3.2 |  | 0 |  |  |  |  | No | No | NO | N/A |  | Yes | Yes | Yes | 40 | 0 | 0 | 0 | 0
Upper Gorge P. P. | 1 | 230 | 100% | Hydro | 1953-06-15 | 37.5 | 37.5 | 112.5 | 109.5 | X |  | X | X | No | Yes | NO | N/A |  | Yes | Yes | Yes | 210 | 2 | -1 | 9 | -21
Middle Gorge P. P. | 1 |  | 100% | Hydro | 1952-05-11 | 37.5 | 37.5 |  |  | X |  | X | X | No | Yes | NO | N/A |  | Yes | Yes | Yes | 210 | 2 | -1 | 9 | -21
Control Gorge P. P. | 1 |  | 100% | Hydro | 1952-04-01 | 37.5 | 37.5 |  |  | X |  | X | X | No | Yes | NO | N/A |  | Yes | Yes | Yes | 210 | 2 | -1 | 9 | -21
PUMP STORAGE [Hydro]
Castaic Power Plant | 1 | 230 | 100% | Pump Storage | 1973-07-11 | 250 | 212 | 1250.00 [2] | 1175 | X | X | X | X | Yes | Yes | Yes | 100% | AGI | Yes | Yes | Yes | 770 | 120 | -60 | 180 | -200
| 2 |  | 100% | Pump Storage | 1974-07-09 | 287.5 | 265 |  |  | X | X | X | X | Yes | Yes | Yes | 100% |  | Yes | Yes | Yes | 770 | 85 | -65 | 150 | -200
| 3 |  | 100% | Pump Storage | 1976-07-13 | 287.5 | 265 |  |  | X | X | X | X | Yes | Yes | Yes | 100% |  | Yes | Yes | Yes | 770 | 96 | -32 | 132 | -122
| 4 |  | 100% | Pump Storage | 1977-06-16 | 287.5 | 265 |  |  | X | X | X | X | Yes | Yes | Yes | 100% |  | Yes | Yes | Yes | 770 | 117 | -39 | 157 | -135
| 5 |  | 100% | Pump Storage | 1977-12-16 | 287.5 | 265 |  |  | X | X | X | X | Yes | Yes | Yes | 100% |  | Yes | Yes | Yes | 770 | 120 | -78 | 160 | -175
| 6 |  | 100% | Pump Storage | 1978-08-11 | 287.5 | 265 |  |  | X | X | X | X | Yes | Yes | Yes | 100% |  | Yes | Yes | Yes | 770 | 80 | -60 | 139 | -200
| 7 |  | 100% | Pump Storage | 1972-01-27 | 70 | 56 |  |  | X | X | X | X | Yes | Yes | Yes | 100% |  | Yes | Yes | Yes | 400 | 45 | -49 | 55 | -60
BASIN THERMAL
Harbor Generating Station | 1 | 138 | 100% | Natural Gas [CC] | 1995-01-31 | 100.4 | 85.34 | 452 | 78 | X | X | X |  | Yes | Yes | Yes | 100% | AGI | NO | Yes | Yes | 275 | 54 | -13 | N/A | N/A
| 2 |  | 100% | Natural Gas [CC] | 1995-01-31 | 100.4 | 85.34 |  | 78 | X | X | X |  | Yes | Yes | Yes | 100% |  | NO | Yes | Yes | 275 | 54 | -13 | N/A | N/A
| 5 |  | 100% | Natural Gas [CC] | 1995-01-31 | 93.75 | 75 |  | 65 | X | X | X |  | Yes | Yes | Yes | 100% |  | NO | Yes | Yes | 300 | 29 | -23 | N/A | N/A
| 10 |  | 100% | Natural Gas [CT] | 2002-01-04 | 71.176 | 60.5 |  | 47.4 | X | X | X |  | Yes | Yes | NO | N/A |  | Yes (+) | Yes | Yes | 213 | 44 | -15 | 55 | -18
| 11 |  | 100% | Natural Gas [CT] | 2002-01-04 | 71.176 | 60.5 |  | 47.4 | X | X | X |  | Yes | Yes | NO | N/A |  | Yes (+) | Yes | Yes | 213 | 44 | -15 | 55 | -18
| 12 |  | 100% | Natural Gas [CT] | 2002-01-04 | 71.176 | 60.5 |  | 47.4 | X | X | X |  | Yes | Yes | NO | N/A |  | Yes (+) | Yes | Yes | 213 | 44 | -15 | N/A | N/A
| 13 |  | 100% | Natural Gas [CT] | 2002-01-04 | 71.176 | 60.5 |  | 47.4 | X | X | X |  | Yes | Yes | NO | N/A |  | Yes (+) | Yes | Yes | 213 | 44 | -15 | 55 | -18
| 14 |  | 100% | Natural Gas [CT] | 2002-01-04 | 71.176 | 60.5 |  | 47.4 | X | X | X |  | Yes | Yes | NO | N/A |  | Yes (+) | Yes | Yes | 213 | 44 | -15 | 55 | -18
Valley Generating Station | 5 | 230 | 100% | Natural Gas [CT] | 2001-08-17 | 71.176 | 60.5 | 43 | 43 | X | X | X |  | Yes | Yes | NO | N/A |  | Yes | Yes | Yes | 213 | 45 | -15 | 55 | -17
| 6 |  | 100% | Natural Gas [CC] | 2003-09-04 | 215 | 182.75 | 156 | 162 | X | X | X |  | Yes | Yes | Yes | 100% |  | NO | Yes | Yes | 555 | 125 | -60 | 145 | -70
| 7 |  | 100% | Natural Gas [CC] | 2003-09-09 | 215 | 182.75 | 156 | 162 | X | X | X |  | Yes | Yes | Yes | 100% |  | NO | Yes | Yes | 555 | 125 | -60 | 145 | -70
| 8 |  | 100% | Natural Gas [CC] | 2003-11-13 | 311 | 264.35 | 201 | 209 | X | X | X |  | Yes | Yes | Yes | 100% |  | NO | Yes | Yes | 860 | 205 | -90 | 220 | -100
Scattergood Generating Station | 1 | 138 | 100% | Natural Gas [ST] | 1958-12-07 | 192 | 163.2 | 796 | 183 | X | X | X |  | Yes | Yes | Yes | 100% |  | NO | Yes | Yes | 450 | 65 | -58 | 130 | -70
| 2 | 138 | 100% | Natural Gas [ST] | 1959-07-01 | 192 | 163.2 |  | 184 | X | X | X |  | Yes | Yes | Yes | 100% |  | NO | Yes | Yes | 450 | 65 | -58 | 130 | -70
| 3 | 230 | 100% | Natural Gas [ST] | 1974-10-06 | 552 | 496.8 |  | 450 | X | X | X |  | Yes | Yes | NO | N/A |  | NO | Yes | Yes | 4183 | 260 | -250 | -395 | -280
Haynes Generating Station | 1 | 230 | 100% | Natural Gas [ST] | 1962-09-02 | 270 | 230 | 1585.2 | 1615.202 | X | X | X |  | Yes | Yes | Yes | 100% |  | NO | Yes | Yes | 971 | 122 | -55 | 182 | -100
| 2 |  | 100% | Natural Gas [ST] | 1963-04-07 | 270 | 230 |  |  | X | X | X |  | Yes | Yes | Yes | 100% |  | NO | Yes | Yes | 971 | 122 | -50 | 182 | -100
| 8 |  | 100% | Natural Gas [ST] | 2005-01-25 | 311 | 264 |  |  | X | X | X |  | Yes | Yes | Yes | 100% |  | NO | Yes | Yes | 863 | 175 | -80 | 220 | -105
| 9 |  | 100% | Natural Gas [CT] | 2005-01-25 | 215 | 182.75 |  |  | X | X | X |  | Yes | Yes | Yes | 100% |  | NO | Yes | Yes | 560 | 120 | -55 | 150 | -70
| 10 |  | 100% | Natural Gas [CT] | 2005-01-25 | 215 | 182.75 |  |  | X | X | X |  | Yes | Yes | Yes | 100% |  | NO | Yes | Yes | 560 | 120 | -55 | 150 | -70
| 11 |  | 100% | Natural Gas [CT] | 2013-06-11 | 127.282 | 108.19 |  |  | X | X | X | X | Yes | Yes | Yes | 100% |  | NO | Yes | Yes |  | 92 | -20 | N/A | N/A
| 12 |  | 100% | Natural Gas [CT] | 2013-06-12 | 127.282 | 108.19 |  |  | X | X | X | X | Yes | Yes | Yes | 100% |  | NO | Yes | Yes |  | 92 | -20 | 136 | -60
| 13 |  | 100% | Natural Gas [CT] | 2013-06-12 | 127.282 | 108.19 |  |  | X | X | X | X | Yes | Yes | Yes | 100% |  | NO | Yes | Yes |  | 92 | -20 | N/A | N/A
| 14 |  | 100% | Natural Gas [CT] | 2013-06-19 | 127.282 | 108.19 |  |  | X | X | X | X | Yes | Yes | Yes | 100% |  | NO | Yes | Yes |  | 92 | -20 | 136 | -60
| 15 |  | 100% | Natural Gas [CT] | 2013-06-12 | 127.282 | 108.19 |  |  | X | X | X | X | Yes | Yes | Yes | 100% |  | NO | Yes | Yes |  | 92 | -20 | N/A | N/A
| 16 |  | 100% | Natural Gas [CT] | 2013-06-12 | 127.282 | 108.19 |  |  | X | X | X | X | Yes | Yes | Yes | 100% |  | NO | Yes | Yes |  | 92 | -20 | N/A | N/A
EXTERNAL THERMAL
Apex Generating Station | 1A |  | 100% | Natural Gas [CC] | 2014-03-28 | 239 | 162 | 479.9 | 531.86 |  |  |  |  | No | No | Yes | 100% | [5 empty] | 39 | -59
| 1B |  | 100% | Natural Gas [CC] | 2014-03-31 | 239 | 162 | [6 empty] | No | No | Yes | 100% | [5 empty] | 37 | -60
| STG |  | 100% | Natural Gas [ST] | 2014-03-28 | 264 | 207.86 | [6 empty] | No | No | Yes | 100% | [5 empty] | 37 | -67
Navajo Generating Station | 1 |  | 21.2% | Coal [FF] | 1974-02-01 | 892.4 | 803 | 477 | 477 |  |  |  |  | No | No | Yes (*) | SRP (*) |  | SRP | NO | Yes | 579 | 350 | -140
| 2 |  | 21.2% | Coal [FF] | 1974-12-02 | 892.4 | 803 | [6 empty] | No | No | Yes (*) | SRP (*) |  | SRP | NO | Yes | 579 | 350 | -140
| 3 |  | 21.2% | Coal [FF] | 1975-11-29 | 892.4 | 803 | [6 empty] | No | No | Yes (*) | SRP (*) |  | SRP | NO | Yes | 579 | 350 | -140
Intermountain Generating Station | 1 | 500DC | 66.79% | Coal [FF] | 1986-06-09 | 991 | 820 | 1202 | 1202 | X |  | X |  | No | Yes | Yes | 100% |  | Yes | Yes | Yes | 3913 | 300 | 300
| 2 |  | 66.79% | Coal [FF] | 1987-04-30 | 991 | 820 |  |  | X |  | X |  | No | Yes | Yes | 100% |  | Yes | Yes | Yes | 3913 | 300 | 300
Palo Verde Nuclear Generating Station | 1 |  | 9.66% | Nuclear | 1986-01-30 | 1550 | 1422 | 380.314 | 386.69 |  |  |  |  | No | No |  |  |  | APS | NO | YES
| 2 |  | 9.66% | Nuclear | 1986-09-19 | 1550 | 1413 | [6 empty] | No | No |  |  |  | APS | NO | YES
| 3 |  | 9.66% | Nuclear | 1988-01-19 | 1550 | 1413 | [6 empty] | No | No |  |  |  | APS | NO | YES
EXTERNAL HYDRO
Hoover Power Plant [1] | 17 units |  | 0% | Hydro | 1936 |  | 2080 | 491 | 390 |  | X | X | X | Yes | No | NO | APS (*) | N/A | N/A
WIND
Pine Tree Wind Power Plant | 1- 90 | 230 | 100.00% | Wind | 2009-06-01 | 150.03 | 135 | 135 | 135 |  |  |  |  | No | No | Yes | ** | AGI | ** | Yes | NO | N/A | N/A | N/A |  |  | Dynamic Signal for all Wind Power Plants
Milford Wind Power Plant I | 1- 97 | 500DC | 90.9% | Wind | 2009-11-06 | 198.993 | 203.5 | 203.5 | 203.5 |  |  |  |  | No | No | NO |  |  |  | Yes | NO | N/A | N/A | N/A
Milford Wind Power Plant II | 1- 67 | 500DC | 100% | Wind | 2011-05-01 | N/A | N/A | N/A | N/A |  |  |  |  | No | No | Yes |  |  |  | Yes | NO | N/A | N/A | N/A
Adelanto Solar Power Plant |  | 500 | 100% | Solar | 2012-06-30 | 10 | 10 | 10 | 10 |  |  |  |  | No | No | Yes |  |  |  | Yes | NO | N/A | N/A | N/A
Pine Tree Solar Pow. Plant |  |  | 100% | Solar | 2013-03-15 | 8.5 | 8.5 | 8.5 | 8.5 |  |  |  |  | No | No | Yes |  |  |  | Yes | NO | N/A | N/A | N/A

## Sheet3
|  | PERCENT |  | DATE FIRST | NET MAXIMUM CAPABILITY (MW) (JUNE 2013) | COMPLIANCE YEAR | AGE AT COMPLIANCE DATE
|  | GENERATING |  | CARRIED
NAME OF | UNIT | UNIT | UNIT | SYSTEM
PLANT | NO. | OWNERSHIP | TYPE | LOAD
Harbor Generating Station | 1 | 100% | Natural Gas [CC] | 1995-01-31 | 82 | 2029 | 34
| 2 | 100% | Natural Gas [CC] | 1995-01-31 | 82 | 2029 | 34
| 5 | 100% | Natural Gas [CC] | 1995-01-31 | 65 | 2029 | 34
| 10 | 100% | Natural Gas [CT] | 2002-01-04 | 47 | N/A
| 11 | 100% | Natural Gas [CT] | 2002-01-04 | 47.4 | N/A
| 12 | 100% | Natural Gas [CT] | 2002-01-04 | 47.4 | N/A
| 13 | 100% | Natural Gas [CT] | 2002-01-04 | 47.4 | N/A
| 14 | 100% | Natural Gas [CT] | 2002-01-04 | 47.4 | N/A
Scattergood Generating Station | 1 | 100% | Natural Gas [ST] | 1958-12-07 | 183 | 2024 | 66
| 2 | 100% | Natural Gas [ST] | 1959-07-01 | 184 | 2024 | 65
| 3 | 100% | Natural Gas [ST] | 1974-10-06 | 450 | 2015 | 41
Haynes Generating Station | 1 | 100% | Natural Gas [ST] | 1962-09-02 | 222 | 2029 | 67
| 2 | 100% | Natural Gas [ST] | 1963-04-07 | 222 | 2029 | 66
| 5 | 100% | Natural Gas [ST] | 1966-08-12 | 600 | 2013 | 47
| 6 | 100% | Natural Gas [ST] | 1967-03-18 |  | 2013 | 46
| 7 | 100% | Natural Gas [Aux] | 1970-09-01 | 1.59 | N/A
| 8 | 100% | Natural Gas [CC] | 2005-01-25 | 250 | 2029 | 24
| 9 | 100% | Natural Gas [CC] | 2005-01-25 | 162.5 | 2029 | 24
| 10 | 100% | Natural Gas [CC] | 2005-01-25 | 162.5 | 2029 | 24
CC:Combined Cycle
CT: Combustion Gas Turbine
ST: Steam Turbine
Units 11 through 16 have replaced Unit 5 and 6 at 100 MW each
Note on G20: dobian: