|  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| O.O. | ***16-07570***  **16-07564**  ***16-03092***  **16-03094** | | | MISO No | **1-11113624**  ***1-10308732***  **1-10308692** | File No. | 240801 |
| **Abnormal Operating Condition:** | | 115 kV Line GP1 (Great Falls G.S. – Pine Falls G.S.)  230 kV Line D55Y (Dorsey – LaVerendrye) | | | | | |
| **Effective Dates:** | | | 2016-08-11 from 0700 to 2016-08-12 at 1600 CST  (2016-08-11 from 0700 to 2016-08-12 at 1600 EST) | | | | |
| **Standing Guide Reference:** | | | System Study as per L. Ruchkall - Generation Pattern 1 (Summer 451- 591 MW's) | | | | |

|  |  |
| --- | --- |
| **Description of Work:** | GP1 – Switching for Pine Falls 115-12 kV Bank 7 and associated 115kv Bus for civil to drill piles for the new 115kv Line PQ95 to Manigotagan.  D55Y – Momentary outage required to D55Y during switching to facilitate restoration of co-terminated Laverendrye Bank 1 for mtce.  Rescheduled from momentary outage Friday Aug 12 1530-1600 to two day outage Aug 11-12 to facilitate wiring mods related to LaVerendrye R21 synchronizer. |





|  |  |
| --- | --- |
| **Special Instructions to MHEB Operator:** | **Export**:  None.  **Import**: If RTCA indicates that the loss of F3M, ST5 or ST6 will cause overloads on WT34, transfer from IESO may need to be curtailed. |

|  |  |
| --- | --- |
| **MISO North RC Notes:** | MH\_ONT\_E (Export) SOL = 225 MW  MH\_ONT\_W (Import) SOL = 177 MW |
|  |  |
| **Special Instructions:** | **TOI Extensions** - This TOI may be extended until 23:59, by performing the following steps.  a) Verify system conditions to confirm there are no additional tie line facilities outages, or new internal MH outages.  b) Review RTCA to confirm there are no new contingencies.  c) Contact MISO to confirm there are no new outages, if there are no new outages provide notice to MISO that MH is extending the TOI.  d) Extend the outage in COLA  e) Update TLAP outage table  f) Provide notice to affected balancing authorities |

|  |  |  |  |
| --- | --- | --- | --- |
| **Prepared By:** | S. Brooks | **Date:** | 2016 08 09 |

Copies to:

SOSS, System Control Centre NSSS, System Control Centre

GSSS, System Control Centre GSO, System Control Centre

Operating Order Ontario IESO

MISO – St. Paul MHEB OASIS

File 240801