| O.O. | Forbes-SVS 16-09843 | MISO No. | 1-11221518 | File No. |  |
| --- | --- | --- | --- | --- | --- |
| Name of Outage: | Forbes 500/230 kV SVS |
| Effective Dates: | 2016-08-03 0600 to 2016-08-10 1900 CDT (2016-08-03 0600 to 2016-08-10 1900 EST) |
| Standing Guide Reference: | MHEX – USA Summer Standing Guide |

| Description of Work: | Forced Out due to controls issues |
| --- | --- |
| TRANSFER LIMITS: |
| MH-USA South (MH Export) |
|  |  |  | SOL: | 1855 |  | Schedule Limit | 1630 |
| Location |  | RM |  | CRSG | OM |  |  | Schedule Limit |
|  | TTC |  | Transfer (SOL) |  |  | Firm | Non-Firm |  |
| USA | 1855 | 0 | 1855 | 150 | 75 | 1315 | 0 | 1630 |
| MH-USA North (MH Import) |
| IROL | 1090 |  | SOL: | 900 |  | Schedule Limit | 850 |
| Location |  | RM |  | CRSG | OM |  |  | Schedule Limit |
|  | TTC |  | Transfer (SOL) |  |  | Firm | Non-Firm |  |
| USA | 930 | 30 | 900 | 0 | 890 | 10 | 840 | 850 |
| TLR Triggers | South TLR 1 | South TLR 3 | North TLR 1 | North TLR 3 |  |
|  | 1671 | 1705 | 837 | 855 |  |

| MISO Webtool Postings (Winter) | MISO Webtool Postings TTC TRM Coeff MHEX_S (Export) 1855 540 0.417 MHEX_N (Import) 930 920 0.087 |
| --- | --- |

| Special Notes to MISO North RC | A) During this prior outage condition generation curtailment of the St. Joseph and St. Leon wind farms concurrent with TLR on MHEX_N may be required when Manitoba to USA flows are north to prevent post contingent overloads on G37C following a trip of B10T or M602F. B) The SOL for MHEX_S is 1540 MW and MHEX_ N is 560 MW if the MISO RTCA and MISO Flowgate Monitoring Tool are unavailable prior to or during this outage. |
| --- | --- |

| Special Instructions to MHEB Operator: | A) TOI Extentions - This TOI may be extended until 23:59 by performing the following steps: Verify system conditions to confirm there are no additional tie line facilities outages, or new internal MH outages. Review RTCA to confirm there are no new contingencies. Contact MISO to confirm there are no new outages, if there are no new outages provide notice to MISO that MH is extending the TOI. Extend the outage in COLA. Update TLAP outage table. Provide notice to affected balancing authorities B) When called upon by MISO for the supply of CRSG: If Real Time Contingency Analysis (RTCA) indicates a post contingent overload condition on Y51L for the contingent loss of D14S - redispatch MH generation to maintain CRSG delivery as per: Start Brandon Gas Generation and run up to 60 MW. Brandon generation must be re-dispatched from HVDC generation at Dorsey After 60 MW re-dispatch is complete, should RTCA continues to indicate a post contingent overload condition on Y51L due to the contingent loss of D14S, Continue to re-dispatch generation from Brandon gas in 10 MW increments until post contingent overload on Y51L has been mitigated. The mitigation must be completed within 30 minutes. |
| --- | --- |

Prepared By: Hogeveen Rutter Date: 2016 07 25

Copies to:

SOSS, System Control Centre			MISO

NSSS, System Control Centre			GSO, System Control Centre

GSSS, System Control Centre