|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| O.O. | **16-08046****16-07838** | MISO No | ***1-11569331******1-11523086*** | File No. | 240801 |
| **Abnormal Operating Condition:** | 115 kV Line CR2 (Parkdale – Rosser) 115 kV Line GP1 (Great Falls G.S. – Pine Falls G.S.)  |
| **Effective Dates:** | 2016-11-07 from 0600 to 2016-11-07 at 0900 CST(2016-11-07) from 0700 to 2016-11-07 at 1000 EST) |
| **Standing Guide Reference:** | System study as per L. Ruchkall - Generation Pattern 1 (Winter 451- 591 MW's) |

|  |  |
| --- | --- |
| **Description of Work:** | CR2 – Change tower peak on structure #35 and splice out double dead-ended to a tangent structure. RP16 and CR2 on common tower.GP1 – TLAP Driver for 115 kV Line GP1 open ended at Pine Falls for parent order 16-06645-OO. |





|  |  |
| --- | --- |
| **Special Instructions to MHEB Operator:** | **Export**:  None. **Import**: If RTCA indicates that the loss ST5 or ST6 will cause overloads on WT34, transfer from IESO may need to be curtailed. |

|  |  |
| --- | --- |
| **MISO North RC Notes:** | MH\_ONT\_E (Export) SOL = 300 MWMH\_ONT\_W (Import) SOL = 300 MWMH\_ONT\_E (Export)\_Transfer Limits\_SOL\_During\_Offloads = 190 MW MH\_ONT\_W (Import)\_Transfer Limits\_SOL\_During\_Offloads = 190 MW  |
|  |  |
| **Special Instructions:** | **TOI Extensions** - This TOI may be extended until 23:59, by performing the following steps.a) Verify system conditions to confirm there are no additional tie line facilities outages, or new internal MH outages.b) Review RTCA to confirm there are no new contingencies.c) Contact MISO to confirm there are no new outages, if there are no new outages provide notice to MISO that MH is extending the TOI.d) Extend the outage in COLAe) Update TLAP outage tablef) Provide notice to affected balancing authorities |

|  |  |  |  |
| --- | --- | --- | --- |
| **Prepared By:** | S. Brooks | **Date:** | 2016 11 02 |

Copies to:

 SOSS, System Control Centre NSSS, System Control Centre

 GSSS, System Control Centre GSO, System Control Centre

 Operating Order Ontario IESO

 MISO – St. Paul MHEB OASIS

 File 240801