|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| O.O. |  **17-01066** **17-01486** **17-01487** **17-01488** | MISO No | **1-12546259** | File No. | 240801 |
| **Abnormal Operating Condition:** | 115 kV Line SM26 (Selkirk G.S. – Mercy Street)  |
| **Effective Dates:** | 2017-01-31 from 0830 to 2017-01-31 at 1600 CST(2017-01-31) from 0930 to 2017-01-31 at 1700 EST) and2017-02-01 from 0830 to 2017-02-01 at 1600 CST(2017-02-01) from 0930 to 2017-02-01 at 1700 EST) and2017-02-02 from 0830 to 2017-02-02 at 1600 CST(2017-02-02) from 0930 to 2017-02-02 at 1700 EST)and2017-02-03 from 0830 to 2017-02-03 at 1600 CST(2017-02-03) from 0930 to 2017-02-03 at 1700 EST) |
| **Standing Guide Reference:** | MH-IESO Standing Guide - Generation Pattern 1 (Winter 451- 591 MW's) |

|  |  |
| --- | --- |
| **Description of Work:** | Insulator changes and repair broken strands on conductors. The work area is from structure # 12 to structure # 28. The west side of the Red River to Mercy station.Line to be returned at the end of each day.  |





|  |  |
| --- | --- |
| **Special Instructions to MHEB Operator:** | **Export**:  None. **Import**: If RTCA indicates that the loss ST5 or ST6 will cause overloads on WT34, transfer from IESO may need to be curtailed. |

|  |  |
| --- | --- |
| **MISO North RC Notes:** | MH\_ONT\_E (Export) SOL = 300 MWMH\_ONT\_W (Import) SOL = 300 MWMH\_ONT\_E (Export)\_Transfer Limits\_SOL\_During\_Offloads = 190 MW MH\_ONT\_W (Import)\_Transfer Limits\_SOL\_During\_Offloads = 190 MW  |
|  |  |
| **Special Instructions:** | **TOI Extensions** - This TOI may be extended until 23:59, by performing the following steps.a) Verify system conditions to confirm there are no additional tie line facilities outages, or new internal MH outages.b) Review RTCA to confirm there are no new contingencies.c) Contact MISO to confirm there are no new outages, if there are no new outages provide notice to MISO that MH is extending the TOI.d) Extend the outage in COLAe) Update TLAP outage tablef) Provide notice to affected balancing authorities |

|  |  |  |  |
| --- | --- | --- | --- |
| **Prepared By:** | J. Thompson | **Date:** | 2017 01 19 |

Copies to:

 SOSS, System Control Centre NSSS, System Control Centre

 GSSS, System Control Centre GSO, System Control Centre

 Operating Order Ontario IESO

 MISO – St. Paul MHEB OASIS

 File 240801