|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| O.O. | ***17-00275*** | MISO No | ***1-14060739*** | File No. | 240801 |
| **Abnormal Operating Condition:** | 115 kV Line TV1 (Transcona – St. Vital) |
| **Effective Dates:** | 2017-07-04 from 0830 to 2017-07-14 at 1600 CST(2017-07-04 from 0830 to 2017-07-14 at 1600 EST) |
| **Standing Guide Reference:** | Study as per L. Ruchkall and K. Prystay - Generation Pattern 1 and 3 (Summer 301- 553 MW's) |

|  |  |
| --- | --- |
| **Description of Work:** | TV1 – Transcona 115 kV Breaker TV1 Line Disconnect corrective, and Bushing replacement. St. Vital 115 kV Brealer TV1 Insulation checks, mechanical checks, and Line Disconnect hot spot repair. |





|  |  |
| --- | --- |
| ***Special Instructions to MHEB Operator:*** | **Export**:  If RTCA indicates that the loss of SR3 will cause an overload on SG12, or the loss of K21W, will cause an overload on Bank 8, loss of K22W, will cause an overload on Bank 7, transfer from IESO may need to be curtailed.  **Import**: If RTCA indicates that the loss of TP65 will cause overload on TV2, transfer from IESO may need to be curtailed. |

|  |  |
| --- | --- |
| **MISO North RC Notes:** | MH\_ONT\_E (Export) SOL = 225 MWMH\_ONT\_W (Import) SOL = 182 MWMH\_ONT\_E (Export)\_Transfer Limits\_SOL\_During\_Offloads = 140 MW MH\_ONT\_W (Import)\_Transfer Limits\_SOL\_During\_Offloads = 130 MW  |
|  |  |
| **Special Instructions:** | **TOI Extensions** - This TOI may be extended until 23:59, by performing the following steps.a) Verify system conditions to confirm there are no additional tie line facilities outages, or new internal MH outages.b) Review RTCA to confirm there are no new contingencies.c) Contact MISO to confirm there are no new outages, if there are no new outages provide notice to MISO that MH is extending the TOI.d) Extend the outage in COLAe) Update TLAP outage tablef) Provide notice to affected balancing authorities |

|  |  |  |  |
| --- | --- | --- | --- |
| **Prepared By:** | J. Thompson | **Date:** | 2017 06 27 |

Copies to:

 SOSS, System Control Centre NSSS, System Control Centre

 GSSS, System Control Centre GSO, System Control Centre

 Operating Order Ontario IESO

 MISO – St. Paul MHEB OASIS

 File 240801