|  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| O.O. | ***17-06121*** | | | MISO No | ***1-14865492*** | File No. | 240801 |
| **Abnormal Operating Condition:** | | 230 kV Line D13R (Dorsey – Rosser) | | | | | |
| **Effective Dates:** | | | 2017-09-12 from 0700 to 2017-09-22 at 1600 CDT  (2017-09-12 from 0700 to 2017-09-22 at 1600 EST) | | | | |
| **Standing Guide Reference:** | | | MH- IESO Standing Guide - Generation Pattern 1, 3 and 5 (Summer 166- 553 MW's) | | | | |

|  |  |
| --- | --- |
| **Description of Work:** | D13R – Civil Construction will be pouring concrete pads. AMD will be putting in a new box and wiring for the line PT. Bank 4 insulation checks, BK4 arrestor repair, BK4 CT conduit replacement. |





|  |  |
| --- | --- |
| **Special Instructions to MHEB Operator:** | **Export**:  If RTCA indicates that the loss of SR3 will cause an overload on SG12, or the loss of K21W will cause an overload on Whiteshell Bank 8, or the loss of K22W will cause an overload on Whiteshell Bank 7 transfer from IESO may need to be curtailed.   **Import**: If RTCA indicates that the loss of ST5 or ST6, will cause an overload on WT34, or the loss of K21W will cause an overload on Whiteshell Bank 8, or the loss of K22W will cause an overload on Whiteshell Bank 7 transfer from IESO may need to be curtailed. |

|  |  |
| --- | --- |
| **MISO North RC Notes:** | MH\_ONT\_E (Export) Transfer Limit = 225 MW  MH\_ONT\_W (Import) Transfer Limit = 225 MW  MH\_ONT\_E (Export) Transfer Limit During Offloads = 140 MW  MH\_ONT\_W (Import) Transfer Limit During Offloads = 130 MW |
|  |  |
| **Special Instructions:** | **TOI Extensions** - This TOI may be extended until 23:59, by performing the following steps.  a) Verify system conditions to confirm there are no additional tie line facilities outages, or new internal MH outages.  b) Review RTCA to confirm there are no new contingencies.  c) Contact MISO to confirm there are no new outages, if there are no new outages provide notice to MISO that MH is extending the TOI.  d) Extend the outage in COLA  e) Update TLAP outage table  f) Provide notice to affected balancing authorities |

|  |  |  |  |
| --- | --- | --- | --- |
| **Prepared By:** | J. Thompson | **Date:** | 2017 09 06 |

Copies to:

SOSS, System Control Centre NSSS, System Control Centre

GSSS, System Control Centre GSO, System Control Centre

Operating Order Ontario IESO

MISO – St. Paul MHEB OASIS

File 240801