|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| O.O. |  ***17-06121*** ***17-09125*** | MISO No |  ***1-14865492***  ***1-14946714*** | File No. | 240801 |
| **Abnormal Operating Condition:** | 230 kV Line D13R (Dorsey – Rosser)115 kV Line MC28 (Mercy – Parkdale) |
| **Effective Dates:** | 2017-09-20 from 0800 to 2017-09-20 at 1600 CDT(2017-09-20 from 0800 to 2017-09-20 at 1600 EST) |
| **Standing Guide Reference:** | Study as per K. Prystay - Generation Pattern 1, 3 and 5 (Summer 165- 553 MW's) |

|  |  |
| --- | --- |
| **Description of Work:** | D13R – Civil Construction will be pouring concrete pads. AMD will be putting in a new box and wiring for the line PT. Bank 4 insulation checks, BK4 arrestor repair, BK4 CT conduit replacement. MC28 – 115 kV Line must be removed from service in order for a crane to get access to remove and install Breaker Bushings at Parkdale. |





|  |  |
| --- | --- |
| **Special Instructions to MHEB Operator:** | **Export**:  If RTCA indicates that the loss of SR3 will cause the overload of SG12, then the transfer from IESO may need to be curtailed. **Import**: If RTCA indicates that the loss of ST5 or ST6 will cause an overload on WT34 or the loss of WT34 will overload ST5, then the transfer from IESO may need to be curtailed. |

|  |  |
| --- | --- |
| **MISO North RC Notes:** | MH\_ONT\_E (Export) Transfer Limit = 225 MWMH\_ONT\_W (Import) Transfer Limit = 225 MWMH\_ONT\_E (Export) Transfer Limit During Offloads = 140 MWMH\_ONT\_W (Import) Transfer Limit During Offloads = 130 MW |
|  |  |
| **Special Instructions:** | **TOI Extensions** - This TOI may be extended until 23:59, by performing the following steps.a) Verify system conditions to confirm there are no additional tie line facilities outages, or new internal MH outages.b) Review RTCA to confirm there are no new contingencies.c) Contact MISO to confirm there are no new outages, if there are no new outages provide notice to MISO that MH is extending the TOI.d) Extend the outage in COLAe) Update TLAP outage tablef) Provide notice to affected balancing authorities |

|  |  |  |  |
| --- | --- | --- | --- |
| **Prepared By:****Revised By:** | J. ThompsonJ. Thompson  | **Date:** | 2017 09 142017 09 18 |

Copies to:

 SOSS, System Control Centre NSSS, System Control Centre

 GSSS, System Control Centre GSO, System Control Centre

 Operating Order Ontario IESO

 MISO – St. Paul MHEB OASIS

 File 240801