|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| O.O. |  ***17-02015*** | MISO No | ***1-15140715*** | File No. | 240801 |
| **Abnormal Operating Condition:** | 115 kV Line WT34 (Whiteshell – Transcona)  |
| **Effective Dates:** | 2017-10-16 from 0800 to 2017-10-19 at 1630 CDT(2017-10-16 from 0800 to 2017-10-19 at 1630 EST) |
| **Standing Guide Reference:** | MH-IESO Standing Guide - Generation Pattern 1, 3 and 5 (Summer 250- 500 MW's) |

|  |  |
| --- | --- |
| **Description of Work:** | WT34 – Clearance needed for the installation of the new tower for Riel electrode Line. |





|  |  |
| --- | --- |
| **Special Instructions to MHEB Operator:** | **Export**:  If RTCA indicates that the loss of SR3 will cause an overload on SG12, transfer from IESO may need to be curtailed. **Import**: If RTCA indicates that the loss of ST5, will cause an overload on ST6, or vice versa, loss of PR2, will cause an overload on SG12, transfer from IESO may need to be curtailed. |

|  |  |
| --- | --- |
| **MISO North RC Notes:** | MH\_ONT\_E (Export) Transfer Limit = 215 MWMH\_ONT\_W (Import) Transfer Limit = 162 MWMH\_ONT\_E (Export) Transfer Limit During Offloads = 140 MWMH\_ONT\_W (Import) Transfer Limit During Offloads = 130 MW |
|  |  |
| **Special Instructions:** | **TOI Extensions** - This TOI may be extended until 23:59, by performing the following steps.a) Verify system conditions to confirm there are no additional tie line facilities outages, or new internal MH outages.b) Review RTCA to confirm there are no new contingencies.c) Contact MISO to confirm there are no new outages, if there are no new outages provide notice to MISO that MH is extending the TOI.d) Extend the outage in COLAe) Update TLAP outage tablef) Provide notice to affected balancing authorities |

|  |  |  |  |
| --- | --- | --- | --- |
| **Prepared By:** | J. Thompson | **Date:** | 2017 10 11 |

Copies to:

 SOSS, System Control Centre NSSS, System Control Centre

 GSSS, System Control Centre GSO, System Control Centre

 Operating Order Ontario IESO

 MISO – St. Paul MHEB OASIS

 File 240801