|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| O.O. |  ***17-10762*** | MISO No | ***1-15377902*** | File No. | 240801 |
| **Abnormal Operating Condition:** | 115 kV Line GS22 (Great Falls – Selkirk)  |
| **Effective Dates:** | 2017-11-01 from 0700 to 2017-11-01 at 1700 CDT(2017-11-01 from 0700 to 2017-11-01 at 1700 EST) |
| **Standing Guide Reference:** | MH- IESO Standing Guide - Generation Pattern 1 and 3 (Winter 301- 500 MW's) |

|  |  |
| --- | --- |
| **Description of Work:** | GS22 – Selkirk Generating Station 115 kV GS22 M.O. Disconnect will not operate in auto, repair is needed.  |





|  |  |
| --- | --- |
| **Special Instructions to MHEB Operator:** | **Export**:  None  **Import**: If RTCA indicates that the loss of ST5 or ST6 will cause an overload on WT34, transfer from IESO may need to be curtailed. |

|  |  |
| --- | --- |
| **MISO North RC Notes:** | MH\_ONT\_E (Export) Transfer Limit = 300 MWMH\_ONT\_W (Import) Transfer Limit = 300 MWMH\_ONT\_E (Export) Transfer Limit During Offloads = 190 MWMH\_ONT\_W (Import) Transfer Limit During Offloads = 190 MW |
|  |  |
| **Special Instructions:** | **TOI Extensions** - This TOI may be extended until 23:59, by performing the following steps.a) Verify system conditions to confirm there are no additional tie line facilities outages, or new internal MH outages.b) Review RTCA to confirm there are no new contingencies.c) Contact MISO to confirm there are no new outages, if there are no new outages provide notice to MISO that MH is extending the TOI.d) Extend the outage in COLAe) Update TLAP outage tablef) Provide notice to affected balancing authorities |

|  |  |  |  |
| --- | --- | --- | --- |
| **Prepared By:** | J. Thompson | **Date:** | 2017 10 26 |

Copies to:

 SOSS, System Control Centre NSSS, System Control Centre

 GSSS, System Control Centre GSO, System Control Centre

 Operating Order Ontario IESO

 MISO – St. Paul MHEB OASIS

 File 240801