| O.O. | 18-04721-OO (B69R) | MISO No. | 1-17566847 | File No. | 240802 |
| --- | --- | --- | --- | --- | --- |
| Name of Outage: | 230 kV Line B69R (Birtle – Raven Lake) |
| Effective Dates: | 2018-03-25 from 0400 to 1600 CDT (2017-05-16 from 0400 to 1600 EST) |
| Standing Guide Reference: | MH-SPC Standing Guide |

| System Posturing | B10T will be operated within the range of "Scheduled / SOL" 150 / 165 MW South and "Scheduled / SOL" 75 / 95 MW North. West Flow “GRAPH” MAXIMUM of 900 MW was studied for this outage for west flow conditions. Monitor Graph by using the “GRAPH LIMIT” calculation. “GRAPH” MINIMUM of 0 MW. Maximum "PH" of 500 MW. Use "ARC Constant" value of 575 MW, for "GRAPH LIMIT" monitoring. East Flow “GRAPH” MAXIMUM of 900 MW was studied for this outage for east flow conditions. Monitor Graph by using the “GRAPH LIMIT” calculation. “GRAPH” MINIMUM of 0 MW. Maximum "PH" of 500 MW. Use "ARC Constant" value of 575 MW, for "GRAPH LIMIT" monitoring. Note: “GRAPH” = sum of Grand Rapids and Power to Ponton and Herblet Lake (This acronym replaces previous “GRPTPH” which had the same parameter value ) Note: “ARC” = sum of U91A and A4D “OUT” at Ashern plus MR11 “OUT” at Raven Lake plus C28R “IN” at Cornwallis. Note: “PH” - sum of Power to Ponton and Herblet Lake from lines P19W, J30P, W73H and W74H. (N.B: This acronym replaces previous “PTPH” which had the same parameter value). |
| --- | --- |
| Description of Work: | Trip and lock out of 230 kV Line B69R. Line patrol, troubleshooting and repair |
|  | TRANSFER Limits: MH-SPC West (MH Export) SOL: 225 Schedule Limit 200 Location TTC RM Transfer OM Schedule Limit (SOL) Firm Non-Firm West 225 0 225 25 200 0 200 MH-SPC East (MH Import) SOL: 75 Schedule Limit 50 Location TTC RM Transfer OM Schedule Limit (SOL) Firm Non-Firm East 75 0 75 25 50 0 50 |

| MISO RC INFO | System Intact FIRM SCHED LIMIT DYNAMIC SCHED LIMIT SOL TLR1 TLR3 MH-SPC_West (MH Export) 200 200 225 209 214 MH-SPC_East (MH Import) 50 50 75 70 71 |
| --- | --- |
|  | MISO Webtool Manual Override is Required MISO Webtool Postings TTC Firm TRM Non-Firm TRM Coeff MH_SPC _West (Export) 225 25 25 1.000 MH_SPC_East (Import) 75 25 25 1.000 |
| Special Instructions: | For high GRAPH conditions combined with MH-SPC East flows conditions (or low west flow conditions), MR11 may experience loading near steady state limits (depending on system conditions). Apply ambient rating as required (maximum 30C rating, MR11 SPS will activate at 30 C rating). Monitor RTCA overloads on A4D for loss of U91A after MR11 RAS operation in RTCA and re-dispatch GRAPH as required to mitigate overloads on A4D. TOI Extensions - This TOI may be extended until 23:59 by performing the following steps: Verify system conditions to confirm there are no additional tie line facilities outages, or new internal MH outages. Review RTCA to confirm there are no new contingencies. Contact MISO to confirm there are no new outages, if there are no new outages provide notice to MISO that MH is extending the TOI. Extend the outage in COLA. Update TLAP outage table. Provide notice to affected balancing authorities |

| Prepared By: | J. Kergen | Date: | 2018.03.25 |
| --- | --- | --- | --- |

Copies to:

SOSS, System Control Centre		NSSS, System Control Centre

GSSS, System Control Centre		GSO, System Control Centre

Operating Order		File 240802

MHEB OASIS		MISO – St. Paul

SPC – Yong Zheng		SPC - Colin Nicholson