## Slide 1
Local Area Planning Update – TRANSAC 6-29-16

## Slide 2
Base Case Status
Base case study models representing the base scenarios will be completed as follows for the 15 year planning horizon:
  Peak Load Scenarios representing Heavy Summer (HS) and Heavy Winter (HW) conditions for the 2016 - 2017, 2021, 2026, and 2031 seasons.
  Off-Peak Scenarios representing Light Spring (LSP) for the 2017 and 2021 seasons.
10 cases total.
Base Cases
Notes: Title, 20pt font, bold, white
Heading 1, 50pt font, RGB 210,0,0
Heading 2 white, 30pt font, background 1, darker 50% (bottom grey down from white color option)
Heading 3, 22pt font, bold, black lighter 25% (third down from black color option)
Body Copy/Bulleted Text, 22pt font, black lighter 25% (third down from black color option)

## Slide 3
Base Case Status – cont.
Existing system configuration will be modeled in 2016 -2017 HS, HW, and LSP cases.
Signed projects (GIA’s, EP&C’s, TSR’s, etc.) including new renewables and budgeted/approved system improvements will be included in future scenarios. Dispatch may depend on TSA’s.
All peak loading base cases will be based on a 1/10 load forecast.
All off-peak loading base cases will be based on 65% of the seasonal peak.
Wind generation dispatch 50% (sensitivity cases will consider other levels such as 0% or 100%)
Base Cases
Notes: Title, 20pt font, bold, white
Heading 1, 50pt font, RGB 210,0,0
Heading 2 white, 30pt font, background 1, darker 50% (bottom grey down from white color option)
Heading 3, 22pt font, bold, black lighter 25% (third down from black color option)
Body Copy/Bulleted Text, 22pt font, black lighter 25% (third down from black color option)

## Slide 4
Contingencies to Study
All new TPL outage scenarios will be performed (P1 through P7), as well as system normal scenario (N-0 or P0).
As done in previous study plans, contingencies will include single segment or element outages (N-1), and multiple element outages (N-1-1, N-2, etc) involving combinations of Lines, Transformers, Buses, and/or Plants (Generation).
Contingency files will be developed/updated to facilitate simulation runs of the same system conditions through each base case.
Contingencies

## Slide 5
Criteria
Study Criteria
System normal and Outage conditions will be modeled and studied for adequacy and system security.
Segment or element thermal loads >85% will be noted under these conditions; loads above 100% of seasonal limits will be noted as overloads.
  Overloaded segments will be “tripped” per standard relaying practice (100% - 150% thermal on lines, 125% minimum thermal on transformers) to check for “cascading” outages;
  Changes in seasonal ratings will be considered (125% winter).
Emergency ratings do not apply.
Existing special protection schemes will be considered.

## Slide 6
Criteria
Study Criteria – cont.
Voltages outside of NWE planning criteria will be noted (90%, 93%, or 95% low voltage limit depending on line voltage and outage scenario; 105% high voltage limit).
  Load-serving bus voltages may fall above or below the tabled value if conditions allow a higher/lower voltage without harm to NWE or customer equipment.
  Certain equipment ratings may dictate different limits (107% will be allowed on 100 kV systems where equipment is nameplate rated 102 kV or higher).

## Slide 7: State of the System Studies System Normal and Outage studies will be completed on all seasons of the 2016 – 2017 base cases to determine the present “state of the system” as it exists today.
Notes: Emphasis slide for questions and visual breaks.
Headline Helvetica, white, 44pt font
Body Helvetica, bold, white, 20pt font

## Slide 8
Next Steps
Next Steps
Q3: Analysis of 2016 - 2017 cases for normal and outage conditions will be completed for state of the system review.
Q4-Q5: Complete the analysis of 2021, 2026, and the 2031 cases.
  Verification of new problems
  Uncertainty scenarios (variable wind, solar, coal fired gen)
Q5: Prioritize problems using Decision Rules
Q5-Q6: Begin Mitigation Studies

## Slide 9: Local Area Planning Update Questions?
Notes: Text, 60pt font, white