## Slide 1
Local Area Planning Update to TRANSAC – September 18, 2014
Notes: 20pt Font – bold for presentation name, regular for date

## Slide 2
Base case study models representing the base scenarios have been completed for all four seasons:
  Heavy Summer (HS)
  Heavy Winter (HW)
  Light Autumn (LA)
  Light Spring (LSP) for the present (2014/15).
Future cases over the 15 year planning horizon…2019, 2024, and 2029, for 16 total cases, will be completed shortly.
Base Case Status
Notes: Title, 24pt font, bold, white
Body Copy/Bulleted Text, 22pt font, black (adjust as necessary)

## Slide 3
Existing system configuration has been modeled in 2014 HS and LA, 2014-15 HW cases and a 2015 LSP case; completed projects and other projects under construction, as well as budgeted and approved system improvements are included in 2014 and later cases.
All cases were based on a 1-in-10 load forecast.
Base Case Status
Notes: Title, 24pt font, bold, white
Body Copy/Bulleted Text, 22pt font, black (adjust as necessary)

## Slide 4
System normal (N-0), single segment or element outage (N-1), and selected credible double segment or element outage (N-2) contingency files have been developed/updated to facilitate simulation runs of the same system conditions through each base case. Outages include:
  Lines
  Transformers
  Buses
  Plants (Generation)
Contingencies to Study

## Slide 5
System normal and outage conditions were modeled and studied for adequacy and system security.
Segment or element thermal loads >85% were noted under these conditions; loads above 100% were noted as overloads (in winter, lines and transformers were allowed up to 125% continuous load).
  Overloaded segments will be tripped per standard relaying practice (100-125% thermal on lines1, 125% minimum thermal on transformers) to check for ‘cascading’ outages except as noted below:
    230 kV lines are not tripped below 150% thermal per requirements of NERC PRC-023.
    May apply to path lines or other system lines and elements deemed critical.
1 Thermal relay settings on lines will be reset to permit 125% thermal load per new Business Practice.
Study Criteria

## Slide 6
Voltages outside of NWE planning criteria were noted – 90% to 95% low voltage limit depending on line voltage and system conditions (N-0, N-1, or N-2); 105% high voltage limit – per NWE FERC Form 715 criteria.
  Load-serving bus voltages may fall above or below these limits if conditions allow a higher/lower voltage without harm to NWE or customer equipment.
  Certain equipment ratings may dictate different limits.
Existing OMS or RAS schemes were considered.
Study Criteria

## Slide 7
System Normal and Outage runs have been completed on all seasons of the 2014 and 2015 base cases to determine the present “state of the system” as it exists today.
N-0, N-1, and N-2 study results have been analyzed for the 2014 and 2015 models.
Study results show several previously known issues are now resolved, and little to no new problems have been observed in the current studies.
State of the System Studies

## Slide 8
Summary Results and Findings for 2014 Cases:
Heavy summer conditions govern for voltage and thermal conditions on most normal and outage scenarios. Heavy winter governs in some other conditions; some high voltage problems are observed under light load conditions.
Almost all higher voltage bulk system segments and elements meet criteria under all operating conditions and scenarios (500, 230, and 161 kV).
  Loss of such elements may increase load on underlying system such as auto transformers and lower voltage lines, or produce low voltage problems.
State of the System Studies

## Slide 9
Summary Results and Findings for 2014 Cases:
Most problems are observed on lower voltage system segments or elements (50 and 69 kV)…older, smaller conductor or transformers, or auto transformer ties to lower voltage systems.
Low voltage problems remain in some areas under outage conditions with some minor problems becoming worse.
  Dillon – Sheridan 69 kV system
  Lewistown Area 50 kV system
  Columbus/Stillwater Area 100 & 50 kV system
  Big Timber Area 50 kV system
State of the System Studies

## Slide 10
Summary Results for 2014 Cases: N-0 Thermal Issues
No system elements illustrate thermal overload under system normal (N-0) conditions.
State of the System Studies

## Slide 11
Summary Results for 2014 Cases: N-1 Thermal Issues
Several system elements can become thermally overloaded under N-1 conditions during heavy loading:
  Loss of the Clyde Park 161/50 kV auto transformer overloads the Melville – Big Timber 50 kV line and Big Timber Auto.
  Loss of the Ennis – Lone Mountain 69 kV line overloads the Jack Rabbit 50/69 kV auto transformer. Mitigation is in progress.
  Loss of 100 kV facilities in the Columbus area may cause additional element overloads, low voltages, and cascading outages on the 50 kV system in the Columbus and Stillwater areas. Mitigation is in process.
State of the System Studies

## Slide 12
Summary Results for 2014 Cases: N-1 Thermal Issues
Several system elements can become heavily loaded under N-1 conditions:
  Loss of the Dillon – Ennis 161 kV line overloads the Dillon-Salmon 161/69 kV auto transformers. Mitigation is currently underway.
  Loss of the Hardin Auto auto transformer overloads the Hardin – Colstrip 115 kV line due to a current limited device. Mitigation is planned.
State of the System Studies

## Slide 13
Summary Results for 2014 Cases: N-1 Thermal Issues
Several substations have two auto transformers operated in parallel (in-service, side-by-side). In some cases, loss of one transformer will cause the sister unit to overload.
  Loss of one of the Dillon-Salmon 161/69 kV auto transformers causes the other auto transformer to overload. Mitigation is currently underway.
  Loss of the Assiniboine 161/69 kV auto transformer or Rainbow 100/69 kV auto transformer heavily loads its sister unit under heavy loading conditions (the Rainbow auto issue is currently being mitigated by the Crooked Falls project).
In many of these N-1 cases, problems had been discovered previously, and mitigation plans are already in process.
State of the System Studies

## Slide 14
Summary Results for 2014 Cases: N-2 Thermal Issues
A loss of the East Gallatin 161 kV bus puts Bozeman at risk and could result in significant loss of the Bozeman 50 kV system due to another transformer overload, and resulting in cascading outages. Mitigation is planned.
The Colstrip – Sarpy Auto 115 kV line can overload for certain double contingency outages. The line rating is now limited by in-line wave traps; planned communications upgrades mitigates the problem. Mitigation is planned.
Loss of the Ennis Auto 161 kV bus can create voltage and thermal problems in the Big Sky area. Mitigation is underway.
State of the System Studies

## Slide 15
Summary Results for 2014 Cases: N-2 Thermal Issues
Loss of the Missoula 4 – Hamilton Heights 161 kV ‘A’ and ‘B’ transmission lines (common corridor) could cause segments of the Missoula 4 – Hamilton 69 kV ‘A’ and ‘B’ lines to overload. Mitigation is planned.
Loss of the Harlowton or Glengarry 100 kV buses results in low voltage in the local 50 kV systems.
Loss of the Mill Creek 100 kV Bus could overload the Anaconda and Drummond 100/50 kV auto transformers. Mitigation is already planned (convert the Anaconda – Drummond 50 kV line to 100 kV).
State of the System Studies

## Slide 16
Summary Results for 2014 Cases: N-0 Voltage Issues
Under normal system operating conditions, minor high voltage under light loading conditions is observed on the:
  Bridger area 50 kV system.
  Bozeman/Livingston area 50 kV system.
  Hi-Line 69 kV system.
  The study results are being verified; transformer tap changes or capacitor bank setting changes may correct the problem.
No voltage problems are present on the NWE BES for normal operating conditions.
State of the System Studies

## Slide 17
Summary Results for 2014 Cases: N-1 Voltage Issues
Low Voltage is produced under N-1 conditions during heavy loading in the following events:
  Loss of the Columbus-Rapelje – Alkali Creek 161kV line produces low voltage in the Columbus-Chrome area 100 & 50 kV systems under heavy summer conditions. Mitigation is planned.
  Loss of the Lower Duck Creek – Columbus-Rapelje 161 kV line produces low voltage in the Big Timber/Melville area 50 kV system during HS conditions. Mitigation is planned.
  Loss of the Dillon-Ennis 161 kV line produces low voltage in the Dillon-Sheridan area 69 kV system during HS conditions. Mitigation is planned.
State of the System Studies

## Slide 18
Summary Results for 2014 Cases: N-1 Voltage Issues
Loss of other auto transformers around the system may produce low voltage problems. High voltage links to low voltage systems are more critical today.
  Loss of the Sheridan Auto 161/69 kV auto transformer results in low voltage in the Dillon area 69 kV system. Mitigation is planned.
  Loss of the Glengarry 100/50 kV auto transformer results in low voltage in the area 50 kV system.
  Loss of the Clyde Park 161/50 kV auto transformer or a bus fault, will result in widespread low voltage across the area 50 kV system under HS or HW conditions. A spare transformer is on-site; mitigation is planned.
State of the System Studies

## Slide 19
Summary Results for 2014 Cases: N-1 Voltage Issues
The Anaconda Mill Creek 161 kV bus outage presents low voltage, overloads and widespread outage risks to the Butte/Helena/Bozeman areas. Mitigation is near completion.
No low voltage problems are present for LA or LSP conditions.
Summary Results for 2014 Cases: N-2 Voltage Issues
Most buses met N-2 voltage criteria. N-2 thermal issues often include voltage issues as well that are corrected with the mitigation of the thermal issue.
State of the System Studies

## Slide 20
Summary Results for 2014 Cases: Stability Problems
Stability (dynamics) runs have not yet been performed on the 2014 base cases, or any others.
These runs should be completed later this year.
No major problems are anticipated.
State of the System Studies

## Slide 21
Analysis of 2014/2015 cases for N-0, N-1, and N-2 conditions is complete.
Complete the analysis of 2019, 2024, and the 2029 cases.
  Verification of new problems
Prioritize problems using Decision Rules.
Begin or continue Mitigation Studies.
Additional progress and next steps

## Slide 22: Questions?
Notes: Text, 60pt font, white

## Slide 23
Notes: End Slide