## Slide 1
Local Area Planning Update to TRANSAC – December 16, 2014
Notes: 20pt Font – bold for presentation name, regular for date

## Slide 2
Status Update
Base cases representing the four base seasonal conditions over the 5, 10, and 15 year planning horizon have been completed, along with System Normal and Contingency case powerflow runs.
Analysis of Future Cases
Notes: Title, 24pt font, bold, white
Body Copy/Bulleted Text, 22pt font, black (adjust as necessary)

## Slide 3
Substation Projects included in 2019-2029 base cases:
Dillon-Salmon Auto upgrade (bus reconfig, new transformers)
Crooked Falls Expansion/Rainbow removal
Wicks Lane Sub upgrade (bus reconfig, tie to adjacent line)
East Gallatin Sub rebuild (bus reconfiguration)
Big Timber Auto upgrade (new line breakers, transformer)
Livingston Sub rebuild (combine subs, added capacitors)
Belgrade West Sub (new sub, 161/50 kV auto transformer)
York Switchyard (new sub, added line breakers)
Analysis of Future Cases
Notes: Title, 24pt font, bold, white
Body Copy/Bulleted Text, 22pt font, black (adjust as necessary)

## Slide 4
Transmission Projects included in 2019-2029 base cases:
Anaconda – Drummond 100 kV upgrade from 50 kV
Baseline – Meridian 100 kV conductor upgrade
Carbon – Stillwater 100 kV line (new)
Jack Rabbit – Big Sky 161 kV line upgrade from 69 kV
Holter – Helena 100 kV conductor upgrade
Helena Valley 100 kV Loop (new)
Missoula – Stevensville 161 kV line upgrade from 69 kV
Analysis of Future Cases
Notes: Title, 24pt font, bold, white
Body Copy/Bulleted Text, 22pt font, black (adjust as necessary)

## Slide 5
Summary Results 2019 – 2029 Cases: Thermal Issues
No thermal overloads were observed under normal system conditions.
Mill Creek 161/100 kV autos approach capacity in the ten to fifteen year planning horizon for Butte area bus fault.
Older Great Falls City 100 kV lines approach capacity in the ten to fifteen year planning horizon for certain N-1 line outages in Great Falls.
Billings Steam Plant 230/100 kV and Rimrock 161/100 kV autos overload for various Billings area 230 kV outages (N-1 and N-2) within the five year planning horizon.
Older Billings City 100 kV lines approach capacity in the fifteen year planning horizon for the N-1 of Shorey Road – Alkali Creek 230 kV.
Analysis of Future Cases
Notes: Title, 24pt font, bold, white
Body Copy/Bulleted Text, 22pt font, black (adjust as necessary)

## Slide 6
Summary Results 2019 – 2029 Cases: Thermal Issues
Baseline 100 kV bus fault overloads Steam Plant – Laurel 100 kV line in fifteen year planning horizon.
Ennis/Big Sky 69 kV system approaches capacity in ten to fifteen year planning horizon for loss of Bozeman feed.
Missoula – Bitterroot 69 kV line approaches capacity in ten to fifteen year planning horizon for a Missoula area bus fault.
At generation related switchyards under Peak Hydro conditions, N-1/N-2 losses cause remaining lines to overload:
  Loss of a Canyon Ferry 100 kV line (WAPA) overloads the other
  Loss of a Kerr 161 kV line overloads the other
  Loss of both Kerr 161 kV lines overloads the BPA tie-line to Kalispell
  Loss of two Crooked Falls to Great Falls Switchyard 100 kV line overloads the remaining line
Analysis of Future Cases
Notes: Title, 24pt font, bold, white
Body Copy/Bulleted Text, 22pt font, black (adjust as necessary)

## Slide 7
Summary Results 2019 – 2029 Cases: Voltage Issues
Under normal system conditions, minor voltage problems were observed on certain area 50 and 69 kV systems, easily mitigated with tap changes or capacitors. No problems observed on BES elements.
The following bus outages cause low voltage in their respective areas due to older bus designs:
  Mill Creek 100 kV bus
  Harlowton 100 kV bus
  Glengarry 100 kV bus
  Judith Gap 100 kV bus
Analysis of Future Cases

## Slide 8
Summary Results 2019-2029 Cases: Voltage Issues
Loss of both Missoula 4 – Hamilton Heights 161 kV lines may result in minor low voltage problems on the Hamilton 69 kV system within the five year planning horizon.
Loss of parallel Broadview – Billings 230 kV lines causes low voltage in the Billings City area in the five year planning horizon and voltage collapse in the ten to fifteen year planning horizon.
Loss of the Garrison 230 kV bus (BPA) may result in marginal to low voltages in Butte, Helena, and Bozeman areas in the fifteen year planning horizon.
Analysis of Future Cases

## Slide 9
Stability Issues
Stability (Dynamics) runs have not yet been performed on the base cases.
These runs should be completed later this year.
No major problems are anticipated.
Analysis of Future Cases

## Slide 10
Next Steps
Verify New Problems Found.
Prioritize Problems using Decision Rules.
Begin or Continue Mitigation Studies.
Next Steps

## Slide 11: Questions?
Notes: Text, 60pt font, white

## Slide 12
Notes: End Slide