## HL_graph
Final | Heavy
| MCDC = 50MW, CS=Full | Full CS | CS=1313or less
YT20 | 133 | 337 | 600
YT288 | 389 | 600 | 600
145
300
467
600
B
A
E
G
D

## LL_graph
Final
Light
| MCDC = 50MW, CS=Full | Full CS | CS=1800or less | CS=1628or less
YT20 | 197 | 415 | 501 | 600
YT288 | 331 | 448 | 600 | 600
145
300
467
600
A
B
C
E
F
G

## Heavy_Results
Heavy Winter 2002-03 Case | Corner | Fault | Open | Low Voltage | Cycles @ | Low Bus | Sheridan 230 | Colstrip | Pre-event
| ID | Bus | Line(s) |  | < 80% |  | Voltage | Units Tripped | Sheridan 230
The following set the nomogram corner points for heavy winter 2002
MTSE = -133 | A | Broadview | Broadview Garrison Double | 0.7 | <40 | SHERIDAN35.0 | 0.7 | 1S | 1.02
MCDC=50, YT=20 |  | Three-phase | [5 empty] | 2L
Colstrip = Full
MTSE = -337 | B | Broadview | Broadview Garrison Double | 0.7 | <40 | SHERIDAN35.0 | 0.7 | 1S | 1.01
MCDC=195, YT=20 |  | Three-phase | [5 empty] | 2L
Colstrip = Full
MTSE = -604 | D | Broadview | Broadview Garrison Double | 0.83 | <40 | SHERIDAN35.0 | 0.83 | 1S | 0.97
MCDC=195, YT=20 |  | Three-phase | [5 empty] | 2L
Colstrip = 1313
MTSE = -389 | E | Broadview | Broadview Garrison Double | 0.7 | <40 | SHERIDAN35.0 | 0.7 | 1S | 0.99
MCDC=50, YT=288 |  | Three-phase | [5 empty] | 2L
Colstrip = Full
MTSE = -601 | G | Broadview | Broadview Garrison Double | 0.7 | <40 | SHERIDAN35.0 | 0.7 | 1S | 0.97
MCDC=195, YT=288 |  | Three-phase | [5 empty] | 2L
Colstrip = Full(also passes CS<full)

## heavy_pf
Corner Point-----------> | A | B | D | E | G
Heavy Winter 2002-03 Case | MTSE = -133 | MTSE = -337 | MTSE = -604 | MTSE = -389 | MTSE = -601
| MCDC=50, YT=20 | MCDC=195, YT=20 | MCDC=195, YT=20 | MCDC=50, YT=288 | MCDC=195, YT=288
| Colstrip = Full | Colstrip = Full | Colstrip = 1313 | Colstrip = Full | Colstrip = Full
NORTH OF JOHN DAY | 5174.6 | 5200 | 4984.2 | 5145.2 | 5178.1
COI | 2955.7 | 2962.4 | 2906.9 | 2940.3 | 2947.5
PCDC FLOWS @CELILO1&2 | 1001.2 | 1001.2 | 1001.2 | 1001.2 | 1001.2
PCDC FLOWS @CELILO3&4 | 1501.8 | 1501.8 | 1501.8 | 1501.8 | 1501.8
BC HYDRO-NORTHWEST | 500 | 500 | 500 | 499.9 | 499.9
WEST OF HATWAI | 1453.8 | 1580.6 | 1203.3 | 1608.4 | 1732.1
WESTERN MONTANA HYDRO | 1405.7 | 1405.7 | 1405.7 | 1405.7 | 1405.7
MONTANA-NORTHWEST | 1003.8 | 1190.7 | 658.2 | 1239.1 | 1431.7
AMPS + JEFFERSON | 225.9 | 251.2 | 153 | 247.9 | 274.9
BROADVIEW-GARRISON #1 | 817.6 | 908.8 | 608.6 | 928.2 | 1024.9
BROADVIEW-GARRISON#2 | 817.6 | 908.8 | 608.6 | 928.2 | 1024.9
BROADVIEW-JUDITH GAP | 133.4 | 141.1 | 116.9 | 145.6 | 155.6
SHOREYROAD-WILSALL | 161.1 | 179.8 | 152.7 | 185.2 | 203.1
ALKALI-CLYDE PARK | 106.4 | 115 | 103.1 | 119.2 | 128.4
BROADVIEW 230/100 #1 | 33.9 | 35 | 30.9 | 35.6 | 37
BROADVIEW 230/100 #2 | 33.1 | 34.2 | 30.3 | 34.8 | 36.2
WEST OF BROADVIEW | 2103.1 | 2322.7 | 1651.1 | 2376.9 | 2610.2
COLSTRIP 1 | 330 | 330 | 200 | 330 | 330
COLSTRIP 2 | 330 | 330 | 200 | 330 | 330
COLSTRIP 3 | 767.5 | 787.4 | 460.8 | 790 | 819.6
COLSTRIP 4 | 815 | 815 | 451 | 815 | 815
COLSTRIP TTL | 2242.5 | 2262.4 | 1311.8 | 2265 | 2294.6
WEST OF COLSTRIP | 2078 | 2098 | 1147 | 2101 | 2130
WEST OF CROSSOVER | 2125 | 2317 | 1476 | 2241 | 2440
MILES CITY DC TIE FLOW | 50 | 195 | 195 | 50 | 195
IDAHO-NORTHWEST | 250.3 | 216.4 | 472.4 | 268.9 | 228.8
MIDPOINT - SUMMER LAKE | 488.6 | 470.5 | 635.6 | 506.6 | 482.4
BORAH WEST | 1116.5 | 1086 | 1330.6 | 1133.1 | 1097.4
BRIDGER WEST | 2046.9 | 2010.8 | 2114.7 | 2072.2 | 2029
PATH C | -429.9 | -451.7 | -260 | -419 | -440.9
PATH 15 | 736.4 | 729.3 | 784.8 | 750.2 | 743
TOT2 | 519.6 | 525.1 | 468.7 | 506.5 | 514.3
MONTANA-SOUTHEAST | -133.3 | -337.4 | -604.2 | -388.6 | -600.6
YELLOWTAIL NORTH (+ = North) | 96.3 | 162.7 | 432.1 | 353 | 427.9
YELLOWTAIL SOUTH (+ = South) | -80.7 | -147.2 | -416 | -72.5 | -148.3
TOT4A | 291.4 | 235.8 | 297.2 | 369 | 310.8
TOT4B | 453 | 526 | 641.2 | 448 | 532
YELLOWTAIL GENERATION | 20 | 20 | 20 | 288 | 288

## Light_Results
Light Winter 2002-03 Case | Corner | Fault | Open | Low Voltage | Cycles @ | Low Bus | Sheridan 230 | Colstrip
| ID | Bus | Line(s) |  | < 80% |  | Voltage | Units Tripped
The following set the nomogram corner points for Light Winter 2002-03
MTSE = -197 | A | Broadview | Broadview Garrison Double | 0.7 | <40 | SHERIDAN35.0 | 0.7 | 1S
MCDC=50, YT=20 |  | Three-phase | [5 empty] | 2L
Colstrip = Full
MTSE = -415 | B | Broadview | Broadview Garrison Double | 0.7 | <40 | SHERIDAN35.0 | 0.7 | 1S
MCDC=195, YT=20 |  | Three-phase | [5 empty] | 2L
Colstrip = Full
MTSE = -501 | C | Broadview | Broadview Garrison Double | 0.7 | <40 | WILSALL230 | 0.71 | 2S
MCDC=195, YT=20 |  | Three-phase | [5 empty] | 1L
Colstrip = 1800 or less
MTSE = -602 | D | Broadview | Broadview Garrison Double | 0.72 | <40 | SHERIDAN35.0 | 0.72 | 1S
MCDC=195, YT=20 |  | Three-phase | [5 empty] | 2L
Colstrip = 1628 or less
MTSE = -331 | E | Broadview | Broadview-Garrison Double | 0.7 | <40 | Big Timber 161 | >80% | 1S
MCDC=50, YT=288 |  | Three-phase | [5 empty] | 2L
Colstrip = Full
MTSE = -448 | F | Broadview | Broadview Garrison Double | 0.7 | <40 | Big Timber 161 | >80% | 1S
MCDC=195, YT=288 |  | Three-phase | [5 empty] | 2L
Colstrip = Full
MTSE = -604 | G | Broadview | Broadview Garrison Double | 0.7 | <40 | Big Timber 161 | >80% | 1S
MCDC=195, YT=288 |  | Three-phase | [5 empty] | 2L
Colstrip = 1800 or less

## light_pf
Corner Point-----------> | A | B | C | D | E | F | G
Light Winter 2002-03 case | MTSE = -197 | MTSE = -415 | MTSE = -501 | MTSE = -602 | MTSE = -331 | MTSE = -448 | MTSE = -604
| MCDC=50, YT=20 | MCDC=195, YT=20 | MCDC=195, YT=20 | MCDC=195, YT=20 | MCDC=50, YT=288 | MCDC=195, YT=288 | MCDC=195, YT=288
| Colstrip = Full | Colstrip = Full | Colstrip = 1800 | Colstrip = 1628 | Colstrip = Full | Colstrip = Full | Colstrip = 1800
NORTH OF JOHN DAY | -682.1 | -651.4 | -850.2 | -786.2 | -769.5 | -791.9 | -950.7
COI | -2751.2 | -2728.6 | -2891.1 | -2853.9 | -2802 | -2813.7 | -2947.2
PCDC FLOWS @CELILO1&2 | -737.8 | -737.8 | -737.8 | -737.8 | -737.8 | -737.8 | -737.8
PCDC FLOWS @CELILO3&4 | -1107.1 | -1107.1 | -1107.1 | -1107.1 | -1107.1 | -1107.1 | -1107.1
BC HYDRO-NORTHWEST | 500 | 500 | 500 | 500.1 | 500 | 499.9 | 500
WEST OF HATWAI | 877.3 | 1003.2 | 798.5 | 753.7 | 956 | 1026.3 | 863.4
WESTERN MONTANA HYDRO | 518.5 | 518.5 | 518.5 | 518.5 | 518.5 | 518.5 | 518.5
MONTANA-NORTHWEST | 1895.3 | 2087.8 | 1793.9 | 1717.7 | 2029.5 | 2141.8 | 1904.7
AMPS + JEFFERSON | -114 | -81.1 | -150 | -146.1 | -114.4 | -101.6 | -156.5
BROADVIEW-GARRISON #1 | 962.7 | 1057.1 | 892.2 | 855.4 | 1019.7 | 1072 | 937.1
BROADVIEW-GARRISON#2 | 962.7 | 1057.1 | 892.2 | 855.4 | 1019.7 | 1072 | 937.1
BROADVIEW-JUDITH GAP | 106.9 | 116.2 | 100.6 | 97.8 | 113.5 | 117.9 | 105.4
SHOREYROAD-WILSALL | 129.2 | 148.6 | 128.9 | 128.7 | 141.8 | 152.9 | 138.6
ALKALI-CLYDE PARK | 79.2 | 89.8 | 79.9 | 80.2 | 85.9 | 91.2 | 84.6
BROADVIEW 230/100 #1 | 24.1 | 25.4 | 23 | 22.5 | 25 | 25.6 | 23.6
BROADVIEW 230/100 #2 | 23.5 | 24.9 | 22.5 | 22 | 24.4 | 25 | 23.1
WEST OF BROADVIEW | 2288.1 | 2519.1 | 2139.3 | 2062 | 2430 | 2556.5 | 2249.7
COLSTRIP 1 | 330 | 330 | 330 | 280 | 330 | 330 | 260
COLSTRIP 2 | 330 | 330 | 330 | 280 | 330 | 330 | 260
COLSTRIP 3 | 787.1 | 805.5 | 331.3 | 513.3 | 797.8 | 810.9 | 646.9
COLSTRIP 4 | 815 | 815 | 815 | 555 | 815 | 815 | 650
COLSTRIP TTL | 2262.1 | 2280.5 | 1806.3 | 1628.3 | 2272.8 | 2285.9 | 1816.9
WEST OF COLSTRIP | 2108 | 2127 | 1652 | 1474 | 2119 | 2132 | 1663
WEST OF CROSSOVER | 2178 | 2361 | 1929 | 1790 | 2239 | 2381 | 1980
MILES CITY DC TIE FLOW | 50 | 195 | 195 | 195 | 50 | 195 | 195
IDAHO-NORTHWEST | 1344 | 1319 | 1450.7 | 1389.5 | 1427.1 | 1448.6 | 1552.1
MIDPOINT - SUMMER LAKE | 884.2 | 873.4 | 947.2 | 906.1 | 941.1 | 957.9 | 1014.9
BORAH WEST | 1546.5 | 1526.2 | 1645.9 | 1590.9 | 1621.7 | 1642.9 | 1736.8
BRIDGER WEST | 2118.1 | 2076.5 | 2177.9 | 2124.5 | 2179.6 | 2187.2 | 2260
PATH C | 143.6 | 126 | 229.1 | 216.7 | 165.5 | 166.8 | 255.6
PATH 15 | 3373.3 | 3352 | 3505.6 | 3469.9 | 3421.3 | 3431.6 | 3557.9
TOT2 | -214.3 | -233.6 | -94.2 | -127.2 | -170 | -160.2 | -45.5
MONTANA-SOUTHEAST | -196.9 | -415 | -501 | -602.2 | -330.5 | -448 | -604
YELLOWTAIL NORTH (+ = North) | 157.5 | 238 | 324.8 | 427.2 | 291.7 | 271.1 | 428.7
YELLOWTAIL SOUTH (+ = South) | -141.6 | -223.6 | -310.7 | -415.1 | -10.5 | 10.1 | -148.9
TOT4A | 431.1 | 372.1 | 466.1 | 379.3 | 520.8 | 533.1 | 579.2
TOT4B | 453 | 545 | 651 | 784 | 314 | 293 | 467
YELLOWTAIL GENERATION | 20 | 20 | 20 | 20 | 288 | 288 | 288

## yt_so_nomgram
| Billings to | Crossover to Yellowtail
Yellowtail
|  | 0.625 | 0.96429 | 1 | <==Slope
|  | YT=15 MW | YT=125 MW | YT=216 MW
| 0 | 300 | 300 | 300
| 40 | 300 | 300 | 300
| 60 | 300 | 300 | 290
| 80 | 300 | 300 | 270
| 100 | 300 | 300 | 250
| 120 | 300 | 300 | 230
| 140 | 287.5 | 280.7143 | 210
| 160 | 275 | 261.4286 | 190
| 180 | 262.5 | 242.1429 | 170
The southbound MTSE | 200 | 250 | 222.8571 | 150
operating point (603 MW) | 220 | 237.5 | 203.5714 | 130
is 220, 218 which is | 240 | 225 | 184.2857 | 110
well below | 260 | 212.5 | 165 | 90
the 220, 238 allowed | 280 | 200 | 145.7143 | 70
with YT at 15 MW | 300 | 187.5 | 126.4286 | 50
| 320 | 175 | 107.1429 | 30
| 340 | 160 | 87.8571 | 10
| 360 | 140 | 68.5714 | -10
| 380 | 120 | 49.2857 | -30
| 400 | 100 | 30 | -50