Northwest - Montana Study Report

Path 8 West to East

Summer 2003

Draft OTC Report

March 31, 2003

Northwestern Energy, Montana

# Description of path

Path 8 (Northwest – Montana), received an accepted rating of 1350 MW west-to-east based on extensive seasonal studies under all hydro and load conditions. This path (eastbound) is limited by post-disturbance thermal overloads that may occur when the critical contingency occurs.  The critical contingency is the simultaneous opening of both of the Taft – Garrison 500 kV lines.

A path diagram is at the end of this report.  The path consists of the following 10 interconnecting branches:

- Broadview-Garrison 500 kV #1 and #2,

- Rattlesnake 230/161 Auto transformer,

- Ovando – Garrison 230,

- Ovando – Hot Springs 230,

- Anaconda – Garrison 230 #1,

- Anaconda – Garrison 230 #2,

- Kerr-Elmo 115,

- Thompson Falls – Burke 115, and

- Crow Creek - Burke 115.

This path will only load to flows greater than 1100 MW net into Montana if loads are very high in Montana, the Montana control area generation is reduced to extremely low values, and the Montana-Southeast path (MTSE) is at or near the maximum (OTC) export capacity.  For this to occur the Miles City DC converter (MCDC) must be flowing west to east at or near its maximum capability (150 MW) and the flow on the Yellowtail-North portion of the MTSE path is also at or near its maximum southbound capacity.  Note also that, because the MTSE path is fully controlled by phase-shifting transformers and by the Miles City DC converter, this flow condition will only occur when a schedule exists for maximum flows outward on both portions of the MTSE path.  NWE would expect to immediately cut these schedules as well as schedules on Path 8 in the event that the critical contingency were to occur.  NWE is capable of immediately (in minutes) forcing these flows to be reduced (by adjusting phase-shifting transformers, and by notifying WAPA the eastbound schedule (and actual flow) on the MCDC must be cut.  NWE and WAPA are prohibited by the WECC loop flow mitigation and phase-shifter operating policies from forcing the actual flows to exceed the scheduled flows on the MTSE path.  An Overload Mitigation Scheme (OMS) based on these principles can be used to quickly (in minutes) reduce the flow on this path after the critical outage has occurred.  Results are presented showing the appropriate OTC for three levels of OMS response.  For each of these levels of OMS response, no critical branch may remain above 100 percent of its summer rating after the critical event assuming that the prescribed OMS response has been performed:

- NO OMS - This level assumes that no OMS is available.

- ONE OMS - This level assumes that only one (either the PSTs or the MCDC) of the proposed OMS schemes is applied after the critical disturbance.

- TWO OMS - This level assumes that both of the proposed OMS schemes will be applied to reduce flows after the critical disturbance.

# Base case descriptions

## Ratings

This study was performed using the “RATE A” ratings that were in the case that was approved through the normal WECC base case creation process.  For the critical branches listed below the ratings are those specified their respective owners (BPA and AVA):

- Columbia Falls – Kalispell 115 kV line, 85.6 MVA.

- Hot Springs – Dixon 230 kV line, 426.3 MVA.

- Burke – Burke AVA 115 kV line, 73.9 MVA.

- Pine Creek 230/115 kV transformer 144 MVA (this branch was open throughout the study).

While other branches may show overloading, they are generally in series with one of these four branches, and intermediate loads assure that they are not overloaded when the above four branches are below their ratings.  The results table shows the flow as a percent of rated amperes, based one these ratings, thus they accurately reflect whether an “overload” exists based on these ratings.

## Adjustments

The following adjustments were made to achieve the flows needed for this study:

- Increase southbound flows on the Yellowtail-north path using the eastern Montana phase shifters that control flows on that path.

- Increase eastbound flow on the MCDC, (Eastbound capacity = 150 MW),

- Reduce Montana control area hydro-generation to low levels (actual generation is reported with the results).

- All thermal generation in the Montana control area was reduced (actual generation is reported with the results).   Specifically, three Colstrip generators are off-line for most cases, and for the light load case all thermal generation is off-line except for Colstrip unit three.

- Western Mt Hydro (WMH) is reported in the results table.

# Known Sensitivities

There are several variables that can affect the Northwest – Montana OTC (NWMTOTC).  The most important of these are:

- Flathead Area Net Load (FNLD).

- Western Montana Hydro generation (Libby, Noxon, Hungry Horse, and Cabinet Gorge).

- Pre-disturbance phase-angle taps of the eastern Montana phase-shifting transformers (PSTs).

- Pre-disturbance flow on the Miles City DC Tie.

The definition of the Flathead Area Net Load (FNLD) is the sum of the flow on the Hot Springs - Flathead 230 kV line, the Libby - Haskill 230 kV line and the Elmo - Kalispell 115 kV line.  These lines are metered at Hot Springs, Libby, and Kalispell respectively.  An equivalent definition of the FNLD is:

FNLD  =  CFAC  +  OTHER LOADS  +  LOSSES  -  HHGEN

CFAC is the load at the Columbia Falls Aluminum plant.  OTHER LOADS are the loads in the small towns inside the area bound by the metering points at Hot Springs, Kalispell, and Libby.  HHGEN is the total generation at the Hungry Horse hydroelectric plant.  If the FNLD is less than 100 MW it can cause a reduction in the OTC for Path 8 for eastbound flows.  If it is negative, (HHGEN is greater than the total load in the Flathead area) it can severely limit the OTC.  When FNLD is negative by more than 100 MW (certainly possible with HHGEN at maximum output) it can overload the Columbia Falls – Kalispell 115 kV line with no line outages.  This could be taken as a limiting condition for Path 8 when the Columbia Falls – Kalispell 115 kV line is thermally protected.  However, it is quite practical to simply open this line preemptively to prevent overloading, as was shown in this study.  A greater OTC can be achieved with the line opened preemptively.

The total Western Montana Hydro generation (WMH) can have an effect on the OTC, but this effect (generation other than Hungry Horse) is smaller than the effect of FNLD (which includes effects of Hungry Horse).   These are not completely independent since HHGEN is one component of WMH.  There is no clear reason for scaling all for WMH plants together since they have different owners, and different roles to play in the overall hydro operations on the Columbia river system.  Hungry Horse is the first dam on its branch of the Columbia system.  As such it performs a significant role as a storage dam.  Because of this, WMH is an important parameter, but does not provide a simple index for setting the OTC.  Clearly there is no basis for assuming any particular generation mix for the four WMH units.

The Pre-disturbance phase-angle taps of the eastern Montana PSTs must be more than 15-25 degrees negative (the sense that forces power south on the lines that converge on the Yellowtail plant).  This is necessary to assure that the studied amount of each PSTs angle change (25 degrees) is available for OMS action.  When they are not this OMS is less effective.  If this condition is not met it will result in the reduction of the OTC to the ONE OMS level or below.  Generally these conditions are more than satisfied.  This implies that the reported results are an underestimate of the effectiveness of this OMS.

The Pre-disturbance flow on the Miles City DC Tie must be 150 MW west-to-east to match the modeled reductions.  This assures the effectiveness of an OMS based on decreasing the flow on the Mile City DC Tie (as modeled in the study).  Less eastbound flow on this tie would imply a lower degree of effectiveness for this action.  If this flow is too low the OTC should be reduced to the ONE OMS level or below.  Generally, it is not possible to get the loading studied without meeting this condition.  Note that if a reverse schedule were put into place, the flow on the MCDC could be reversed adding to the effectiveness of this OMS.

If both the Pre-disturbance phase-angle on the eastern Montana PSTs and the MCDC flow are not suitable for OMS application, then the OTC must be reduced to the NO OMS level (see summary of results).

## Elements that overload:

This path is limited by thermal overloads that occur on the remaining lines when the critical contingency occurs (i.e. post-disturbance thermal overloads).  There are four limiting elements that set the OTC:

- The Columbia Falls – Kalispell 115 kV line, summer rating is 85.6 MVA.  This line can overload for the critical contingency if the Flathead Area Net Load is small or negative (net export).  This net load is monitored by BPA Dittmer Dispatchers and the real-time OTC is managed based on the monitor requirement.  The NO OMS OTC limit (see spreadsheet) will protect this line from contingency overload with no need for an OMS response.  Also, the pre-event flow on this line is very controllable as there are two large generators to the north of the line (Libby at 600 MW and Hungry Horse at well over 300 MW) and two generators to the south of the line (Kerr is capable of more than 175 MW and Thompson Falls is capable of more than 90 MW).  It is important to realize that the best tools to control the flows on the Columbia Falls – Kalispell 115 line are local generators.  In extremely high hydro generation cases without the CFAC load, the line should be protected by thermal overload relays.

- The Hot Springs – Dixon – Rattlesnake 230 kV line.  In some cases the critical contingency can cause this line to overload.  It is rated at 426.3 MVA for this study.  See the spreadsheet of results to find those cases for which this line was overloaded.

- The Pine Creek 230/115 kV transformer was out-of-service for this study per instructions from AVA.

- The Burke – Burke AVAA line can exceed the AVA hot weather rating for this branch.  This branch segment was rated at 73.9 MVA for this study.  This is based on an assumed ambient temperature of 30 degrees Celsius.  This line never overloaded for the flow levels used in this study using the configuration instructions provided by AVA.

Light load vs. heavy load

Both a heavy-load case and a light-load case were studied.  The loads found in the base cases were left unchanged.  For the light load case, generation in Montana was reduced to extremely low levels (see results table).

Colstrip Inertia

# The reader should refer to the three-phase path rating documentation for a discussion of the importance of inertia in achieving the full rated capacity of this path.

# Disturbances

Many thermal and transient studies were completed during the three-phase rating process on 11 different base cases with a wide variety of generation patterns.  All of these results were fully published and reviewed by the WECC at large through the three-phase rating process.  Since the most critical contingency was found to be the double Taft – Garrison 500 kV line outage, this OTC study was based on this event.  For the dynamic simulations, a three-phase fault was placed at the Taft 500 kV bus, and both Garrison – Taft 500 kV lines were opened in three cycles.  Two of the Garrison 500 kV reactors were tripped 6.5 cycles after the initiation of the fault to simulate the BPA RAS scheme (WMRAS).

## Existing RAS

- The Colstrip ATR is modeled, but does not act under these conditions

- The Garrison reactor-tripping scheme (WMRAS) will be in-service.

## Overload Mitigation Schemes (OMS)

This report includes OTC values for three different OMS policy choices. The lowest OTC is based on the assumption that no OMS will be applied. The middle OTC level assumes the on OMS action will be applied (either the reduction of the phase shifts on the three eastern Montana phase-shifting transformers (PST) or the ramping of the Miles City DC Tie. The highest OTC is based on the assumption that both of the above described OMS responses are employed (PSTs and Miles City DC ramping).  It also contains OTC values for three different switching policy choices for operation of the Columbia Falls – Kalispell – Elmo – Kerr 115 kV line.  These are (1.) leaving the line in-service from end to end with no thermal protection, (2.) leaving the line in service but with thermal relay protection to prevent overloading, and (3.) preemptively opening the line at the Kerr end.  These studies clearly demonstrate the effectiveness (in principal) of the two OMS responses.  They also demonstrate the advantages and disadvantages of the various policy choices.  See attached Excel spreadsheet package “otc_summary_summer03.xls”.

## Operating Procedure items

Pine Creek 230/115 is out-of-service for summer operations (per instructions from AVA).

When the Flathead Net Area Load is negative the Columbia Falls – Kalispell line may have a relatively high initial loading.  The OTC limits provided by the net load monitor will protect this line from overload if the critical contingency occurs.

Specific OTCPG items:

- When was the last time the path was studied?

This path was studied for the three-phase rating process in 2001-02.  This path also received an expedited 1350 MW OTC for the winter of 02-03.  It was also studied for the spring 2003 OTC season.  This study for summer 2003 completes one full year of OTC study work.

- What is the critical season for this path?  Summer

- Full studies or check cases?  Full study

- What are the impacts of this path on system reliability?  Are problems local only or is there potential for cascading outside the local area?

This path is only a local problem.  It is not a threat to the security of the WECC grid.

- What is the limiting factor: transient, reactive, thermal?

Post-disturbance thermal limits for the double-contingency loss of the Taft – Garrison 500 kV lines.

- Have load and generation changes been accounted for?

Yes

- Is it appropriate to study this path in the OTCPC arena?

No, NWE, respectfully requests that OTC work on this path be discontinued.  While there are local issues, these do not represent threats to the over-all security of the WECC operations.