Bulk Electric System

Facility Rating Methodology

Table of Contents

Scope and Purpose	2

Transmission Facilities	2

1. Transmission Lines	2

1.1	Underground Transmission Cable	2

1.2	Overhead Transmission Line	2

2. Transformers	2

2.1	AutoTransformers	10

2.2	Generator Step-up transformers (GSU’s)	2

3. Shunt Capacitors	2

4. Shunt Reactors	2

5. Series Reactors	2

Terminal Equipment	2

Substation Conductors	2

Circuit Breakers	2

Instrument Transformers	2

Switches	2

Line Traps	2

Relay Settings	2

Appendix A: Generation Facilities	16

Revisions

| Rev. No. | Date | Description | By | Approval |
| --- | --- | --- | --- | --- |
| 0 | 12-9-2005 | Initial Issue | DMH | RWT |
| 1 | 5-27-2006 | OUC Review | DMH | RWT |
| 2 | 6-29-2006 | OUC General Revisions | DMH | RWT |
| 3 | 2-23-2007 | Section 3 & 5 Revisions, with "Emergency" Rating Additions | DMH | RWT |
| 4 | 5-31-2007 | OUC General Revisions for FAC-008 compliance and Generator Facility section addition | DMH/FU | RWT |

# Scope and Purpose

This document describes the methodology OUC presently uses to rate its Bulk Electric System (BES) Facilities.  The methodology described herein covers Facilities solely owned by OUC and Facilities jointly owned for which OUC has responsibility for providing ratings.  It is intended to provide documentation in compliance with the NERC Reliability Standard FAC-008-1, approved by NERC Board of Trustees with an effective date of August 7, 2006. OUC bases its rating methodology on industry standards as discussed herein.  These standards have changed over the years and OUC modifies its rating methodology from time to time to keep pace with accepted industry practice.  This document describes OUC current methodology and makes no assumptions as to the design criteria of legacy equipment and facilities.

This document describes the current OUC rating methodology for the following Bulk Electric System Facilities as defined in the NERC Glossary of Terms dated August 2, 2006:

- Transmission lines

- Transformers

- Shunt Compensators which includes Shunt Capacitors and Shunt Reactors.

- Series Reactors

- Generators

The Facilities addressed in this document are comprised of various electrical equipment or Elements (defined term by NERC).  OUC Facilities may contain one or more Elements.  For example, a transmission line includes conductors, line traps, switches, and breakers.  Protective relays for the line will also be included as part of the transmission line Facility.  All this equipment or Elements operate together with the limiting Facility ratings being derived from the individual equipment ratings.  Thus the Facility ratings will be limited by the most limiting equipment rating.  Likewise, the Facility rating will not exceed the most limiting rating of any equipment that comprises the Facility.

The scope of equipment or Elements addressed in this document includes the following:

- Transmission Conductors

- Transformers

- Series and Shunt Compensation Devices

- Generators

- Terminal Equipment

Terminal Equipment includes: circuit breakers, switches, substation conductors, instrument transformers, line traps and associated relay settings.

OUC has no transmission level Series Capacitors, Shunt Capacitors, Series Reactors, Flexible A/C Transmission Systems such as SVC or STATCOM, High Voltage Direct Current, or Electrical Energy Storage devices.

# Transmission Facilities

## Transmission Lines

OUC transmission lines are defined as those transmission circuits that terminate at fault interrupting circuit breakers.  The lines between distribution stations are termed “transmission line sections.”

Transmission Line Facilities are comprised of three main sets of equipment:  transmission substation terminal equipment, distribution substation high-side equipment and transmission line conductors.  Line conductors may be underground cable or overhead. The transmission terminal equipment includes breakers, switches, line traps, buswork, current transformers and protective relays. Switches and buswork also comprise distribution substation high-side equipment.  Since all this associated transmission line equipment is also used in other Facilities besides transmission lines, the rating methodology for this equipment is shown under a separate section, “Terminal Equipment.”  Each transmission line section of a line may have multiple conductor sizes, types, and ampacity ratings.  A particular transmission line or line section is rated based on the most limiting rating of its associated equipment.

In some cases the limiting element for a line may change with various switching arrangements.  Where a line is terminated with two breakers in parallel the line rating may be reduced when one of the breakers is open and the remaining breaker has an ampacity lower than the line conductors.  Such situations, if any, are to be handled in the Energy Control Center with specific EMS alarm logic.  For the purpose of this document an autotransformer in series with a transmission line is treated as a separate Facility with its own ratings.

### Underground Transmission Cable

Normal and Emergency Rating Criteria

Normal Ratings for underground transmission cables are determined using the below rating methodology.  OUC also has ratings above normal for these cables as have been conveyed by the cable manufacturers under a 30-minute time frame;  These ratings have been applied as our Emergency Ratings.  Pre-loading of underground transmission cables to values in excess of 75% load factor must be considered in the Emergency Ratings as a de-rating factor, and shall be determined on a case by case basis.  If pre-loading is beyond 75% load factor (i.e. loading) in excess of 2-hours in duration prior to an event, the Emergency Rating equals to Normal Rating.

Industry Standards

OUC Underground Transmission Facilities are designed per the following applicable industry standards.

For pipe type cables and accessories, the industry standard used includes the Association of Edison Illuminating Companies specification CS2-90 (AEIC CS2-90 Specifications for Impregnated Paper and Laminated Paper Polypropylene Insulated Cable, High Pressure Pipe Type).

For Solid Dielectric Crosslinked Polyethylene (XLPE) cables and accessories, the industry standard used is AEIC CS7-93 (Specifications for Crosslinked Polyethylene Insulated Shielded Power Cables Rated 69 through 138kV).

Rating Data

The AEIC cable standards listed above specify the allowable temperatures for various types and voltages of cable insulations which govern how much current may be transferred through the insulated conductor of the cable.

Acceptable Rating Methods

OUC rates cables in the following ways:

- The cable manufacturer's cable calculations using industry algorithms (such as AEIC methodology or the Neher-McGrath method outlined in "The Calculation of Temperature Rise and Load Capability of Cable Systems," in AIEE Transactions on Power Apparatus and Systems, vol. 76, October 1957)  and proprietary software.

- Certain conditions not adequately modeled by existing software may be rated using numerical methods, or other calculation techniques.

Input Criteria Assumptions

The OUC inputs to the underground rating algorithms are as follows:

- Earth Ambient Temperature: assumed to be 30-degrees Celsius per the EPRI Underground Transmission Systems Reference Book (1992 Edition, p. 209) unless can be proved otherwise.  In some cases, the manufacturer has undertaken studies or utlitized regional thermal data in order to apply lesser ambient temperature values;  These values are typically not less than 25-degrees Celsius.

- Soil Thermal Resistivity: Based on Moisture Content and is to be determined at each location an underground line is to be installed, in the form of a "Dry-Out Curve."  Typically one soil sample location is required every 1000-feet or less at each depth the cable(s) is to be placed.

- Moisture Content: To be determined at each location an underground line is to be installed, based on the type of soil, the water level at that location, and the pipe depth.

- Load Factor of Proposed Underground Line: Obtained for each line but generally not to be less than 75%.  For new lines, the use of a 100% load factor shall be considered in the preliminary engineering phase, and applied if the application warrants its use.

- Cable Depth: To be based on proposed route profile and local code restrictions.

- Fault Current: Obtained from a system fault study for each proposed installation.

- Adjacent Heat Sources:  (i.e.: adjacent heat pipes, distribution lines, or transmission lines) are to be taken into account as outlined in the EPRI Underground Transmission Systems Reference Book (1992 Edition).

- Cable Characteristics: The cable's characteristics (conductor size, type, stranding, bonding method, insulation thickness, etc.) are used to determine the cables thermal and electric losses.

### Overhead Transmission Line

Normal and Emergency Rating Criteria

OUC overhead transmission lines are defined as those lines between fault current rated circuit breakers. These lines may have one or more distribution (load serving) substations in the line between breakers. The lines between these stations are termed "transmission line sections."

Each transmission line section may have multiple conductor sizes, types, and ampacity ratings. The overall ampacity rating of each line section is based on the ampacity of the lowest rated conductor in each line section.  Original transmission line design criteria and assumptions shall be considered.  In some cases, older or heavily loaded lines will require a condition assessment and rating analysis.  Mandated Ground Clearance values by the NESC, FDOT, FDEP, and etcetera, shall be maintained at all times.

The ampacity rating of bare overhead conductors at OUC is:

1. 	Based on the steady state load current carrying capacity of the conductor.

- A continuous thermal rating based on a maximum rated conductor temperature. This rating serves as the "normal" or "full time" continuous rating for the line section it is in.  On occasion, and only as permitted by the FRCC Reliability Coordinators, real time ratings can be applied based upon sag measurements in cases where the conductor and overall installation are suitable.

- Assuming the conductor has not exceeded 75% of its "normal" rating in the prior 2-hour period, an "Emergency" 30-minute rating is listed for maximum conductor temperature in consideration of stated field and wire conditions.  Pre-loading of overhead transmission conductors to values in excess of 75% load factor must be considered in the Emergency Ratings as a de-rating factor, and shall be determined on a case by case basis.  If pre-loading is beyond 75% load factor (i.e. loading) in excess of 2-hours in duration prior to an event, the Emergency Rating equals to Normal Rating.

Industry Standards

Bare overhead transmission conductor ratings at OUC are consistent with and use the methodology described in the IEEE Standard for Calculating the Current-Temperature Relationship of Bare Overhead Conductors (IEEE Standard 738 -1993).  The solar heating model of IEEE P738/D1 (June 5, 2003) is also taken into consideration.

Input Criteria Assumptions

Summarized in the following sections is the OUC criteria used in the methodology described in the IEEE Standard for Calculating the Current-Temperature Relationship of Bare Overhead Conductors (IEEE Standard 738 –1993).

1.	Weather Conditions for rating overhead transmission conductors

Ambient Air Temperature

OUC’s current ampacity rating criteria uses a 90 degree Fahrenheit (32.2 degree Celsius) ambient air temperature.

Wind Speed (Normal to Conductor)

OUC’s current ampacity rating criteria uses a 2.0 feet per second (1.4 mile per hour) wind that is normal/perpendicular to the conductor.

Solar Insolation (Full Sun, Clear Atmosphere)

OUC’s current ampacity rating criteria typically uses 96 watts per square-foot solar insulation level unless can be proved otherwise.

2.	Maximum continuous conductor operating temperatures:

Summarized in the table below is the maximum continuous conductor operating temperatures used for the different transmission conductor types:

1. Weather conditions for rating overhead transmission conductors:

| 1.1 Ambient air temperature | 100 Degrees Fahrenheit (37.8 Degrees Celsius), down to 30 Degrees Fahrenheit, by increments of 10 degrees in tabular form for use by Operations. |
| --- | --- |
| 1.2 Wind speed (normal to conductor) | Typically 2.0 feet per second |
| 1.3 Solar insolation (full sun, clear atmosphere) | Typically 96 Watts/sq. ft. |

2. Maximum continuous conductor operating temperatures:

| 2.1 ACSR | Varies, typically 90 Degrees Celsius (194 Degrees Fahrenheit) |
| --- | --- |
| 2.2 AAC | Varies, typically 75 Degrees Celsius (167 Degrees Fahrenheit) |
| 2.3 ACSS / TW | Varies, typically 200 Degrees Celsius (392 Degrees Fahrenheit) |
| 2.4 Copper Hard Drawn | Varies, typically 75 Degrees Celsius (167 Degrees Fahrenheit) |

3. Conductor properties:

| 3.1 Conductivity |  |
| --- | --- |
| ACSR | 62% IACS* |
| AAC | 62% IACS* |
| ACSS / TW | 63% IACS* |
| Copper | 97% IACS* |
| 3.2 Emissivity, absorptivity | Typically 0.5 |

*International Annealed Copper Standard

1.2.1 	Introduction--Overhead Ground Wires

OUC overhead transmission lines are defined as those lines between fault current rated circuit breakers. These lines may have one or more distribution (load serving) substations in the line between breakers. The lines between these stations are termed "transmission line sections."

Generally, each transmission line has one or more overhead ground wires that provide protection from lightning strikes and provide a low impedance path to ground for ground fault currents. Each transmission line section may have multiple overhead ground wire sizes, types, and fault current capacity ratings. The overhead ground wire must have sufficient capacity to carry the expected fault current magnitude for the location on the line it protects. The maximum fault current occurs at the bus. The magnitude of the fault current available at each transmission line structure decreases as the distance from the buss increases due to the impedance of the line.

Several steps are followed to determine the size of overhead ground wire sufficient to withstand the available fault current. First, the magnitude of the fault current available at each bus on the transmission line is calculated. Next, the magnitude of the fault current available at each structure along the line is calculated. Finally, an overhead ground wire with sufficient fault current capacity is selected for the line.

The fault current capacity rating of galvanized steel and aluminum clad steel overhead ground wires at OUC is:

1. Based on the short term current carrying capacity of the wire.

2. A short term thermal rating based on a maximum wire temperature.

The fault current capacity rating of optical ground wires (OPGW) overhead ground wires at OUC is specified as follows:

Size 			Fault Current Capacity (kA2 -sec)

.507" diameter				75
.602" diameter 			80

.646" diameter 			102

1.2.2 	Rating Methodology for Overhead Ground Wires

Transmission line overhead ground wire ratings at OUC are consistent with and use the methodology described in the Paper by S. R. Lambert titled Minimum Shield Wire Size Fault Current Considerations published in the IEEE Transactions on Power Apparatus and Systems, Vol. PAS-I02, No.3, March 1983.

1.2.3 	Overhead Ground Wire Fault Current Capacity Criteria

1. Maximum wire temperatures:

| 1.1 Alumoweld | 371 Deg-C (700 Deg-F) momentary |
| --- | --- |

2. Initial wire temperatures:

| 2.1 Alumoweld | 35 Deg-C (95 Deg-F) |
| --- | --- |

## Transformers

Transformer Facilities include Generator Step-up (GSU) transformers, AutoTransformers and associated connected equipment.  Associated equipment connected to the transformer such as breakers, buswork, switches and protective relays associated with Transformer Facilities are shown under section entitled “Terminal Equipment.”  This other equipment is designed not to be limiting Elements for the operation of the transformer.  Therefore the transformer ratings become the limiting ratings of the Facility.

### AutoTransformers

At OUC, only AutoTransformers are used for voltage transformation between transmission voltage levels, 69 kV and above. Transmission system autotransformers are rated on an individual basis for those AutoTransformers that are part of the bulk transmission system. The bases for these ratings are the continuous or nameplate ratings. These ratings are maintained on a list that includes the substation name, the OUC equipment company asset number or location within the substation, the AutoTransformer nameplate rating in MVA (Mega-Volt-Amperes), and the Summer Emergency and Winter Emergency ratings, also in MVA. The emergency ratings have been determined over time by a variety of methods including the following:

- Application of Standard IEEE C57 .115, Guide for Loading Mineral-Oil Immersed Power Transformers Rated in Excess of 100 MV A (65° C Winding Rise).

- Limitations of the transformer bushings as established and evaluated by the original bushing manufacturer or by bushing nameplate rating.

The following specified criteria are used to determine autotransformer emergency ratings. The transformer shall be capable of being loaded in consideration of its nameplate rating with less than 1 % loss- of-life cumulative.

Worst case operational requirements under either Summer or Winter overloads are as follows:

- Top oil temperature shall not exceed 95°C or manufacturer's limits during the 24-hour period

- Winding hottest-spot temperature shall not exceed 105°C or manufacturer's limits during the 24-hour period

- Temperature of any metallic part shall not exceed 120°C or manufacturer's limits during the 24-hour period

- Free gas or dissolved acetylene and combustible gases indicative of evolving damage conditions shall not be generated during the 24-hour period

- The maximum ratings in some cases are limited by the ampacity of the transformer bushings.

### Generator Step-Up Transformers (GSU’s)

Transmission GSU’s at OUC are specified and rated according to:

- IEEE C57.1200 , IEEE General Requirements for Liquid-Immersed Distribution, Power, and Regulating Transformers, and IEEE C57.116 Guide for Transformers Directly Connected to Generation.

Transmission GSU’s are specified, designed and applied for the full range of normal system loading conditions and ranges to which they will be subjected. The Normal Rating for OUC transmission GSU’s are rated per the manufacturer’s nameplate.  OUC does not have ratings above normal for GSU’s therefore no Emergency Ratings are provided as they would be equal to the Normal Ratings.

Other associated power system equipment connected to the GSU such as breakers, switches, buswork, and relay settings are designed not to be limiting Elements for the operation of the GSU. Therefore the GSU ratings become the limiting ratings of the Facility.  The rating methodology for these other devices is provided under section, “Terminal Equipment”.

## Shunt Capacitors

Transmission shunt capacitors at OUC are specified and rated according to:

- IEEE 18, IEEE Standard for Shunt Power Capacitors

- IEEE 1036, IEEE Guide for the Application of Shunt Power Capacitors

- IEEE C37.99, IEEE Guide for the Protection of Shunt Power Capacitors

Transmission shunt capacitors are specified, designed and applied for the full range of normal system voltage conditions and ranges to which they will be subjected. The Normal Rating for OUC transmission shunt capacitors are rated per the manufacturer’s nameplate.  OUC does not have ratings above normal for shunt capacitor banks therefore no Emergency Ratings are provided as they would be equal to the Normal Ratings.

Other associated power system equipment connected to the bank such as breakers, switches, buswork and relay settings are designed not to be limiting Elements for the operation of the bank. Therefore the shunt capacitor bank ratings become the limiting ratings of the Facility.  The rating methodology for these other devices is provided under section, “Terminal Equipment”.

## Shunt Reactors

Shunt reactors in support of the Bulk Electric System are specified and rated according to:

- IEEE C57.21, IEEE Standard Requirements, Terminology, and Test Code for Shunt Reactors Rated Over 500 kVA

Shunt reactors in support of the Bulk Electric System are specified, designed and applied for the full range of system voltage conditions and ranges to which they will be subjected. The Normal Rating for OUC shunt reactors are rated per the manufacturer’s nameplate.  OUC does not have ratings above normal for shunt reactors therefore no Emergency Ratings are provided as they would be equal to the Normal Ratings.

Other associated power system equipment connected to the reactor such as breakers, switches, buswork and relay settings are designed not to be limiting Elements for the operation of the reactor. Therefore the reactor ratings become the limiting ratings of the Facility.  The rating methodology for these other devices is provided under section “Terminal Equipment”.

## Series Reactors

Transmission series connected reactors are specified and rated according to:

- ANSI/IEEE C57.16, IEEE Standard Requirements, Terminology, and Test Code for Dry-Type Air-Core Series-Connected Reactors

- ANSI C57.99, Guide for Loading Dry-Type and Oil-Immersed Current-Limiting Reactors.

Transmission series reactors are rated per the manufacturer’s specifications. The Normal Rating for OUC transmission series reactors is given on the manufacturer’s nameplate. OUC does not provide ratings above normal for series reactors therefore no Emergency Ratings are provided as they would be equal to the Normal Ratings.

Other associated power system equipment connected to the series reactor such as breakers, switches, buswork and relay settings are designed not to be limiting Elements for the operation of the reactor. Therefore the reactor ratings become the limiting ratings of the Facility.  The rating methodology for these other devices is provided under section “Terminal Equipment”.

# Terminal Equipment

## Substation Conductors

Ampacities for most conductors used in outdoor substations are based on single bus conductors in free air, 40° C ambient temperature, in the sun, 2-foot/second wind velocity, and typical emissivity factors of 0.35 with sun for copper and 0.5 with sun for aluminum, and a percent conductivity based on the International Annealed Copper Standard (IACS) conductivity. For new installations, the conductor sizes will normally be determined with conductor ampacities for a 30° C temperature rise above 40° C ambient, and shall ordinarily be based upon industry and manufacturer's recommendations.

Aluminum and copper rigid bus conductors, including bar, angle, tube, and integral web, are rated with 2-foot/second wind velocity.  The rigid bus conductor ratings at OUC are consistent with and use the methodology described in the IEEE Guide for Design of Substation Rigid-Bus Structures, IEEE Std 605.

ACSR conductors are normally used at OUC substations in high voltage areas and are rated with 2-foot/second wind velocity.  The ACSR conductor ratings at OUC are consistent with and use the methodology described in the IEEE Standard for Calculating the Current-Temperature of Bare Overhead Conductors, IEEE Std 738.

Bare copper cables are rated with 2-foot/second wind velocity.  Bare copper cable conductor ratings at OUC are consistent with the ratings listed in the Anderson Electrical Connectors – Technical Data booklet.

OUC’s philosophy is that conductors and connectors should be ampacity rated at or above the switches and equipment to which they are connected.  For any given ampacity, the conductor should operate cooler than the switch or equipment, thus acting as a heat sink. OUC does not have ratings above normal for substation conductors therefore no Emergency Ratings are provided as they would be equal to the Normal Ratings.

## Circuit Breakers

AC High-Voltage Circuit Breaker are specified by operating voltage, continuous current, interrupting current, and operating time in accordance with ANSI/IEEE Standards C37 series, “Symmetrical Current Basis.” These ratings are indicated on the individual Circuit Breaker nameplate.  The following standards are referenced in the breaker specifications:

- ANSI C37.04, IEEE Standard Rating Structure

- ANSI C37.06, Standard for Switchgear- AC High-Voltage Circuit Breakers Rated on a Symmetrical Current Basis- Preferred Ratings and Related Required Capabilities.

- ANSI C37.09, IEEE Standard Test Procedure for AC High-Voltage Circuit Breakers Rated on a Symmetrical Current Basis.

- IEEE C37.010b, Standard for Emergency Load Current-Carrying Capability

- IEEE C37.010e, (Supplement to IEEE C37.010).

OUC rates transmission circuit breakers according to the manufacturer’s specifications. The Normal Rating for OUC transmission circuit breakers are rated as shown on the manufacturer’s nameplate.  Nameplate interrupting ratings are adjusted for reclosing of oil circuit breakers per ANSI C37.04, IEEE Standard Rating Structure.  OUC does not have ratings above normal for transmission circuit breakers therefore no Emergency Ratings are provided as they would be equal to the Normal Ratings.

## Instrument Transformers

Free standing current transformers, metering units or voltage transformers, are rated according to:

- IEEE C57.13, Standard Requirements for Instrument Transformers.

OUC rates transmission instrument transformers according to the manufacturer’s specifications. The Normal Rating for OUC transmission instrument transformers are rated as shown on the manufacturer’s nameplate.  OUC does not have ratings above normal for transmission instrument transformers therefore no Emergency Ratings are provided as they would be equal to the Normal Ratings.

## Switches

The following Standards are used to rate High-Voltage switches:

- IEEE C37.30, Standard Requirements for High-Voltage Switches.

- IEEE C37.37, Standard Loading Guide for AC High-Voltage Switches (in excess of 1000 volts).

- IEEE C37.37a, Standard Loading Guide for AC High-Voltage Air Switches Under Emergency Conditions.

Transmission switches are rated according to the manufacturer’s specifications. The Normal Rating for OUC transmission switches are rated as shown on the manufacturer’s nameplate.  OUC does not have ratings above normal for transmission switches therefore no Emergency Ratings are provided as they would be equal to the Normal Ratings.

## Line Traps

Line traps are rated according to:

- ANSI C93.3, Requirements for Power-line Carrier Line Traps.

Line traps are rated according to the manufacturer’s specifications. The Normal Rating for OUC line traps are rated as shown on the manufacturer’s nameplate.  OUC does not have ratings above normal for line traps therefore no Emergency Ratings are provided as they would be equal to the Normal Ratings.

OUC is working to eliminate Power-line Carrier Line Traps from the transmission system by use of fiber optic cable in Optical Ground Wire (OPGW) and other overhead and underground fiber optic cable systems.

## Relay Settings

OUC is currently following NERC System Protection Control Task Force applicable guidelines for relay loadability.  It is OUC’s design philosophy that relay settings shall not be the limiting factor on transmission system transfer capability, and shall be implemented to properly coordinate with neighboring Utilities, as may be required.  Relays sensitive to system loading are being set above rated ampacity.

# Appendix “A” – Generation Facilities

Rev 0

## Generation Facility

## Rating Methodology

| Rev. No. | Date | Description | By | Approval |
| --- | --- | --- | --- | --- |
| 0 | 5/31/07 | Origination of Document for Generation Facilities | RAP | MJB |

- GENERATION FACILITY RATING METHODOLOGY

This facility rating methodology document addresses three capabilities:

- Unit generation commitment capabilities – These ratings are net generation power by unit.  The ratings are short-term representing capabilities for the succeeding year only.

- Unit generation long-term capabilities – These ratings are net generation power by unit.  The ratings are long-term, representing capabilities beyond the current year.

- Gross generator reactive capabilities – These ratings are gross reactive power by generator.  The ratings represent generator maximum lagging reactive capabilities at maximum sustainable generation for summer conditions.

- COMMITMENT GENERATION CAPABILITY RATING METHODOLOGY

  - OBJECTIVES

The purpose of this procedure is to document the process used to determine the unit commitment capability ratings for the OUC system.  These ratings are short-term in nature and represent the expected unit generation capability for the next year.

  - CAPABILITY RATING SYSTEM

OUC will document unit and system capabilities in the Power Resources Business Unit annually for the succeeding year.

Documentation of the OUC system capability ratings by unit will be performed at three operational states:  On-Control, Off-Control, and Peak.  The definitions of these states are as follows:

- On-Control Continuous

The maximum hourly generation which can be obtained from a unit without encountering any delays and which can be maintained for sustained periods without operating difficulties.  This is the high load limit set into the automatic load control by plant operators under normal conditions.

- Off-Control Continuous

An intermediate peaking generation, which after advanced notice to the plant, can be maintained for sustained periods.

- Peak

The maximum hourly generation, which after advance notice to the plant, can be maintained for periods of up to four hours, or longer with local management approval.

Furthermore, these states are each rated for two seasons:  Summer (April through October), and Winter (November through March).  The seasonal rating for each unit differs by the effects of ambient conditions on the unit,  such as ambient air temperature and circulating water temperature.  These conditions are specific to each unit, where necessary, to reflect a representative seasonal day.

Unit capability ratings are intended to represent each unit’s actual capability for the current year.  Typically, OUC re-assesses unit capability ratings on an annual basis.

Each unit’s actual capability is determined and compared to its rated capability.  If a unit’s rated capability is not representative of the actual capability, the reason is analyzed.  If this reason is considered short-term (less than one year), the rating is not changed.  If this reason is considered long-term (longer than one year), a new actual capability is determined and the rating is changed to reflect this new capability.

In cases for planned long-term changes during the current year, such as new generation, equipment upgrades, repowering, etc., a date for the rating change will be included for clarity.

  - UNIT DESIGN CAPABILITY

Initially, the capability rating process begins with the unit’s design capability.  Depending on the status of the unit (new generation, repowering, performance upgrade, etc.), this may involve evaluating design heat balances, engineering studies, manufacturer design information, or other material.

The capability rating based on design is the best estimate of unit performance for the current year.  Once the unit can be tested, the rated capability may be revised to reflect actual capability.

  - UNIT CAPABILITY TESTING

When a unit can be tested, capability is determined from test data derived from formal test results, such as acceptance testing, post-overhaul testing, incremental heat rate testing, etc.  Typically, this involves adjusting test data for ambient conditions and operational conditions to simulate performance for various conditions.

These tests are performed in accordance with OUC test procedures, which are based on ASME Power Test Codes.

Test data is reviewed and compared to rated capability for most units annually.  If it is determined that the unit capability rating is to be changed, this change will be documented to reflect the new rating.

  - SYSTEM CAPABILITY

System commitment capability is determined as the summation of relevant (off-control/on-control, or Summer/Winter, etc.) unit capabilities.

- LONG-TERM GENERATION CAPABILITY RATING METHODOLOGY

  - OBJECTIVES

The purpose of this procedure is to document the process used to determine the unit long-term (longer than one year) capability ratings for the OUC system.  These ratings are the basis for long-term capability expectations, typically for long-range planning purposes.

  - CAPABILITY RATING SYSTEM

OUC officially documents unit and system capabilities for the Power Resources Business Unit, issued annually.

Long-term planning is documented for the OUC system capability ratings by unit at three operational states:  On-Control, Off-Control, and Peak.  The definitions of these states are as follows:

- On-Control Continuous

The maximum hourly generation which can be obtained from a unit without encountering any delays and which can be maintained for sustained periods without operating difficulties.  This is the high load limit set into the automatic load control by plant operators under normal conditions.

- Off-Control Continuous

An intermediate peaking generation, which after advanced notice to the plant, can be maintained for sustained periods.

- Peak

The maximum hourly generation, which after advanced notice to the plant, can be maintained for periods of up to four hours, or longer with local management approval.

Furthermore, these states are each rated for two seasons:  Summer (April through October), and Winter (November through March).  The seasonal rating for each unit differs by the effects of ambient conditions on the unit, such as ambient air temperature and circulating water temperature.  These conditions are specific to each unit, where necessary, to reflect a representative seasonal day.

Unit capability ratings are intended to represent each unit’s expected capability at an average state of maintenance between overhaul cycles.  Typically, OUC re-assesses these unit capability ratings on an annual basis.

  - UNIT “BEST-ATTAINABLE” CAPABILITY

Each unit’s expected capability is the unit’s “best-attainable” performance degraded by a factor representative of the typical average state of performance between overhauls.  The “best attainable” is determined from the actual best performance of the unit (typically acceptance test or post-overhaul test).  If a unit is new generation, the “best-attainable” capability will be based on the unit’s design capability.

In cases for planned long-term changes during the current year, such as new generation, equipment upgrades, repowering, etc., a date for the rating change will be specified.  Depending on the unit, this may involve evaluating design heat balances, engineering studies, manufacturer design information, or other material.  Once the unit can be tested, the rated “best-attainable” capability may be revised to reflect the actual capability.

An appropriate degradation factor is applied to the “best-attainable” performance to represent a level of performance mid-way between overhauls.  This factor is based on the unit’s or fleet’s typical historical degradation rate.

  - UNIT CAPABILITY TESTING

When a unit can be tested, capability is determined from results derived from formal test data, such as acceptance testing, post-overhaul testing, incremental heat rate testing, etc.  Typically, this involves adjusting test data for ambient conditions and operational conditions to simulate performance for various conditions.

These tests are performed in accordance with OUC test procedures, which are based on ASME Power Test Codes.

Test data is reviewed and compared to rated capability for most units annually.  If it is determined that the unit long-term rating is to be changed due to a permanent change in design capability (equipment upgrade, repowering, etc.) a new capability is determined and the long-term rating is changed and documented.

  - SYSTEM CAPABILITY

System long-term capability is determined as the summation of relevant (off-control/on-control, or Summer/Winter, etc.) unit capabilities.

- REACTIVE POWER CAPABILITY RATING METHODOLOGY

  - OBJECTIVES

The purpose of this procedure is to document the process used to determine the generator reactive power capability ratings for the OUC system.  These ratings are the basis for establishing the expected reactive capability of the units to meet current system reactive power demands.

  - CAPABILITY RATING SYSTEM

OUC documents unit and system reactive power capabilities in the Power Resources Business Unit for reference.

Documentation will cover the OUC system capability ratings by generator at three operational states:  1) Maximum lagging reactive power @ Maximum generation, 2) Maximum leading reactive power @ Maximum generation, and 3) Maximum lagging reactive power @ Minimum generation.  The descriptions of these states are as follows:

- Maximum lagging reactive power @ Maximum generation

This is the maximum sustainable lagging reactive power that can be obtained from a generator operating at the unit’s maximum sustainable generation.  This generator capability is rated by testing under summer conditions per FRCC requirements.  When a generator cannot be tested for whatever reason, it may be rated based on prior testing or planned work.

If the summer testing demonstrates full design capability, the generator will be deemed design-capable, and the summer rating will be the design lagging capability at the design power factor.  The winter rating will be determined using the design lagging capability curve also, but at the winter maximum sustainable generation.

If the summer testing demonstrates the inability to achieve full design capability due to:

- The inability of the power system grid to accept the full generator capability (such as high system voltage), the generator will be deemed design-capable, and that the summer and winter ratings will be the full design lagging capability at the generator design power factor.

- Limits associated with the generator or unit (such as ancillary system capability, or equipment issues), the generator will not be deemed design-capable.  The summer and winter ratings will be the actual lagging capability achieved during the summer test (due to summer’s more critical operating conditions).

- Maximum leading reactive power @ Maximum generation

This is the maximum sustainable leading reactive power that can be obtained from a generator operating at the unit’s maximum sustainable generation.  This generator capability is rated by evaluating the capability achieved during the summer maximum lagging reactive power test.

If the generator was deemed design-capable by the summer test, then the capability will be rated at its full leading reactive power capability at the winter maximum sustainable generation, using the design capability curve.

If the generator was not deemed fully design-capable by the summer test, then the lagging reactive power capability will be based on previous operating data or engineering judgment, depending on the nature of the issue.

These generator reactive power capabilities are represented as:

- Gross Reactive Power

This is the rating at the generator terminals.  This rating is used by OUC to monitor generator performance.

- Net Reactive Power – Low Side

This is the rating at the low voltage side of the generating station step-up transformer.  This is calculated by estimating the reactive power loss due to the auxiliary bus power factor.  This rating is used by OUC for system planning.

- Net Reactive Power – High Side

This is the rating at the high voltage side of the generating station step-up transformer.  This is calculated by additionally estimating the reactive power loss due to the transformer impedance.  This rating was requested by the FRCC.

Generator reactive power capability ratings are intended to represent each generator’s actual capability for the current year.  OUC re-assesses unit capability ratings as required by the FRCC.

These reactive power capability ratings are based on generator capability and not unit capability due to complications inherent with reactive power testing.  Because reactive power capability demonstration can be hampered by grid system conditions, it is more likely that one generator’s capability be demonstrated successfully, than if several were tested simultaneously from the same unit.

  - GENERATOR DESIGN CAPABILITY

Initially, the capability rating process begins with the unit’s design capability.  This may involve evaluating engineering studies, manufacturer design information, or other material.

Ancillary systems or grid conditions may limit the generator’s ability to demonstrate full capability.  If the generator can be successfully tested, the rating may be revised to reflect actual capability.

  - UNIT CAPABILITY TESTING

When a generator can be tested, the objective is to achieve the design capability curve capability.  If the design capability target is achieved, it will be rated at the design reactive capability at the design power factor.  If it is limited by system conditions beyond the control of the unit, it will be rated at the design capability at the design power factor.

If it is limited by an ancillary system, or other unit issue, the limitation will be analyzed.  If the limitation can be addressed in the short term, the unit will be re-tested.  If the issue cannot be resolved, it will be rated at the tested capability.

These tests are performed in accordance with OUC test procedures, which are based on the FRCC Standards Handbook – Voltage and Reactive Control, Rev Feb 2004.

Test data is reviewed and compared to rated capability for most units annually. If it is determined that the unit capability rating is to be changed, this change will be documented to reflect the new rating.

  - SYSTEM CAPABILITY

System reactive power capability is determined as the summation of generator capabilities.